## Recent Changes
List of Approved Backflow Prevention Assemblies
2025-01-01
Supersedes All Prior Lists
2025 © University of Southern California
Foundation for Cross-Connection Control and Hydraulic Research
a Division of the Viterbi School of Engineering
ADDITIONS
Type | Manufacturer | Model | Size | Orientation(s) | Date Added | Type | Manufacturer | Model | Size | Orientation(s) | Date Added
Double Check Valve Assemblies | [5 empty] | Double Check Detector Assemblies
Pressure Vaccum Breaker | [5 empty] | Reduced Pressure Principle Detector Assemblies
Spill-Resistant Vacuum Breaker | [5 empty] | Double Check Detector Assemblies-Type II
Reduced Pressure Principle Assemblies | [5 empty] | Reduced Pressure Principle Detector Assemblies-Type II
SUSPENSIONS
AS PART OF AN ASSEMBLY'S ONGOING APPROVAL PROCESS, MANUFACTURERS ARE REQUIRED TO SUBMIT SELECTED ASSEMBLIES FOR REVIEW AND RE-EVALUATION.
WHEN A MANUFACTURER FAILS TO PROVIDE A REQUIRED ASSEMBLY, THE ASSEMBLY’S APPROVAL IS SUSPENDED. ONCE THE ASSEMBLY SATISFACTORILY
COMPLETES THE RENEWAL REVIEW AND RE-EVALUATION, THE SUSPENSION WILL BE REMOVED.
Type | Manufacturer | Model | Size | Orientation(s) | Date Suspended
DELETIONS
ASSEMBLY AND SPARE PARTS ARE NO LONGER MANUFACTURED
Type | Manufacturer | Model | Size | Orientation(s) | Date Deleted

## Notices
Notices
REGARDING RENEWALS: The original Certificate of Approval–identified by the Edition of the Manual and the approval date shown in this list is valid as of the date of this list, only if the original or renewal date shown hereon is within three (3) years of the date of this list. The responsibility to request a renewal of an Approval is that of each manufacturer. The USC Foundation retains the right of determining the extent of re-evaluation required before renewal is granted. Certificates of Approval are not recalled for the purpose of updating the effective date. This revision of date is only published via the current List of Approved Backflow Prevention Assemblies. REGARDING INSTALLATION: Unless otherwise specified by the manufacturer all assemblies are to be installed on cold potable water applications - below 110oF. Also, all of the assemblies listed are Approved for the INDICATED ORIENTATION(S) ONLY. Rotation of assemblies on either axis will invalidate the USC Foundation’s Approval. Use of spare parts other than those of the original manufacturer invalidates the Approval. Rotation of shutoff valves of one bolt hole only is permitted only for the 2 1/2” and larger flanged assemblies. REGARDING LEAD CONTENT: In order to determine if backflow preventers comply with lead-free requirements of several states and the Safe Drinking Water Act, USC Foundation Approved assemblies which comply with the ≤ 0.25% lead requirement are indicated by a Y in the column ≤ 0.25%Pb. REGARDING LIST UPDATES: The List of Approved Assemblies is printed annually in the first quarter of the year. Update notices are printed and sent to USC Foundation Members quarterly. The most recent changes to the List may be found on the USC Foundation’s website. The web version of the List is updated each time a change is made. REGARDING SUSPENSIONS: As part of an assembly's ongoing approval process, manufacturers are required to submit selected assemblies for review and re-evaluation. When a manufacturer fails to provide a required assembly, the assembly’s approval is suspended. Once the assembly satisfactorily completes the renewal review and re-evaluation, the suspension will be removed.

## List
Type | Manufacturer | Model | Size | Orientation(s) | Approved | Renewed | ≤0.25% Pb | Manual | Shutoffs | Y-Spare Parts Only | Bypass | Meters | Notes
AVB | Ames | A100 | 0.75 | VUH | 1991-11-01 | 2024-11-01 | N | 8 |  | Y
AVB | Ames | A100 | 1 | VUH | 1991-11-01 | 2024-11-01 | N | 8 |  | Y
AVB | Ames | A100 | 1.5 | VUH | 1991-09-27 | 2024-09-27 | N | 8 |  | Y
AVB | Ames | A100 | 2 | VUH | 1991-08-21 | 2024-08-21 | N | 8 |  | Y
AVB | Watts | 288AM3 | 1.25 | VUH | 1991-08-12 | 2024-08-12 | N | 8 |  | Y
AVB | Watts | 288AM3 | 1.5 | VUH | 1991-09-27 | 2024-09-27 | N | 8 |  | Y
AVB | Watts | 288AM3 | 2 | VUH | 1991-08-21 | 2024-08-21 | N | 8 |  | Y
AVB | Watts | 288AM3 | 2.5 | VUH | 1991-09-10 | 2024-09-10 | N | 8 |  | Y
AVB | Watts | 288AM3 | 3 | VUH | 1991-09-16 | 2024-09-16 | N | 8 |  | Y
AVB | Watts | 288AM5 | 0.75 | VUH | 1991-11-01 | 2024-11-01 | N | 8 |  | Y
AVB | Watts | 288AM5 | 1 | VUH | 1991-11-01 | 2024-11-01 | N | 8 |  | Y
DC | Ames | 2000-DC | 10 | H | 1987-08-04 | 2023-08-04 | N | 7 | tt,ee,ff,gg,hh,ll,mm,oo,pp,uu,ccc,ddd,ffff,gggg | Y |  |  | formerly Model DC
DC | Ames | 2000-DCA | 4 | H | 1988-01-11 | 2024-01-11 | N | 7 | tt,ee,ff,gg,hh,ll,mm,oo,pp,uu,ccc,ddd,ffff,gggg | Y |  |  | formerly Model DCA
DC | Ames | 2000-DCA | 6 | H | 1988-01-11 | 2024-01-11 | N | 7 | tt,ee,ff,gg,hh,ll,mm,oo,pp,uu,ccc,ddd,ffff,gggg | Y |  |  | formerly Model DCA
DC | Ames | 2000-DCA | 8 | H | 1988-01-11 | 2024-01-11 | N | 7 | tt,ee,ff,gg,hh,ll,mm,oo,pp,uu,ccc,ddd,ffff,gggg | Y |  |  | formerly Model DCA
DC | Ames | 2000-G-DC | 10 | H | 1987-08-04 | 2023-08-04 | N | 7 | tt,ee,ff,gg,hh,ll,mm,oo,pp,uu,ccc,ddd,ffff,gggg | Y |  |  | formerly Model DC
DC | Ames | 2000-G-DCA | 4 | H | 1988-01-11 | 2024-01-11 | N | 7 | tt,ee,ff,gg,hh,ll,mm,oo,pp,uu,ccc,ddd,ffff,gggg | Y |  |  | formerly Model DCA
DC | Ames | 2000-G-DCA | 6 | H | 1988-01-11 | 2024-01-11 | N | 7 | tt,ee,ff,gg,hh,ll,mm,oo,pp,uu,ccc,ddd,ffff,gggg | Y |  |  | formerly Model DCA
DC | Ames | 2000-G-DCA | 8 | H | 1988-01-11 | 2024-01-11 | N | 7 | tt,ee,ff,gg,hh,ll,mm,oo,pp,uu,ccc,ddd,ffff,gggg | Y |  |  | formerly Model DCA
DC | Ames | 2000B | 0.5 | H | 1983-12-06 | 2022-12-06 | N | 8 | (vv),xx,ooo,hhhh,pppp,rrrrr | N |  |  | Upgraded to 9th Ed.
DC | Ames | 2000B | 0.5 | H | 1997-06-16 | 2024-06-16 | N | 9 | (vv),xx,ooo,hhhh,pppp,rrrrr | N |  |  | Previous 8th Ed. Approval
DC | Ames | 2000B | 0.5 | VU | 1997-06-16 | 2024-06-16 | N | 9 | (vv),xx,ooo,hhhh,pppp,rrrrr | N
DC | Ames | 2000B | 0.75 | H | 1993-04-05 | 2023-04-05 | N | 8 | (vv),xx,ooo,hhhh,pppp,rrrrr | N
DC | Ames | 2000B | 0.75 | VU | 1996-08-27 | 2023-08-27 | N | 8 | (vv),xx,ooo,hhhh,pppp,rrrrr | N
DC | Ames | 2000B | 1 | H | 1991-02-26 | 2024-02-26 | N | 8 | (vv),xx,ooo,hhhh,pppp,rrrrr | N |  |  | Upgraded to 9th Ed.
DC | Ames | 2000B | 1 | H | 1998-05-18 | 2022-05-18 | N | 9 | (vv),xx,ooo,hhhh,pppp,rrrrr | N |  |  | Previous 8th Ed. Approval
DC | Ames | 2000B | 1 | VU | 1998-05-18 | 2022-05-18 | N | 9 | (vv),xx,ooo,hhhh,pppp,rrrrr | N
DC | Ames | 2000B | 1.25 | H | 1996-10-01 | 2023-10-01 | N | 8 | (vv),xx,ooo,hhhh,pppp,rrrrr | N
DC | Ames | 2000B | 1.25 | VU | 1996-10-01 | 2023-10-01 | N | 8 | (vv),xx,ooo,hhhh,pppp,rrrrr | N
DC | Ames | 2000B | 1.5 | H | 1994-05-24 | 2024-05-24 | N | 8 | (vv),xx,ooo,hhhh,pppp,rrrrr | N
DC | Ames | 2000B | 1.5 | VU | 1996-03-11 | 2023-03-11 | N | 8 | (vv),xx,ooo,hhhh,pppp,rrrrr | N
DC | Ames | 2000B | 2 | H | 1992-06-30 | 2022-06-30 | N | 8 | (vv),xx,ooo,hhhh,pppp,rrrrr | N
DC | Ames | 2000B | 2 | VU | 1996-03-08 | 2023-03-08 | N | 8 | (vv),xx,ooo,hhhh,pppp,rrrrr | N
DC | Ames | 2000B-FP | 0.75 | H | 2009-09-01 | 2024-09-01 | N | 9 | (eeeee) | N
DC | Ames | 2000B-FP | 1 | [9 empty] | Model Designation changed to 2000BM1-FP
DC | Ames | 2000B-FP | 1.25 | [9 empty] | Model Designation changed to 2000BM2-FP
DC | Ames | 2000B-FP | 1.5 | [9 empty] | Model Designation changed to 2000BM2-FP
DC | Ames | 2000B-FP | 2 | [9 empty] | Model Designation changed to 2000BM1-FP
DC | Ames | 2000BM1-FP | 1 | H | 2009-09-01 | 2024-09-01 | N | 9 | (eeeee),uuuuuu | N |  |  | formerly Model 2000B-FP. Model Change effective beginning with serial #: 028561
DC | Ames | 2000BM1-FP | 1 | VU | 2017-08-21 | 2023-08-21 | N | 9 | (eeeee),uuuuuu | N
DC | Ames | 2000BM1-FP | 2 | H | 2009-09-01 | 2024-09-01 | N | 9 | (eeeee),uuuuuu | N |  |  | formerly Model 2000B-FP. Model Change effective beginning with serial #: 039123
DC | Ames | 2000BM1-FP | 2 | VU | 2017-08-21 | 2023-08-21 | N | 9 | (eeeee),uuuuuu | N
DC | Ames | 2000BM2-FP | 1.25 | H | 2009-09-01 | 2024-09-01 | N | 9 | (eeeee),uuuuuu | N |  |  | formerly Model 2000B-FP. Model Change effective beginning with serial #: 017727
DC | Ames | 2000BM2-FP | 1.25 | VU | 2017-08-21 | 2023-08-21 | N | 9 | (eeeee),uuuuuu | N
DC | Ames | 2000BM2-FP | 1.5 | H | 2009-09-01 | 2024-09-01 | N | 9 | (eeeee),uuuuuu | N |  |  | formerly Model 2000B-FP. Model Change effective beginning with serial #: 034639
DC | Ames | 2000BM2-FP | 1.5 | VU | 2017-08-21 | 2023-08-21 | N | 9 | (eeeee),uuuuuu | N
DC | Ames | 2000BM3 | 0.75 | H | 2000-03-27 | 2023-03-27 | N | 9 | (vv),xx,ooo,hhhh,pppp,rrrrr | N
DC | Ames | 2000BM3 | 0.75 | VU | 2000-03-27 | 2023-03-27 | N | 9 | (vv),xx,ooo,hhhh,pppp,rrrrr | N
DC | Ames | 2000BM3-FP | 0.75 | H | 2009-09-01 | 2024-09-01 | N | 9 | (eeeee) | N
DC | Ames | 2000CIV | 4 | H | 1982-01-15 | 2024-01-15 | N | 6 | (oo),gg,hh,ll,mm,pp,tt,uu,eee | Y
DC | Ames | 2000CIV | 4 | VU | 1996-03-11 | 2023-03-11 | N | 8 | (oo),gg,hh,ll,mm,pp,tt,uu,eee | Y
DC | Ames | 2000CIV | 6 | H | 1982-05-18 | 2024-05-18 | N | 6 | (oo),gg,hh,ll,mm,pp,tt,uu,eee | Y
DC | Ames | 2000CIV | 6 | VU | 1996-12-05 | 2023-12-05 | N | 8 | (oo),gg,hh,ll,mm,pp,tt,uu,eee | Y
DC | Ames | 2000CIV | 8 | H | 1981-07-06 | 2023-07-06 | N | 6 | (oo),gg,hh,ll,mm,pp,tt,uu,eee | Y
DC | Ames | 2000CIV | 8 | VU | 1996-12-05 | 2023-12-05 | N | 8 | (oo),gg,hh,ll,mm,pp,tt,uu,eee | Y
DC | Ames | 2000CIV | 10 | H | 1983-03-16 | 2022-03-16 | N | 6 | (oo),gg,hh,ll,mm,pp,tt,uu,eee | Y
DC | Ames | 2000CIV | 10 | VU | 1996-12-05 | 2023-12-05 | N | 8 | (oo),gg,hh,ll,mm,pp,tt,uu,eee | Y
DC | Ames | 2000SE | 2.5 | H | 1996-09-10 | 2023-09-10 | N | 8 | (mm),ee,ff,gg,hh,ll,mm,oo,pp,tt,uu,ccc,ddd,ffff,gggg | Y
DC | Ames | 2000SE | 6 | H | 1993-11-22 | 2023-11-22 | N | 8 | tt,ee,ff,gg,hh,ll,mm,oo,pp,uu,ccc,ddd,ffff,gggg | Y
DC | Ames | 2000SE | 8 | H | 1992-09-09 | 2022-09-09 | N | 8 | tt,ee,ff,gg,hh,ll,mm,oo,pp,uu,ccc,ddd,ffff,gggg | Y
DC | Ames | 2000SS | 0.75 | H | 1995-05-05 | 2022-05-05 | N | 8 | ii | Y
DC | Ames | 2000SS | 1 | H | 1995-05-05 | 2022-05-05 | N | 8 | ii | Y
DC | Ames | 2000SS | 1.25 | H | 1995-07-14 | 2022-07-14 | N | 8 | ii | Y
DC | Ames | 2000SS | 1.5 | H | 1995-10-13 | 2022-10-13 | N | 8 | ii | Y
DC | Ames | 2000SS | 2 | H | 1995-10-13 | 2022-10-13 | N | 8 | ii | Y
DC | Ames | 2000SS | 2.5 | H | 1991-07-11 | 2024-07-11 | N | 8 | (tt),ee,ff,gg,hh,pp,uu,ccc,ddd | N
DC | Ames | 2000SS | 2.5 | H | 1991-07-11 | 2024-07-11 | Y | 8 | ll,mm,oo,ffff,gggg | N
DC | Ames | 2000SS | 3 | H | 1991-07-11 | 2024-07-11 | N | 8 | (tt),ee,ff,gg,hh,pp,uu,ccc,ddd | N
DC | Ames | 2000SS | 3 | H | 1991-07-11 | 2024-07-11 | Y | 8 | ll,mm,oo,ffff,gggg | N
DC | Ames | 2000SS | 4 | H | 1991-07-11 | 2024-07-11 | N | 8 | (tt),ee,ff,gg,hh,pp,uu,ccc,ddd | N
DC | Ames | 2000SS | 4 | H | 1991-07-11 | 2024-07-11 | Y | 8 | ll,mm,oo,ffff,gggg | N
DC | Ames | 2000SS | 6 | H | 1992-09-09 | 2022-09-09 | N | 8 | (tt),ee,ff,gg,hh,pp,uu,ccc,ddd | N
DC | Ames | 2000SS | 6 | H | 1992-09-09 | 2022-09-09 | Y | 8 | ll,mm,oo,ffff,gggg | N
DC | Ames | 2000SS | 8 | H | 1996-09-16 | 2023-09-16 | N | 8 | (tt),ee,ff,gg,hh,pp,uu,ccc,ddd | N
DC | Ames | 2000SS | 8 | H | 1996-09-16 | 2023-09-16 | Y | 8 | ll,mm,oo,ffff,gggg | N
DC | Ames | 2000SS | 10 | H | 2001-02-16 | 2022-02-16 | N | 8 | pp, | N
DC | Ames | 2000SS | 10 | H | 2001-02-16 | 2022-02-16 | Y | 8 | (ll),mm,oo | N
DC | Ames | 2000SS | 12 | H | 2009-07-22 | 2024-07-22 | N | 9 | pp, | N
DC | Ames | 2000SS | 12 | H | 2009-07-22 | 2024-07-22 | Y | 9 | (ll),mm,oo | N
DC | Ames | 2000SS | 12 | VU | 2011-02-22 | 2023-02-22 | N | 9 | pp, | N
DC | Ames | 2000SS | 12 | VU | 2011-02-22 | 2023-02-22 | Y | 9 | (ll),mm,oo | N
DC | Ames | 2000SS-M | 4 | H | 1995-05-05 | 2022-05-05 | N | 8 | (tt),ee,ff,gg,hh,ll,mm,oo,pp,uu,ccc,ddd,ffff,gggg | N
DC | Ames | 2000SS-M | 6 | H | 1995-05-05 | 2022-05-05 | N | 8 | (tt),ee,ff,gg,hh,ll,mm,oo,pp,uu,ccc,ddd,ffff,gggg | N
DC | Ames | 200B | 0.5 | H | 2006-04-21 | 2024-04-21 | N | 9 | (vv),xx,ooo,hhhh,pppp,rrrrr | Y
DC | Ames | 200B | 0.5 | VD | 2006-04-21 | 2024-04-21 | N | 9 | (vv),xx,ooo,hhhh,pppp,rrrrr | Y
DC | Ames | 200B | 0.5 | VU | 2006-04-21 | 2024-04-21 | N | 9 | (vv),xx,ooo,hhhh,pppp,rrrrr | Y
DC | Ames | 200B | 0.75 | H | 2006-04-21 | 2024-04-21 | N | 9 | (vv),xx,ooo,hhhh,pppp,rrrrr | Y
DC | Ames | 200B | 0.75 | VD | 2006-04-21 | 2024-04-21 | N | 9 | (vv),xx,ooo,hhhh,pppp,rrrrr | Y
DC | Ames | 200B | 0.75 | VU | 2006-04-21 | 2024-04-21 | N | 9 | (vv),xx,ooo,hhhh,pppp,rrrrr | Y
DC | Ames | 200B | 1 | H | 2006-04-21 | 2024-04-21 | N | 9 | (vv),xx,ooo,hhhh,pppp,rrrrr | Y
DC | Ames | 200B | 1 | VD | 2006-04-21 | 2024-04-21 | N | 9 | (vv),xx,ooo,hhhh,pppp,rrrrr | Y
DC | Ames | 200B | 1 | VU | 2006-04-21 | 2024-04-21 | N | 9 | (vv),xx,ooo,hhhh,pppp,rrrrr | Y
DC | Ames | 200B | 1.25 | H | 2006-04-21 | 2024-04-21 | N | 9 | (vv),xx,ooo,hhhh,pppp,rrrrr | Y
DC | Ames | 200B | 1.25 | VD | 2006-04-21 | 2024-04-21 | N | 9 | (vv),xx,ooo,hhhh,pppp,rrrrr | Y
DC | Ames | 200B | 1.25 | VU | 2006-04-21 | 2024-04-21 | N | 9 | (vv),xx,ooo,hhhh,pppp,rrrrr | Y
DC | Ames | 200B | 1.5 | H | 2006-04-21 | 2024-04-21 | N | 9 | (vv),xx,ooo,hhhh,pppp,rrrrr | Y
DC | Ames | 200B | 1.5 | VD | 2006-04-21 | 2024-04-21 | N | 9 | (vv),xx,ooo,hhhh,pppp,rrrrr | Y
DC | Ames | 200B | 1.5 | VU | 2006-04-21 | 2024-04-21 | N | 9 | (vv),xx,ooo,hhhh,pppp,rrrrr | Y
DC | Ames | 200B | 2 | H | 2006-04-21 | 2024-04-21 | N | 9 | (vv),xx,ooo,hhhh,pppp,rrrrr | Y
DC | Ames | 200B | 2 | VD | 2006-04-21 | 2024-04-21 | N | 9 | (vv),xx,ooo,hhhh,pppp,rrrrr | Y
DC | Ames | 200B | 2 | VU | 2006-04-21 | 2024-04-21 | N | 9 | (vv),xx,ooo,hhhh,pppp,rrrrr | Y
DC | Ames | 200B R10 | 0.5 | H | 2006-04-21 | 2024-04-21 | N | 9 | (vv),xx,ooo,hhhh,pppp,rrrrr | Y
DC | Ames | 200B R10 | 0.5 | VD | 2006-04-21 | 2024-04-21 | N | 9 | (vv),xx,ooo,hhhh,pppp,rrrrr | Y
DC | Ames | 200B R10 | 0.5 | VU | 2006-04-21 | 2024-04-21 | N | 9 | (vv),xx,ooo,hhhh,pppp,rrrrr | Y
DC | Ames | 200B R10 | 0.75 | H | 2006-04-21 | 2024-04-21 | N | 9 | (vv),xx,ooo,hhhh,pppp,rrrrr | Y
DC | Ames | 200B R10 | 0.75 | VD | 2006-04-21 | 2024-04-21 | N | 9 | (vv),xx,ooo,hhhh,pppp,rrrrr | Y
DC | Ames | 200B R10 | 0.75 | VU | 2006-04-21 | 2024-04-21 | N | 9 | (vv),xx,ooo,hhhh,pppp,rrrrr | Y
DC | Ames | 200B-A | 0.5 | VUVD | 2006-04-21 | 2024-04-21 | N | 9 | (vv),xx,ooo,hhhh,pppp,rrrrr | Y
DC | Ames | 200B-A | 1 | VUVD | 2006-04-21 | 2024-04-21 | N | 9 | (vv),xx,ooo,hhhh,pppp,rrrrr | Y
DC | Ames | 200B-A | 1.25 | VUVD | 2006-04-21 | 2024-04-21 | N | 9 | (vv),xx,ooo,hhhh,pppp,rrrrr | Y
DC | Ames | 200B-A | 1.5 | VUVD | 2006-04-21 | 2024-04-21 | N | 9 | (vv),xx,ooo,hhhh,pppp,rrrrr | Y
DC | Ames | 200B-A | 2 | VUVD | 2006-04-21 | 2024-04-21 | N | 9 | (vv),xx,ooo,hhhh,pppp,rrrrr | Y
DC | Ames | 200B-AR10 | 0.5 | VUVD | 2013-07-03 | 2022-07-03 | N | 9 | (vv),xx,ooo,hhhh,pppp,rrrrr | Y
DC | Ames | 200B-AR10 | 0.75 | VUVD | 2013-07-03 | 2022-07-03 | N | 9 | (vv),xx,ooo,hhhh,pppp,rrrrr | Y
DC | Ames | Colt 200 | 2.5 | H | 2004-07-20 | 2022-07-20 | N | 9 | (ppp),qqq,nnnnn | N
DC | Ames | Colt 200 | 2.5 | H | 2004-07-20 | 2022-07-20 | Y | 9 | yyy,zzz,dddd,eeee,dddd,gggg,kkkk,llll,mmmm,nnnn | N
DC | Ames | Colt 200 | 2.5 | VU | 2004-07-20 | 2022-07-20 | N | 9 | (ppp),qqq,nnnnn | N
DC | Ames | Colt 200 | 2.5 | VU | 2004-07-20 | 2022-07-20 | Y | 9 | yyy,zzz,dddd,eeee,dddd,gggg,kkkk,llll,mmmm,nnnn | N
DC | Ames | Colt 200 | 3 | H | 2004-07-20 | 2022-07-20 | N | 9 | (ppp),qqq,nnnnn | N
DC | Ames | Colt 200 | 3 | H | 2004-07-20 | 2022-07-20 | Y | 9 | yyy,zzz,dddd,eeee,dddd,gggg,kkkk,llll,mmmm,nnnn | N
DC | Ames | Colt 200 | 3 | VU | 2004-07-20 | 2022-07-20 | N | 9 | (ppp),qqq,nnnnn | N
DC | Ames | Colt 200 | 3 | VU | 2004-07-20 | 2022-07-20 | Y | 9 | yyy,zzz,dddd,eeee,dddd,gggg,kkkk,llll,mmmm,nnnn | N
DC | Ames | Colt 200 | 4 | H | 2004-07-20 | 2022-07-20 | N | 9 | (ppp),qqq,nnnnn | N
DC | Ames | Colt 200 | 4 | H | 2004-07-20 | 2022-07-20 | Y | 9 | yyy,zzz,dddd,eeee,dddd,gggg,kkkk,llll,mmmm,nnnn | N
DC | Ames | Colt 200 | 4 | VU | 2004-07-20 | 2022-07-20 | N | 9 | (ppp),qqq,nnnnn | N
DC | Ames | Colt 200 | 4 | VU | 2004-07-20 | 2022-07-20 | Y | 9 | yyy,zzz,dddd,eeee,dddd,gggg,kkkk,llll,mmmm,nnnn | N
DC | Ames | Colt 200 | 6 | H | 2006-04-21 | 2024-04-21 | N | 9 | (ppp),qqq,aaaa,bbbb,nnnnn | N
DC | Ames | Colt 200 | 6 | H | 2006-04-21 | 2024-04-21 | Y | 9 | yyy,zzz,dddd,eeee,ffff,gggg,kkkk,llll,mmmm,nnnn | N
DC | Ames | Colt 200 | 6 | VU | 2006-04-21 | 2024-04-21 | N | 9 | (ppp),qqq,aaaa,bbbb,nnnnn | N
DC | Ames | Colt 200 | 6 | VU | 2006-04-21 | 2024-04-21 | Y | 9 | yyy,zzz,dddd,eeee,ffff,gggg,kkkk,llll,mmmm,nnnn | N
DC | Ames | Colt 200 | 8 | H | 2004-08-11 | 2022-08-11 | N | 9 | ppp,qqq,aaaa,bbbb,nnnnn | N
DC | Ames | Colt 200 | 8 | H | 2004-08-11 | 2022-08-11 | Y | 9 | (yyy),zzz,dddd,eeee,gggg,kkkk,llll,mmmm,nnnn | N
DC | Ames | Colt 200 | 8 | VU | 2006-02-10 | 2024-02-10 | N | 9 | ppp,qqq,aaaa,bbbb,nnnnn | N
DC | Ames | Colt 200 | 8 | VU | 2006-02-10 | 2024-02-10 | Y | 9 | (yyy),zzz,dddd,eeee,gggg,kkkk,llll,mmmm,nnnn | N
DC | Ames | Colt 200 | 10 | H | 2008-05-02 | 2023-05-02 | N | 9 | ppp,qqq,aaaa,bbbb | N
DC | Ames | Colt 200 | 10 | H | 2008-05-02 | 2023-05-02 | Y | 9 | yyy,zzz,dddd,eeee,ggg,kkkk,llll,mmmm,nnnn | N
DC | Ames | Colt 200 | 10 | VU | 2008-05-02 | 2023-05-02 | N | 9 | (ppp),qqq,aaaa,bbbb | N
DC | Ames | Colt 200 | 10 | VU | 2014-12-05 | 2023-12-05 | Y | 9 | yyy,zzz,dddd,eeee,ggg,kkkk,llll,mmmm,nnnn | N
DC | Ames | Colt 200a | 2.5 | H | 2002-10-07 | 2023-10-07 | N | 9 | (ppp),fff,qqq,yyy,zzz,aaaa,bbbb,dddd,eeee,gggg,kkkk,llll,mmmm,nnnn,nnnnn | Y
DC | Ames | Colt 200a | 2.5 | VU | 2002-10-07 | 2023-10-07 | N | 9 | (ppp),qqq,yyy,zzz,aaaa,bbbb,dddd,eeee,ffff,gggg,kkkk,llll,mmmm,nnnn,nnnnn | Y
DC | Ames | Colt 200a | 3 | H | 2002-10-07 | 2023-10-07 | N | 9 | (ppp),qqq,yyy,zzz,aaaa,bbbb,dddd,eeee,ffff,gggg,kkkk,llll,mmmm,nnnn,nnnnn | Y
DC | Ames | Colt 200a | 3 | VU | 2002-10-07 | 2023-10-07 | N | 9 | (ppp),qqq,yyy,zzz,aaaa,bbbb,dddd,eeee,ffff,gggg,kkkk,llll,mmmm,nnnn,nnnnn | Y
DC | Ames | Colt 200a | 4 | H | 2002-10-07 | 2023-10-07 | N | 9 | (ppp),qqq,yyy,zzz,aaaa,bbbb,dddd,eeee,ffff,gggg,kkkk,llll,mmmm,nnnn,nnnnn | Y
DC | Ames | Colt 200a | 4 | VU | 2002-10-07 | 2023-10-07 | N | 9 | (ppp),qqq,yyy,zzz,aaaa,bbbb,dddd,eeee,ffff,gggg,kkkk,llll,mmmm,nnnn,nnnnn | Y
DC | Ames | Colt 200a | 6 | H | 2003-07-03 | 2024-07-03 | N | 9 | (ppp),qqq,yyy,zzz,aaaa,bbbb,dddd,eeee,ffff,gggg,kkkk,llll,mmmm,nnnn,nnnnn | Y
DC | Ames | Colt 200a | 6 | VU | 2003-07-03 | 2024-07-03 | N | 9 | (ppp),qqq,yyy,zzz,aaaa,bbbb,dddd,eeee,ffff,gggg,kkkk,llll,mmmm,nnnn,nnnnn | Y
DC | Ames | Colt 200N | 2.5 | VUVD | 2009-04-07 | 2024-04-07 | N | 9 | (ppp),qqq,nnnnn | N
DC | Ames | Colt 200N | 2.5 | VUVD | 2009-04-07 | 2024-04-07 | Y | 9 | yyy,zzz,dddd,eeee,dddd,gggg,kkkk,llll,mmmm,nnnn | N
DC | Ames | Colt 200N | 3 | VUVD | 2009-04-07 | 2024-04-07 | N | 9 | (ppp),qqq,nnnnn | N
DC | Ames | Colt 200N | 3 | VUVD | 2009-04-07 | 2024-04-07 | Y | 9 | yyy,zzz,dddd,eeee,dddd,gggg,kkkk,llll,mmmm,nnnn | N
DC | Ames | Colt 200N | 4 | VUVD | 2009-04-07 | 2024-04-07 | N | 9 | (ppp),qqq,nnnnn | N
DC | Ames | Colt 200N | 4 | VUVD | 2009-04-07 | 2024-04-07 | Y | 9 | yyy,zzz,dddd,eeee,dddd,gggg,kkkk,llll,mmmm,nnnn | N
DC | Ames | Colt 200N | 6 | VUVD | 2009-04-07 | 2024-04-07 | N | 9 | (ppp),qqq,nnnnn | N
DC | Ames | Colt 200N | 6 | VUVD | 2009-04-07 | 2024-04-07 | Y | 9 | yyy,zzz,dddd,eeee,dddd,gggg,kkkk,llll,mmmm,nnnn | N
DC | Ames | Colt 200N | 8 | VUVD | 2013-01-03 | 2022-01-03 | N | 9 | ppp,qqq,aaaa,bbbb | N
DC | Ames | Colt 200N | 8 | VUVD | 2013-01-03 | 2022-01-03 | Y | 9 | yyy, zzz,dddd,eeee,gggg,kkkk,llll,mmmm,nnnn | N
DC | Ames | Colt 200N | 10 | VUVD | 2009-09-01 | 2024-09-01 | N | 9 | (ppp),qqq | N
DC | Ames | Colt 200N | 10 | VUVD | 2009-09-01 | 2024-09-01 | Y | 9 | yyy,zzz,dddd,eeee,dddd,gggg,kkkk,llll,mmmm,nnnn | N
DC | Ames | Colt 200Na | 2.5 | VUVD | 2003-03-20 | 2024-03-20 | N | 9 | (ppp),qqq,yyy,zzz,aaaa,bbbb,dddd,eeee,ffff,gggg,kkkk,llll,mmmm,nnnn,nnnnn | Y
DC | Ames | Colt 200Na | 3 | VUVD | 2003-03-20 | 2024-03-20 | N | 9 | (ppp),qqq,yyy,zzz,aaaa,bbbb,dddd,eeee,ffff,gggg,kkkk,llll,mmmm,nnnn,nnnnn | Y
DC | Ames | Colt 200Na | 4 | VUVD | 2003-03-20 | 2024-03-20 | N | 9 | (ppp),qqq,yyy,zzz,aaaa,bbbb,dddd,eeee,ffff,gggg,kkkk,llll,mmmm,nnnn,nnnnn | Y
DC | Ames | Colt 200Na | 6 | VUVD | 2003-07-03 | 2024-07-03 | N | 9 | (ppp),qqq,yyy,zzz,aaaa,bbbb,dddd,eeee,ffff,gggg,kkkk,llll,mmmm,nnnn,nnnnn | Y
DC | Ames | DC | 4 | H | 1985-06-14 | 2024-06-14 | N | 6 | oo,pp,ffff,gggg | Y
DC | Ames | DC | 6 | H | 1985-06-14 | 2024-06-14 | N | 6 | oo,pp,ffff,gggg | Y
DC | Ames | DC | 8 | H | 1987-08-04 | 2023-08-04 | N | 7 | oo,pp,ffff,gggg | Y
DC | Ames | DC | 10 | [9 empty] | model designation changed to 2000-DC
DC | Ames | DC | 10 | [9 empty] | model designation changed to 2000-G-DC
DC | Ames | DCA | 4 | [9 empty] | model designation changed to 2000-DCA
DC | Ames | DCA | 4 | [9 empty] | model designation changed to 2000-G-DCA
DC | Ames | DCA | 6 | [9 empty] | model designation changed to 2000-DCA
DC | Ames | DCA | 6 | [9 empty] | model designation changed to 2000-G-DCA
DC | Ames | DCA | 8 | [9 empty] | model designation changed to 2000-DCA
DC | Ames | DCA | 8 | [9 empty] | model designation changed to 2000-G-DCA
DC | Ames | Deringer 20 | 2.5 | H | 2020-03-26 | 2023-03-26 | Y | 10 | (int) | N
DC | Ames | Deringer 20 | 2.5 | VU | 2020-03-26 | 2023-03-26 | Y | 10 | (int) | N
DC | Ames | Deringer 20 | 3 | H | 2020-03-26 | 2023-03-26 | Y | 10 | (int) | N
DC | Ames | Deringer 20 | 3 | VU | 2020-03-26 | 2023-03-26 | Y | 10 | (int) | N
DC | Ames | Deringer 20 | 4 | H | 2020-03-26 | 2023-03-26 | Y | 10 | (int) | N
DC | Ames | Deringer 20 | 4 | VU | 2020-03-26 | 2023-03-26 | Y | 10 | (int) | N
DC | Ames | Deringer 20 | 6 | H | 2020-03-26 | 2023-03-26 | Y | 10 | (int) | N
DC | Ames | Deringer 20 | 6 | VU | 2020-03-26 | 2023-03-26 | Y | 10 | (int) | N
DC | Ames | Deringer 20 | 8 | H | 2020-03-26 | 2023-03-26 | Y | 10 | (int) | N
DC | Ames | Deringer 20 | 8 | VU | 2020-03-26 | 2023-03-26 | Y | 10 | (int) | N
DC | Ames | Deringer 20G | 2.5 | H | 2020-03-26 | 2023-03-26 | Y | 10 | (ssssss), tttttt | N
DC | Ames | Deringer 20G | 2.5 | VU | 2020-03-26 | 2023-03-26 | Y | 10 | (ssssss), tttttt | N
DC | Ames | Deringer 20G | 3 | H | 2020-03-26 | 2023-03-26 | Y | 10 | (ssssss), tttttt | N
DC | Ames | Deringer 20G | 3 | VU | 2020-03-26 | 2023-03-26 | Y | 10 | (ssssss), tttttt | N
DC | Ames | Deringer 20G | 4 | H | 2020-03-26 | 2023-03-26 | Y | 10 | (ssssss), tttttt | N
DC | Ames | Deringer 20G | 4 | VU | 2020-03-26 | 2023-03-26 | Y | 10 | (ssssss), tttttt | N
DC | Ames | Deringer 20G | 6 | H | 2020-03-26 | 2023-03-26 | Y | 10 | (ssssss), tttttt | N
DC | Ames | Deringer 20G | 6 | VU | 2020-03-26 | 2023-03-26 | Y | 10 | (ssssss), tttttt | N
DC | Ames | Deringer 20G | 8 | H | 2020-03-26 | 2023-03-26 | Y | 10 | (ssssss), tttttt | N
DC | Ames | Deringer 20G | 8 | VU | 2020-03-26 | 2023-03-26 | Y | 10 | (ssssss), tttttt | N
DC | Ames | Deringer 20GX | 4 | H | 2020-03-26 | 2023-03-26 | Y | 10 | (ssssss), tttttt | N
DC | Ames | Deringer 20GX | 4 | VU | 2020-03-26 | 2023-03-26 | Y | 10 | (ssssss), tttttt | N
DC | Ames | Deringer 20GX | 6 | H | 2020-03-26 | 2023-03-26 | Y | 10 | (ssssss), tttttt | N
DC | Ames | Deringer 20GX | 6 | VU | 2020-03-26 | 2023-03-26 | Y | 10 | (ssssss), tttttt | N
DC | Ames | Deringer 20X | 4 | H | 2020-03-26 | 2023-03-26 | Y | 10 | (int) | N
DC | Ames | Deringer 20X | 4 | VU | 2020-03-26 | 2023-03-26 | Y | 10 | (int) | N
DC | Ames | Deringer 20X | 6 | H | 2020-03-26 | 2023-03-26 | Y | 10 | (int) | N
DC | Ames | Deringer 20X | 6 | VU | 2020-03-26 | 2023-03-26 | Y | 10 | (int) | N
DC | Ames | LF2000B | 0.5 | H | 2013-09-25 | 2022-09-25 | Y | 9 | (hhhh) | N
DC | Ames | LF2000B | 0.5 | VU | 2013-09-25 | 2022-09-25 | Y | 9 | (hhhh) | N
DC | Ames | LF2000BM1 | 1 | H | 2013-09-25 | 2022-09-25 | Y | 9 | (hhhh) | N
DC | Ames | LF2000BM1 | 1 | VU | 2013-09-25 | 2022-09-25 | Y | 9 | (hhhh) | N
DC | Ames | LF2000BM1 | 2 | H | 2013-09-25 | 2022-09-25 | Y | 9 | (hhhh) | N
DC | Ames | LF2000BM1 | 2 | VU | 2013-09-25 | 2022-09-25 | Y | 9 | (hhhh) | N
DC | Ames | LF2000BM1-FP | 1 | H | 2019-03-12 | 2022-03-12 | Y | 9 | (eeeee),uuuuuu | N
DC | Ames | LF2000BM1-FP | 1 | VU | 2019-03-12 | 2022-03-12 | Y | 9 | (eeeee),uuuuuu | N
DC | Ames | LF2000BM1-FP | 2 | H | 2019-03-12 | 2022-03-12 | Y | 9 | (eeeee),uuuuuu | N
DC | Ames | LF2000BM1-FP | 2 | VU | 2019-03-12 | 2022-03-12 | Y | 9 | (eeeee),uuuuuu | N
DC | Ames | LF2000BM2 | 1.25 | H | 2013-09-25 | 2022-09-25 | Y | 8 | (hhhh) | N
DC | Ames | LF2000BM2 | 1.25 | VU | 2013-09-25 | 2022-09-25 | Y | 8 | (hhhh) | N
DC | Ames | LF2000BM2 | 1.5 | H | 2013-09-25 | 2022-09-25 | Y | 8 | (hhhh) | N
DC | Ames | LF2000BM2 | 1.5 | VU | 2013-09-25 | 2022-09-25 | Y | 8 | (hhhh) | N
DC | Ames | LF2000BM2-FP | 1.25 | H | 2019-03-12 | 2022-03-12 | Y | 9 | (eeeee),uuuuuu | N
DC | Ames | LF2000BM2-FP | 1.25 | VU | 2019-03-12 | 2022-03-12 | Y | 9 | (eeeee),uuuuuu | N
DC | Ames | LF2000BM2-FP | 1.5 | H | 2019-03-12 | 2022-03-12 | Y | 9 | (eeeee),uuuuuu | N
DC | Ames | LF2000BM2-FP | 1.5 | VU | 2019-03-12 | 2022-03-12 | Y | 9 | (eeeee),uuuuuu | N
DC | Ames | LF2000BM3 | 0.75 | H | 2013-09-25 | 2022-09-25 | Y | 9 | (hhhh) | N
DC | Ames | LF2000BM3 | 0.75 | VU | 2013-09-25 | 2022-09-25 | Y | 9 | (hhhh) | N
DC | Ames | LF200B | 0.5 | H | 2013-07-03 | 2022-07-03 | Y | 9 | (hhhh) | Y
DC | Ames | LF200B | 0.5 | VD | 2013-07-03 | 2022-07-03 | Y | 9 | (hhhh) | Y
DC | Ames | LF200B | 0.5 | VU | 2013-07-03 | 2022-07-03 | Y | 9 | (hhhh) | Y
DC | Ames | LF200B | 0.75 | H | 2013-07-03 | 2022-07-03 | Y | 9 | (hhhh) | Y
DC | Ames | LF200B | 0.75 | VD | 2013-07-03 | 2022-07-03 | Y | 9 | (hhhh) | Y
DC | Ames | LF200B | 0.75 | VU | 2013-07-03 | 2022-07-03 | Y | 9 | (hhhh) | Y
DC | Ames | LF200B | 1 | H | 2006-06-14 | 2024-06-14 | N | 9 | (vv),xx,ooo,hhhh,pppp,rrrrr | Y
DC | Ames | LF200B | 1 | VD | 2006-06-14 | 2024-06-14 | N | 9 | (vv),xx,ooo,hhhh,pppp,rrrrr | Y
DC | Ames | LF200B | 1 | VU | 2006-06-14 | 2024-06-14 | N | 9 | (vv),xx,ooo,hhhh,pppp,rrrrr | Y
DC | Ames | LF200B | 1.25 | H | 2006-06-14 | 2024-06-14 | N | 9 | (vv),xx,ooo,hhhh,pppp,rrrrr | Y
DC | Ames | LF200B | 1.25 | VD | 2006-06-14 | 2024-06-14 | N | 9 | (vv),xx,ooo,hhhh,pppp,rrrrr | Y
DC | Ames | LF200B | 1.25 | VU | 2006-06-14 | 2024-06-14 | N | 9 | (vv),xx,ooo,hhhh,pppp,rrrrr | Y
DC | Ames | LF200B | 1.5 | H | 2006-06-14 | 2024-06-14 | N | 9 | (vv),xx,ooo,hhhh,pppp,rrrrr | Y
DC | Ames | LF200B | 1.5 | VD | 2006-06-14 | 2024-06-14 | N | 9 | (vv),xx,ooo,hhhh,pppp,rrrrr | Y
DC | Ames | LF200B | 1.5 | VU | 2006-06-14 | 2024-06-14 | N | 9 | (vv),xx,ooo,hhhh,pppp,rrrrr | Y
DC | Ames | LF200B | 2 | H | 2006-06-14 | 2024-06-14 | N | 9 | (vv),xx,ooo,hhhh,pppp,rrrrr | Y
DC | Ames | LF200B | 2 | VD | 2006-06-14 | 2024-06-14 | N | 9 | (vv),xx,ooo,hhhh,pppp,rrrrr | Y
DC | Ames | LF200B | 2 | VU | 2006-06-14 | 2024-06-14 | N | 9 | (vv),xx,ooo,hhhh,pppp,rrrrr | Y
DC | Ames | LF200B R10 | 0.5 | H | 2006-06-14 | 2024-06-14 | N | 9 | (vv),xx,ooo,hhhh,pppp,rrrrr | Y
DC | Ames | LF200B R10 | 0.5 | VD | 2006-06-14 | 2024-06-14 | N | 9 | (vv),xx,ooo,hhhh,pppp,rrrrr | Y
DC | Ames | LF200B R10 | 0.5 | VU | 2006-06-14 | 2024-06-14 | N | 9 | (vv),xx,ooo,hhhh,pppp,rrrrr | Y
DC | Ames | LF200B R10 | 0.75 | H | 2006-06-14 | 2024-06-14 | N | 9 | (vv),xx,ooo,hhhh,pppp,rrrrr | Y
DC | Ames | LF200B R10 | 0.75 | VD | 2006-06-14 | 2024-06-14 | N | 9 | (vv),xx,ooo,hhhh,pppp,rrrrr | Y
DC | Ames | LF200B R10 | 0.75 | VU | 2006-06-14 | 2024-06-14 | N | 9 | (vv),xx,ooo,hhhh,pppp,rrrrr | Y
DC | Ames | LF200B-A | 1 | VUVD | 2006-06-14 | 2024-06-14 | N | 9 | (vv),xx,ooo,hhhh,pppp,rrrrr | Y
DC | Ames | LF200B-A | 1.25 | VUVD | 2006-06-14 | 2024-06-14 | N | 9 | (vv),xx,ooo,hhhh,pppp,rrrrr | Y
DC | Ames | LF200B-A | 1.5 | VUVD | 2006-06-14 | 2024-06-14 | N | 9 | (vv),xx,ooo,hhhh,pppp,rrrrr | Y
DC | Ames | LF200B-A | 2 | VUVD | 2006-06-14 | 2024-06-14 | N | 9 | (vv),xx,ooo,hhhh,pppp,rrrrr | Y
DC | Ames | LFU200B | 1 | H | 2006-06-14 | 2024-06-14 | N | 9 | (vv),xx,ooo,hhhh,pppp | Y
DC | Ames | LFU200B | 1 | VD | 2006-06-14 | 2024-06-14 | N | 9 | (vv),xx,ooo,hhhh,pppp | Y
DC | Ames | LFU200B | 1 | VU | 2006-06-14 | 2024-06-14 | N | 9 | (vv),xx,ooo,hhhh,pppp | Y
DC | Ames | LFU200B | 1.25 | H | 2006-06-14 | 2024-06-14 | N | 9 | (vv),xx,ooo,hhhh,pppp | Y
DC | Ames | LFU200B | 1.25 | VD | 2006-06-14 | 2024-06-14 | N | 9 | (vv),xx,ooo,hhhh,pppp | Y
DC | Ames | LFU200B | 1.25 | VU | 2006-06-14 | 2024-06-14 | N | 9 | (vv),xx,ooo,hhhh,pppp | Y
DC | Ames | LFU200B | 1.5 | H | 2006-06-14 | 2024-06-14 | N | 9 | (vv),xx,ooo,hhhh,pppp | Y
DC | Ames | LFU200B | 1.5 | VD | 2006-06-14 | 2024-06-14 | N | 9 | (vv),xx,ooo,hhhh,pppp | Y
DC | Ames | LFU200B | 1.5 | VU | 2006-06-14 | 2024-06-14 | N | 9 | (vv),xx,ooo,hhhh,pppp | Y
DC | Ames | LFU200B | 2 | H | 2006-06-14 | 2024-06-14 | N | 9 | (vv),xx,ooo,hhhh,pppp | Y
DC | Ames | LFU200B | 2 | VD | 2006-06-14 | 2024-06-14 | N | 9 | (vv),xx,ooo,hhhh,pppp | Y
DC | Ames | LFU200B | 2 | VU | 2006-06-14 | 2024-06-14 | N | 9 | (vv),xx,ooo,hhhh,pppp | Y
DC | Ames | Maxim 200 | 2.5 | H | 2004-07-20 | 2022-07-20 | N | 9 | (ppp),qqq,nnnnn | N
DC | Ames | Maxim 200 | 2.5 | H | 2004-07-20 | 2022-07-20 | Y | 9 | yyy,dddd,eeee,gggg,kkkk,llll,mmmm,nnnn | N
DC | Ames | Maxim 200 | 2.5 | VU | 2004-07-20 | 2022-07-20 | N | 9 | (ppp),qqq,nnnnn | N
DC | Ames | Maxim 200 | 2.5 | VU | 2004-07-20 | 2022-07-20 | Y | 9 | yyy,dddd,eeee,gggg,kkkk,llll,mmmm,nnnn | N
DC | Ames | Maxim 200 | 3 | H | 2004-07-20 | 2022-07-20 | N | 9 | (ppp),qqq,nnnnn | N
DC | Ames | Maxim 200 | 3 | H | 2004-07-20 | 2022-07-20 | Y | 9 | yyy,dddd,eeee,gggg,kkkk,llll,mmmm,nnnn | N
DC | Ames | Maxim 200 | 3 | VU | 2004-07-20 | 2022-07-20 | N | 9 | (ppp),qqq,nnnnn | N
DC | Ames | Maxim 200 | 3 | VU | 2004-07-20 | 2022-07-20 | Y | 9 | yyy,dddd,eeee,gggg,kkkk,llll,mmmm,nnnn | N
DC | Ames | Maxim 200 | 4 | H | 2006-04-21 | 2024-04-21 | N | 9 | (ppp),qqq,aaaa,bbbb,nnnnn | N
DC | Ames | Maxim 200 | 4 | H | 2006-04-21 | 2024-04-21 | Y | 9 | yyy,zzz,dddd,eeee,gggg,kkkk,llll,mmmm,nnnn | N
DC | Ames | Maxim 200 | 4 | VU | 2006-04-21 | 2024-04-21 | N | 9 | (ppp),qqq,aaaa,bbbb,nnnnn | N
DC | Ames | Maxim 200 | 4 | VU | 2006-04-21 | 2024-04-21 | Y | 9 | yyy,zzz,dddd,eeee,gggg,kkkk,llll,mmmm,nnnn | N
DC | Ames | Maxim 200 | 6 | H | 2004-08-11 | 2022-08-11 | N | 9 | ppp,qqq,aaaa,bbbb,nnnnn | N
DC | Ames | Maxim 200 | 6 | H | 2004-08-11 | 2022-08-11 | Y | 9 | (yyy),zzz,dddd,eeee,gggg,kkkk,llll,mmmm,nnnn | N
DC | Ames | Maxim 200 | 6 | VU | 2006-02-10 | 2024-02-10 | N | 9 | ppp,qqq,aaaa,bbbb,nnnnn | N
DC | Ames | Maxim 200 | 6 | VU | 2006-02-10 | 2024-02-10 | Y | 9 | (yyy),zzz,dddd,eeee,gggg,kkkk,llll,mmmm,nnnn | N
DC | Ames | Maxim 200 | 8 | H | 2008-05-02 | 2023-05-02 | N | 9 | ppp,qqq,aaaa,bbbb,nnnnn | N
DC | Ames | Maxim 200 | 8 | H | 2008-05-02 | 2023-05-02 | Y | 9 | (yyy),zzz,dddd,eeee,gggg | N
DC | Ames | Maxim 200 | 8 | VU | 2008-05-02 | 2023-05-02 | N | 9 | ppp,qqq,aaaa,bbbb,nnnnn | N
DC | Ames | Maxim 200 | 8 | VU | 2008-05-02 | 2023-05-02 | Y | 9 | (yyy),zzz,dddd,eeee,gggg | N
DC | Ames | Maxim 200 | 10 | H | 2008-10-20 | 2023-10-20 | N | 9 | (ppp),qqq,aaaa,bbbb | N
DC | Ames | Maxim 200 | 10 | H | 2008-10-20 | 2023-10-20 | Y | 9 | yyy,zzz,dddd,eeee,gggg | N
DC | Ames | Maxim 200 | 10 | VU | 2008-10-20 | 2023-10-20 | N | 9 | (ppp),qqq,aaaa,bbbb | N
DC | Ames | Maxim 200 | 10 | VU | 2008-10-20 | 2023-10-20 | Y | 9 | yyy,zzz,dddd,eeee,gggg | N
DC | Ames | Maxim 200a | 2.5 | H | 2002-10-07 | 2023-10-07 | N | 9 | (yyy),ppp,qqq,zzz,aaaa,bbbb,dddd,eeee,gggg,nnnnn | Y
DC | Ames | Maxim 200a | 2.5 | VU | 2002-10-07 | 2023-10-07 | N | 9 | (yyy),ppp,qqq,zzz,aaaa,bbbb,dddd,eeee,gggg,nnnnn | Y
DC | Ames | Maxim 200a | 3 | H | 2002-10-07 | 2023-10-07 | N | 9 | (yyy),ppp,qqq,zzz,aaaa,bbbb,dddd,eeee,gggg,nnnnn | Y
DC | Ames | Maxim 200a | 3 | VU | 2002-10-07 | 2023-10-07 | N | 9 | (yyy),ppp,qqq,zzz,aaaa,bbbb,dddd,eeee,gggg,nnnnn | Y
DC | Ames | Maxim 200a | 4 | H | 2003-07-03 | 2024-07-03 | N | 9 | (yyy),ppp,qqq,zzz,aaaa,bbbb,dddd,eeee,gggg,nnnnn | Y
DC | Ames | Maxim 200a | 4 | VU | 2003-07-03 | 2024-07-03 | N | 9 | (yyy),ppp,qqq,zzz,aaaa,bbbb,dddd,eeee,gggg,nnnnn | Y
DC | Ames | Maxim 200N | 2.5 | VUVD | 2009-04-07 | 2024-04-07 | N | 9 | (ppp),qqq,nnnnn | N
DC | Ames | Maxim 200N | 2.5 | VUVD | 2009-04-07 | 2024-04-07 | Y | 9 | yyy,zzz,dddd,eeee,dddd,gggg,kkkk,llll,mmmm,nnnn | N
DC | Ames | Maxim 200N | 3 | VUVD | 2009-04-07 | 2024-04-07 | N | 9 | (ppp),qqq,nnnnn | N
DC | Ames | Maxim 200N | 3 | VUVD | 2009-04-07 | 2024-04-07 | Y | 9 | yyy,zzz,dddd,eeee,dddd,gggg,kkkk,llll,mmmm,nnnn | N
DC | Ames | Maxim 200N | 4 | VUVD | 2009-04-07 | 2024-04-07 | N | 9 | (ppp),qqq,nnnnn | N
DC | Ames | Maxim 200N | 4 | VUVD | 2009-04-07 | 2024-04-07 | Y | 9 | yyy,zzz,dddd,eeee,dddd,gggg,kkkk,llll,mmmm,nnnn | N
DC | Ames | Maxim 200N | 6 | VUVD | 2013-01-03 | 2022-01-03 | N | 9 | ppp,qqq,aaaa,bbbb | N
DC | Ames | Maxim 200N | 6 | VUVD | 2013-01-03 | 2022-01-03 | Y | 9 | yyy,zzz,dddd,eeee,gggg,kkkk,llll,mmmm,nnnn | N
DC | Ames | Maxim 200N | 8 | VUVD | 2009-09-01 | 2024-09-01 | N | 9 | (ppp),qqq,nnnnn | N
DC | Ames | Maxim 200N | 8 | VUVD | 2009-09-01 | 2024-09-01 | Y | 9 | yyy,zzz,dddd,eeee,gggg,kkkk,llll,mmmm,nnnn | N
DC | Ames | Maxim 200Na | 2.5 | VUVD | 2003-03-20 | 2024-03-20 | N | 9 | (yyy),ppp,qqq,zzz,aaaa,bbbb,dddd,eeee,gggg,nnnnn | Y
DC | Ames | Maxim 200Na | 3 | VUVD | 2003-03-20 | 2024-03-20 | N | 9 | (yyy),ppp,qqq,zzz,aaaa,bbbb,dddd,eeee,gggg,nnnnn | Y
DC | Ames | Maxim 200Na | 4 | VUVD | 2003-07-03 | 2024-07-03 | N | 9 | (yyy),ppp,qqq,zzz,aaaa,bbbb,dddd,eeee,gggg,nnnnn | Y
DC | Ames | U200B | 1 | H | 2006-04-21 | 2024-04-21 | N | 9 | (vv),xx,ooo,hhhh,pppp | Y
DC | Ames | U200B | 1 | VD | 2006-04-21 | 2024-04-21 | N | 9 | (vv),xx,ooo,hhhh,pppp | Y
DC | Ames | U200B | 1 | VU | 2006-04-21 | 2024-04-21 | N | 9 | (vv),xx,ooo,hhhh,pppp | Y
DC | Ames | U200B | 1.25 | H | 2006-04-21 | 2024-04-21 | N | 9 | (vv),xx,ooo,hhhh,pppp | Y
DC | Ames | U200B | 1.25 | VD | 2006-04-21 | 2024-04-21 | N | 9 | (vv),xx,ooo,hhhh,pppp | Y
DC | Ames | U200B | 1.25 | VU | 2006-04-21 | 2024-04-21 | N | 9 | (vv),xx,ooo,hhhh,pppp | Y
DC | Ames | U200B | 1.5 | H | 2006-04-21 | 2024-04-21 | N | 9 | (vv),xx,ooo,hhhh,pppp | Y
DC | Ames | U200B | 1.5 | VD | 2006-04-21 | 2024-04-21 | N | 9 | (vv),xx,ooo,hhhh,pppp | Y
DC | Ames | U200B | 1.5 | VU | 2006-04-21 | 2024-04-21 | N | 9 | (vv),xx,ooo,hhhh,pppp | Y
DC | Ames | U200B | 2 | H | 2006-04-21 | 2024-04-21 | N | 9 | (vv),xx,ooo,hhhh,pppp | Y
DC | Ames | U200B | 2 | VD | 2006-04-21 | 2024-04-21 | N | 9 | (vv),xx,ooo,hhhh,pppp | Y
DC | Ames | U200B | 2 | VU | 2006-04-21 | 2024-04-21 | N | 9 | (vv),xx,ooo,hhhh,pppp | Y
DC | Ames | U200BR10 | 0.5 | H | 2006-04-21 | 2024-04-21 | N | 9 | (vv),xx,ooo,hhhh,pppp | Y
DC | Ames | U200BR10 | 0.5 | VD | 2006-04-21 | 2024-04-21 | N | 9 | (vv),xx,ooo,hhhh,pppp | Y
DC | Ames | U200BR10 | 0.5 | VU | 2006-04-21 | 2024-04-21 | N | 9 | (vv),xx,ooo,hhhh,pppp | Y
DC | Ames | U200BR10 | 0.75 | H | 2006-04-21 | 2024-04-21 | N | 9 | (vv),xx,ooo,hhhh,pppp | Y
DC | Ames | U200BR10 | 0.75 | VD | 2006-04-21 | 2024-04-21 | N | 9 | (vv),xx,ooo,hhhh,pppp | Y
DC | Ames | U200BR10 | 0.75 | VU | 2006-04-21 | 2024-04-21 | N | 9 | (vv),xx,ooo,hhhh,pppp | Y
DC | Apollo/Conbraco | 1/2DC | 0.5 | [9 empty] | model designation changed to DC4S
DC | Apollo/Conbraco | 1/2DC | 0.5 | [9 empty] | model designation changed to DC4S
DC | Apollo/Conbraco | 10DC | 10 | [9 empty] | model designation changed to DC4S
DC | Apollo/Conbraco | 10DC | 10 | [9 empty] | model designation changed to DC4S
DC | Apollo/Conbraco | 2 1/2DC | 2.5 | H | 2000-10-16 | 2024-10-16 | N | 9 | (ll),mm | Y
DC | Apollo/Conbraco | 2 1/2DC | 2.5 | VU | 2000-10-16 | 2024-10-16 | N | 9 | (ll),mm | Y
DC | Apollo/Conbraco | 2 1/2DC-7 | 2.5 | H | 2001-10-23 | 2022-10-23 | N | 9 | (mm)[#1SOV], (qqq)[#2SOV] | Y
DC | Apollo/Conbraco | 2 1/2DC-7 | 2.5 | VU | 2001-10-23 | 2022-10-23 | N | 9 | (mm)[#1SOV], (qqq)[#2SOV] | Y
DC | Apollo/Conbraco | 2 1/2DC8 | 2.5 | H | 2004-09-29 | 2022-09-29 | N | 9 | (ppp),qqq | Y
DC | Apollo/Conbraco | 2 1/2DC8 | 2.5 | VU | 2004-09-29 | 2022-09-29 | N | 9 | (ppp),qqq | Y
DC | Apollo/Conbraco | 2 1/2DCU | 2.5 | VUVD | 2001-04-10 | 2022-04-10 | N | 9 | (ll),mm | Y
DC | Apollo/Conbraco | 2 1/2DCU | 2.5 | VUVD | 2001-04-10 | 2022-04-10 | N | 9 | (ll),mm | Y
DC | Apollo/Conbraco | 3DC | 3 | H | 2000-10-16 | 2024-10-16 | N | 9 | (ll),mm | Y
DC | Apollo/Conbraco | 3DC | 3 | VU | 2000-10-16 | 2024-10-16 | N | 9 | (ll),mm | Y
DC | Apollo/Conbraco | 3DC7 | 3 | H | 2001-10-23 | 2022-10-23 | N | 9 | (mm)[#1SOV], (qqq)[#2SOV] | Y
DC | Apollo/Conbraco | 3DC7 | 3 | VU | 2001-10-23 | 2022-10-23 | N | 9 | (mm)[#1SOV], (qqq)[#2SOV] | Y
DC | Apollo/Conbraco | 3DC8 | 3 | H | 2004-09-29 | 2022-09-29 | N | 9 | (ppp),qqq | Y
DC | Apollo/Conbraco | 3DC8 | 3 | VU | 2004-09-29 | 2022-09-29 | N | 9 | (ppp),qqq | Y
DC | Apollo/Conbraco | 3DCU | 3 | VUVD | 2001-04-10 | 2022-04-10 | N | 9 | (ll),mm | Y
DC | Apollo/Conbraco | 3DCU | 3 | VUVD | 2001-04-10 | 2022-04-10 | N | 9 | (ll),mm | Y
DC | Apollo/Conbraco | 40-100-02 | 3 | H | 1991-04-08 | 2024-04-08 | N | 8 | tt,bb,ee,ll | Y
DC | Apollo/Conbraco | 40-100-03 | 3 | H | 1991-04-08 | 2024-04-08 | N | 8 | uu,cc,mm | Y
DC | Apollo/Conbraco | 40-100-05 | 3 | H | 1998-12-08 | 2022-12-08 | N | 8 | mmm | Y
DC | Apollo/Conbraco | 40-103-02 | 0.5 | H | 1995-05-01 | 2022-05-01 | N | 8 | dd | Y
DC | Apollo/Conbraco | 40-104-02 | 0.75 | H | 1989-03-17 | 2022-03-17 | N | 8 | dd | Y
DC | Apollo/Conbraco | 40-104-99T | 0.75 | [9 empty] | model designation changed to DC40
DC | Apollo/Conbraco | 40-104-A2 | 0.75 | H | 1993-06-21 | 2023-06-21 | N | 8 | dd | Y
DC | Apollo/Conbraco | 40-104-A2T | 0.75 | H | 1992-03-25 | 2022-03-25 | N | 8 | dd | Y
DC | Apollo/Conbraco | 40-104-T2 | 0.75 | [9 empty] | model designation changed to DC40
DC | Apollo/Conbraco | 40-104-TC2 | 0.75 | [9 empty] | model designation changed to DC40
DC | Apollo/Conbraco | 40-105-02 | 1 | H | 1989-03-17 | 2022-03-17 | N | 8 | dd | Y
DC | Apollo/Conbraco | 40-105-99T | 1 | [9 empty] | model designation changed to DC40
DC | Apollo/Conbraco | 40-105-A2 | 1 | H | 1993-06-21 | 2023-06-21 | N | 8 | dd | Y
DC | Apollo/Conbraco | 40-105-A2T | 1 | H | 1992-03-25 | 2022-03-25 | N | 8 | dd | Y
DC | Apollo/Conbraco | 40-105-T2 | 1 | [9 empty] | model designation changed to DC40
DC | Apollo/Conbraco | 40-105-TC2 | 1 | [9 empty] | model designation changed to DC40
DC | Apollo/Conbraco | 40-106-02 | 1.25 | H | 1992-04-06 | 2022-04-06 | N | 8 | dd | Y
DC | Apollo/Conbraco | 40-106-99T | 1.25 | [9 empty] | model designation changed to DC40
DC | Apollo/Conbraco | 40-106-A2 | 1.25 | H | 1993-06-21 | 2023-06-21 | N | 8 | dd | Y
DC | Apollo/Conbraco | 40-106-A2T | 1.25 | H | 1993-05-22 | 2023-05-22 | N | 8 | dd | Y
DC | Apollo/Conbraco | 40-106-T2 | 1.25 | [9 empty] | model designation changed to DC40
DC | Apollo/Conbraco | 40-107-02 | 1.5 | H | 1989-03-17 | 2022-03-17 | N | 8 | dd | Y
DC | Apollo/Conbraco | 40-107-99T | 1.5 | [9 empty] | model designation changed to DC40
DC | Apollo/Conbraco | 40-107-A2 | 1.5 | H | 1993-05-22 | 2023-05-22 | N | 8 | dd | Y
DC | Apollo/Conbraco | 40-107-A2T | 1.5 | H | 1993-05-22 | 2023-05-22 | N | 8 | dd | Y
DC | Apollo/Conbraco | 40-107-T2 | 1.5 | [9 empty] | model designation changed to DC40
DC | Apollo/Conbraco | 40-108-02 | 2 | H | 1989-03-17 | 2022-03-17 | N | 8 | dd | Y
DC | Apollo/Conbraco | 40-108-99T | 2 | [9 empty] | model designation changed to DC40
DC | Apollo/Conbraco | 40-108-A2 | 2 | H | 1993-05-22 | 2023-05-22 | N | 8 | dd | Y
DC | Apollo/Conbraco | 40-108-A2T | 2 | H | 1993-05-22 | 2023-05-22 | N | 8 | dd | Y
DC | Apollo/Conbraco | 40-108-T2 | 2 | [9 empty] | model designation changed to DC40
DC | Apollo/Conbraco | 40-109-02 | 2.5 | H | 1991-04-08 | 2024-04-08 | N | 8 | tt,bb,ee,ll | Y
DC | Apollo/Conbraco | 40-109-03 | 2.5 | H | 1991-04-08 | 2024-04-08 | N | 8 | uu,cc,mm | Y
DC | Apollo/Conbraco | 40-109-05 | 2.5 | H | 1998-12-08 | 2022-12-08 | N | 8 | mmm | Y
DC | Apollo/Conbraco | 40-10A-02 | 4 | H | 1991-04-08 | 2024-04-08 | N | 8 | tt,bb,ee,ll | Y
DC | Apollo/Conbraco | 40-10A-03 | 4 | H | 1991-04-08 | 2024-04-08 | N | 8 | uu,cc,mm | Y
DC | Apollo/Conbraco | 40-10A-05 | 4 | H | 1998-12-08 | 2022-12-08 | N | 8 | mmm | Y
DC | Apollo/Conbraco | 40-10A-06 | 4 | H | 2000-02-01 | 2024-02-01 | N | 8 | mm[#1SOV], nnn[#2SOV] | Y
DC | Apollo/Conbraco | 40-10C-02 | 6 | H | 1991-04-08 | 2024-04-08 | N | 8 | tt,bb,ee,ll | Y
DC | Apollo/Conbraco | 40-10C-03 | 6 | H | 1991-04-08 | 2024-04-08 | N | 8 | uu,cc,mm | Y
DC | Apollo/Conbraco | 40-10C-05 | 6 | H | 1998-12-08 | 2022-12-08 | N | 8 | mmm | Y
DC | Apollo/Conbraco | 40-10C-06 | 6 | H | 2000-02-01 | 2024-02-01 | N | 8 | mm[#1SOV], nnn[#2SOV] | Y
DC | Apollo/Conbraco | 40-10E-02 | 8 | H | 1991-10-22 | 2024-10-22 | N | 8 | tt,bb,ee,ll | Y
DC | Apollo/Conbraco | 40-10E-03 | 8 | H | 1991-10-22 | 2024-10-22 | N | 8 | uu,cc,mm | Y
DC | Apollo/Conbraco | 40-10E-06 | 8 | H | 2000-02-01 | 2024-02-01 | N | 8 | mm[#1SOV], nnn[#2SOV] | Y
DC | Apollo/Conbraco | 40-10G-02 | 10 | H | 1993-04-13 | 2023-04-13 | N | 8 | tt,bb,ee,ll | Y
DC | Apollo/Conbraco | 40-10G-03 | 10 | H | 1993-04-13 | 2023-04-13 | N | 8 | uu,cc,mm | Y
DC | Apollo/Conbraco | 40-10G-06 | 10 | H | 2000-02-01 | 2024-02-01 | N | 8 | mm[#1SOV], nnn[#2SOV] | Y
DC | Apollo/Conbraco | 4D-100 | 2.5 | H | 2012-03-11 | 2024-03-11 | N | 9 | (yyy), cccc, dddd | Y
DC | Apollo/Conbraco | 4D-100 | 2.5 | VU | 2009-03-11 | 2024-03-11 | N | 9 | (yyy), cccc, dddd | Y
DC | Apollo/Conbraco | 4D-100 | 3 | H | 2009-03-11 | 2024-03-11 | N | 9 | (yyy), cccc, dddd | Y
DC | Apollo/Conbraco | 4D-100 | 3 | VU | 2009-03-11 | 2024-03-11 | N | 9 | (yyy), cccc, dddd | Y
DC | Apollo/Conbraco | 4D-100 | 4 | H | 2009-03-11 | 2024-03-11 | N | 9 | (yyy), cccc, dddd | Y
DC | Apollo/Conbraco | 4D-100 | 4 | VU | 2009-03-11 | 2024-03-11 | N | 9 | (yyy), cccc, dddd | Y
DC | Apollo/Conbraco | 4D-100U | 2.5 | VUVD | 2009-03-11 | 2024-03-11 | N | 9 | (yyy), cccc, dddd | Y
DC | Apollo/Conbraco | 4D-100U | 3 | VUVD | 2009-03-11 | 2024-03-11 | N | 9 | (yyy), cccc, dddd | Y
DC | Apollo/Conbraco | 4D-100U | 4 | VUVD | 2009-03-11 | 2024-03-11 | N | 9 | (yyy), cccc, dddd | Y
DC | Apollo/Conbraco | 4DC | 4 | H | 2000-10-16 | 2024-10-16 | N | 9 | (ll),mm | Y
DC | Apollo/Conbraco | 4DC | 4 | VU | 2000-10-16 | 2024-10-16 | N | 9 | (ll),mm | Y
DC | Apollo/Conbraco | 4DC7 | 4 | H | 2001-10-23 | 2022-10-23 | N | 9 | (mm)[#1SOV], (qqq)[#2SOV] | Y
DC | Apollo/Conbraco | 4DC7 | 4 | VU | 2001-10-23 | 2022-10-23 | N | 9 | (mm)[#1SOV], (qqq)[#2SOV] | Y
DC | Apollo/Conbraco | 4DC8 | 4 | H | 2004-09-29 | 2022-09-29 | N | 9 | (ppp),qqq | Y
DC | Apollo/Conbraco | 4DC8 | 4 | VU | 2004-09-29 | 2022-09-29 | N | 9 | (ppp),qqq | Y
DC | Apollo/Conbraco | 4DCU | 4 | VUVD | 2001-04-10 | 2022-04-10 | N | 9 | (ll),mm | Y
DC | Apollo/Conbraco | 4S103 | 0.5 | [9 empty] | model designation changed to W432100
DC | Apollo/Conbraco | 4S103 | 0.5 | [9 empty] | model designation changed to W432100
DC | Apollo/Conbraco | 4SG-100 | 2.5 | [9 empty] | model designation changed to DC4SG
DC | Apollo/Conbraco | 4SG-100 | 2.5 | [9 empty] | model designation changed to DC4SG
DC | Apollo/Conbraco | 4SG-100 | 3 | [9 empty] | model designation changed to DC4SG
DC | Apollo/Conbraco | 4SG-100 | 3 | [9 empty] | model designation changed to DC4SG
DC | Apollo/Conbraco | 4SG-100 | 4 | [9 empty] | model designation changed to DC4SG
DC | Apollo/Conbraco | 4SG-100 | 4 | [9 empty] | model designation changed to DC4SG
DC | Apollo/Conbraco | 4SG-100 | 6 | [9 empty] | model designation changed to DC4SG
DC | Apollo/Conbraco | 4SG-100 | 6 | [9 empty] | model designation changed to DC4SG
DC | Apollo/Conbraco | 4SG-100 | 8 | [9 empty] | model designation changed to DC4SG
DC | Apollo/Conbraco | 4SG-100 | 8 | [9 empty] | model designation changed to DC4SG
DC | Apollo/Conbraco | 4SG-100U | 2.5 | [9 empty] | model designation changed to DC4SGN
DC | Apollo/Conbraco | 4SG-100U | 3 | [9 empty] | model designation changed to DC4SGN
DC | Apollo/Conbraco | 4SG-100U | 4 | [9 empty] | model designation changed to DC4SGN
DC | Apollo/Conbraco | 4SG-100U | 6 | [9 empty] | model designation changed to DC4SGN
DC | Apollo/Conbraco | 4SG-100U | 8 | [9 empty] | model designation changed to DC4SGN
DC | Apollo/Conbraco | 6DC | 6 | H | 2000-10-16 | 2024-10-16 | N | 9 | (ll),mm | Y
DC | Apollo/Conbraco | 6DC | 6 | VU | 2000-10-16 | 2024-10-16 | N | 9 | (ll),mm | Y
DC | Apollo/Conbraco | 6DC7 | 6 | H | 2001-10-23 | 2022-10-23 | N | 9 | (mm)[#1SOV], (qqq)[#2SOV] | Y
DC | Apollo/Conbraco | 6DC7 | 6 | VU | 2001-10-23 | 2022-10-23 | N | 9 | (mm)[#1SOV], (qqq)[#2SOV] | Y
DC | Apollo/Conbraco | 6DC8 | 6 | H | 2004-09-29 | 2022-09-29 | N | 9 | (ppp),qqq | Y
DC | Apollo/Conbraco | 6DC8 | 6 | VU | 2004-09-29 | 2022-09-29 | N | 9 | (ppp),qqq | Y
DC | Apollo/Conbraco | 6DCU | 6 | VUVD | 2001-04-10 | 2022-04-10 | N | 9 | (ll),mm | Y
DC | Apollo/Conbraco | 8DC | 8 | H | 2003-01-16 | 2024-01-16 | N | 9 | (mm),ll | Y
DC | Apollo/Conbraco | 8DC | 8 | VU | 2003-01-16 | 2024-01-16 | N | 9 | (mm),ll | Y
DC | Apollo/Conbraco | 8DC8 | 8 | H | 2004-09-29 | 2022-09-29 | N | 9 | (ppp),qqq | Y
DC | Apollo/Conbraco | 8DC8 | 8 | VU | 2004-09-29 | 2022-09-29 | N | 9 | (ppp),qqq | Y
DC | Apollo/Conbraco | DC40 | 0.75 | H | 1996-06-27 | 2023-06-27 | N | 8 | (dd) | Y |  |  | formerly 40-104-99T, 40-104-T2, 40-104-TC2
DC | Apollo/Conbraco | DC40 | 1 | H | 1996-06-27 | 2023-06-27 | N | 8 | (dd) | Y |  |  | formerly 40-105-99T, 40-105-T2, 40-105-TC2
DC | Apollo/Conbraco | DC40 | 1.25 | H | 1996-10-09 | 2023-10-09 | N | 8 | (dd) | Y |  |  | formerly 40-106-99T, 40-106-T2
DC | Apollo/Conbraco | DC40 | 1.5 | H | 1996-10-09 | 2023-10-09 | N | 8 | (dd) | Y |  |  | formerly 40-107-99T, 40-107-T2
DC | Apollo/Conbraco | DC40 | 2 | H | 1996-10-09 | 2023-10-09 | N | 8 | (dd) | Y |  |  | formerly 40-108-99T, 40-108-T2
DC | Apollo/Conbraco | DC4A | 0.5 | H | 2011-04-27 | 2023-04-27 | N | 9 | (iiiii),sssss | N
DC | Apollo/Conbraco | DC4A | 0.5 | VU | 2011-04-27 | 2023-04-27 | N | 9 | (iiiii),sssss | N
DC | Apollo/Conbraco | DC4A | 0.75 | H | 2011-04-27 | 2023-04-27 | N | 9 | (iiiii),sssss | N
DC | Apollo/Conbraco | DC4A | 0.75 | VU | 2011-04-06 | 2023-04-06 | N | 9 | (iiiii),sssss | N
DC | Apollo/Conbraco | DC4A | 1 | H | 2011-09-27 | 2023-09-27 | N | 9 | (iiiii),sssss,wwwww | N
DC | Apollo/Conbraco | DC4A | 1 | VU | 2011-04-06 | 2023-04-06 | N | 9 | (iiiii),sssss,wwwww | N
DC | Apollo/Conbraco | DC4A | 1.25 | H | 2012-02-07 | 2024-02-07 | N | 9 | (iiiii),sssss,wwwww | N
DC | Apollo/Conbraco | DC4A | 1.25 | VU | 2012-02-07 | 2024-02-07 | N | 9 | (iiiii),sssss,wwwww | N
DC | Apollo/Conbraco | DC4A | 1.5 | H | 2012-02-07 | 2024-02-07 | N | 9 | (iiiii),sssss,wwwww | N
DC | Apollo/Conbraco | DC4A | 1.5 | VU | 2012-02-07 | 2024-02-07 | N | 9 | (iiiii),sssss,wwwww | N
DC | Apollo/Conbraco | DC4A | 2 | H | 2012-02-07 | 2024-02-07 | N | 9 | (iiiii),sssss,wwwww | N
DC | Apollo/Conbraco | DC4A | 2 | VU | 2012-03-27 | 2024-03-27 | N | 9 | (iiiii),sssss,wwwww | N
DC | Apollo/Conbraco | DC4AY | 0.75 | H | 2019-01-16 | 2022-01-16 | N | 10 | (sssss) | N |  |  | body axis oriented with test cocks pointing up and nameplate on the top surface
DC | Apollo/Conbraco | DC4AY | 0.75 | VU | 2018-10-24 | 2024-10-24 | N | 10 | (sssss) | N
DC | Apollo/Conbraco | DC4AY | 1 | H | 2019-01-16 | 2022-01-16 | N | 10 | (sssss) | N |  |  | body axis oriented with test cocks pointing up and nameplate on the top surface
DC | Apollo/Conbraco | DC4AY | 1 | VU | 2018-10-24 | 2024-10-24 | N | 10 | (sssss) | N
DC | Apollo/Conbraco | DC4S | 0.5 | H | 2000-09-18 | 2024-09-18 | N | 9 | (dd) | Y |  |  | formerly 1/2DC
DC | Apollo/Conbraco | DC4S | 0.5 | VU | 2000-09-18 | 2024-09-18 | N | 9 | (dd) | Y |  |  | formerly 1/2DC
DC | Apollo/Conbraco | DC4S | 10 | H | 2003-01-16 | 2024-01-16 | N | 9 | (mm),ll, xxxxx, zzzzz, bbbbbb, cccccc | N |  |  | formerly 10DC
DC | Apollo/Conbraco | DC4S | 10 | VU | 2003-01-16 | 2024-01-16 | N | 9 | (mm),ll, xxxxx, zzzzz, bbbbbb, cccccc | N |  |  | formerly 10DC
DC | Apollo/Conbraco | DC4SG | 2.5 | H | 2007-10-18 | 2022-10-18 | N | 9 | (yyy)ppp,qqq,ttt, xxxxxx | N |  |  | formerly 4SG-100
DC | Apollo/Conbraco | DC4SG | 2.5 | VU | 2007-10-18 | 2022-10-18 | N | 9 | (yyy)ppp,qqq,ttt, xxxxxx | N |  |  | formerly 4SG-100
DC | Apollo/Conbraco | DC4SG | 3 | H | 2007-09-25 | 2022-09-25 | N | 9 | (yyy)ppp,qqq,ttt, xxxxxx | N |  |  | formerly 4SG-100
DC | Apollo/Conbraco | DC4SG | 3 | VU | 2007-09-25 | 2022-09-25 | N | 9 | (yyy)ppp,qqq,ttt, xxxxxx | N |  |  | formerly 4SG-100
DC | Apollo/Conbraco | DC4SG | 4 | H | 2007-09-25 | 2022-09-25 | N | 9 | (yyy)ppp,qqq,ttt, xxxxxx | N |  |  | formerly 4SG-100
DC | Apollo/Conbraco | DC4SG | 4 | VU | 2007-09-25 | 2022-09-25 | N | 9 | (yyy)ppp,qqq,ttt, xxxxxx | N |  |  | formerly 4SG-100
DC | Apollo/Conbraco | DC4SG | 6 | H | 2007-09-25 | 2022-09-25 | N | 9 | (yyy)ppp,qqq,ttt, xxxxxx | N |  |  | formerly 4SG-100
DC | Apollo/Conbraco | DC4SG | 6 | VU | 2007-09-25 | 2022-09-25 | N | 9 | (yyy)ppp,qqq,ttt, xxxxxx | N |  |  | formerly 4SG-100
DC | Apollo/Conbraco | DC4SG | 8 | H | 2007-09-25 | 2022-09-25 | N | 9 | (yyy)ppp,qqq,ttt, xxxxx, yyyyy, zzzzz, aaaaaa, xxxxxx | N |  |  | formerly 4SG-100
DC | Apollo/Conbraco | DC4SG | 8 | VU | 2007-09-25 | 2022-09-25 | N | 9 | (yyy)ppp,qqq,ttt, xxxxx, yyyyy, zzzzz, aaaaaa, xxxxxx | N |  |  | formerly 4SG-100
DC | Apollo/Conbraco | DC4SGN | 2.5 | VUVD | 2007-10-18 | 2022-10-18 | N | 9 | (yyy)ppp,qqq,ttt | Y |  |  | formerly 4SG-100U
DC | Apollo/Conbraco | DC4SGN | 3 | VUVD | 2007-10-18 | 2022-10-18 | N | 9 | (yyy)ppp,qqq,ttt | Y |  |  | formerly 4SG-100U
DC | Apollo/Conbraco | DC4SGN | 4 | VUVD | 2007-10-18 | 2022-10-18 | N | 9 | (yyy)ppp,qqq,ttt | Y |  |  | formerly 4SG-100U
DC | Apollo/Conbraco | DC4SGN | 6 | VUVD | 2007-09-25 | 2022-09-25 | N | 9 | (yyy)ppp,qqq,ttt | Y |  |  | formerly 4SG-100U
DC | Apollo/Conbraco | DC4SGN | 8 | VUVD | 2007-09-25 | 2022-09-25 | N | 9 | (yyy)ppp,qqq,ttt | Y |  |  | formerly 4SG-100U
DC | Apollo/Conbraco | DCLF4A | 0.5 | H | 2011-04-27 | 2023-04-27 | Y | 10 | (jjjjj),ttttt, uuuuu | N
DC | Apollo/Conbraco | DCLF4A | 0.5 | VU | 2011-04-27 | 2023-04-27 | Y | 10 | (jjjjj),ttttt, uuuuu | N
DC | Apollo/Conbraco | DCLF4A | 0.75 | H | 2011-04-27 | 2023-04-27 | Y | 9 | (jjjjj),ttttt | N
DC | Apollo/Conbraco | DCLF4A | 0.75 | VU | 2011-04-06 | 2023-04-06 | Y | 9 | (jjjjj),ttttt | N
DC | Apollo/Conbraco | DCLF4A | 1 | H | 2011-09-27 | 2023-09-27 | Y | 9 | (jjjjj),ttttt,vvvvv | N
DC | Apollo/Conbraco | DCLF4A | 1 | VU | 2011-04-06 | 2023-04-06 | Y | 9 | (jjjjj),ttttt,vvvvv | N
DC | Apollo/Conbraco | DCLF4A | 1.25 | H | 2012-02-07 | 2024-02-07 | Y | 9 | (jjjjj),ttttt,vvvvv | N
DC | Apollo/Conbraco | DCLF4A | 1.25 | VU | 2012-02-07 | 2024-02-07 | Y | 9 | (jjjjj),ttttt,vvvvv | N
DC | Apollo/Conbraco | DCLF4A | 1.5 | H | 2012-02-07 | 2024-02-07 | Y | 9 | (jjjjj),ttttt,vvvvv | N
DC | Apollo/Conbraco | DCLF4A | 1.5 | VU | 2012-02-07 | 2024-02-07 | Y | 9 | (jjjjj),ttttt,vvvvv | N
DC | Apollo/Conbraco | DCLF4A | 2 | H | 2012-02-07 | 2024-02-07 | Y | 9 | (jjjjj),ttttt,vvvvv | N
DC | Apollo/Conbraco | DCLF4A | 2 | VU | 2012-03-27 | 2024-03-27 | Y | 9 | (jjjjj),ttttt,vvvvv | N
DC | Apollo/Conbraco | DCLF4A | 2.5 | H | 2013-11-05 | 2022-11-05 | Y | 10 | (yyy), cccc, dddd, mmmm, nnnn, xxxxx, yyyyy, zzzzz, aaaaaa, xxxxxx | N
DC | Apollo/Conbraco | DCLF4A | 2.5 | VU | 2013-11-05 | 2022-11-05 | Y | 10 | (yyy), cccc, dddd, mmmm, nnnn, xxxxx, yyyyy, zzzzz, aaaaaa, xxxxxx | N
DC | Apollo/Conbraco | DCLF4A | 3 | H | 2013-11-05 | 2022-11-05 | Y | 10 | (yyy), cccc, dddd, mmmm, nnnn, xxxxx, yyyyy, zzzzz, aaaaaa, xxxxxx | N
DC | Apollo/Conbraco | DCLF4A | 3 | VU | 2013-11-05 | 2022-11-05 | Y | 10 | (yyy), cccc, dddd, mmmm, nnnn, xxxxx, yyyyy, zzzzz, aaaaaa, xxxxxx | N
DC | Apollo/Conbraco | DCLF4A | 4 | H | 2013-06-24 | 2022-06-24 | Y | 10 | (yyy), cccc, dddd, mmmm, nnnn, xxxxx, yyyyy, zzzzz, aaaaaa, xxxxxx | N
DC | Apollo/Conbraco | DCLF4A | 4 | VU | 2013-06-24 | 2022-06-24 | Y | 10 | (yyy), cccc, dddd, mmmm, nnnn, xxxxx, yyyyy, zzzzz, aaaaaa, xxxxxx | N
DC | Apollo/Conbraco | DCLF4A | 6 | H | 2013-06-24 | 2022-06-24 | Y | 10 | (yyy), cccc, dddd, mmmm, nnnn, xxxxx, yyyyy, zzzzz, aaaaaa, xxxxxx | N
DC | Apollo/Conbraco | DCLF4A | 6 | VU | 2013-06-24 | 2022-06-24 | Y | 10 | (yyy), cccc, dddd, mmmm, nnnn, xxxxx, yyyyy, zzzzz, aaaaaa, xxxxxx | N
DC | Apollo/Conbraco | DCLF4A | 8 | H | 2014-05-15 | 2023-05-15 | Y | 10 | (yyy), cccc, dddd, mmmm, nnnn, xxxxx, yyyyy, zzzzz, aaaaaa, xxxxxx | N
DC | Apollo/Conbraco | DCLF4A | 8 | VU | 2014-05-15 | 2023-05-15 | Y | 10 | (yyy), cccc, dddd, mmmm, nnnn, xxxxx, yyyyy, zzzzz, aaaaaa, xxxxxx | N
DC | Apollo/Conbraco | DCLF4A | 10 | H | 2021-11-05 | 2024-11-05 | Y | 10 | (zzzzz), yyy,zzz,cccc,dddd,kkkk,llll,mmmm,nnnn,xxxxx, yyyyy,aaaaaa | N
DC | Apollo/Conbraco | DCLF4A | 12 | H | 2021-11-05 | 2024-11-05 | Y | 10 | (bbbbbb), ll,mm,cccccc | N
DC | Apollo/Conbraco | DCLF4AN | 2.5 | VUVD | 2014-06-10 | 2023-06-10 | Y | 10 | (yyy), cccc, dddd, mmmm, nnnn, xxxxx, yyyyy, zzzzz, aaaaaa, xxxxxx | N
DC | Apollo/Conbraco | DCLF4AN | 3 | VUVD | 2014-04-08 | 2023-04-08 | Y | 10 | (yyy), cccc, dddd, mmmm, nnnn, xxxxx, yyyyy, zzzzz, aaaaaa, xxxxxx | N
DC | Apollo/Conbraco | DCLF4AN | 4 | VUVD | 2013-11-22 | 2022-11-22 | Y | 10 | (yyy), cccc, dddd, mmmm, nnnn, xxxxx, yyyyy, zzzzz, aaaaaa, xxxxxx | N
DC | Apollo/Conbraco | DCLF4AN | 6 | VUVD | 2014-04-15 | 2023-04-15 | Y | 10 | (yyy), cccc, dddd, mmmm, nnnn, xxxxx, yyyyy, zzzzz, aaaaaa, xxxxxx | N
DC | Apollo/Conbraco | DCLF4AN | 8 | VUVD | 2014-02-20 | 2023-02-20 | Y | 10 | (yyy), cccc, dddd, mmmm, nnnn, xxxxx, yyyyy, zzzzz, aaaaaa, xxxxxx | N
DC | Apollo/Conbraco | DCLF4AN | 10 | VUVD | 2021-11-05 | 2024-11-05 | Y | 10 | (zzzzz), yyy,zzz,cccc,dddd,kkkk,llll,mmmm,nnnn,xxxxx, yyyyy,aaaaaa | N
DC | Apollo/Conbraco | DCLF4AN | 12 | VUVD | 2021-11-05 | 2024-11-05 | Y | 10 | (bbbbbb), ll,mm,cccccc | N
DC | Apollo/Conbraco | DCLF4AR | 2.5 | H | 2015-11-09 | 2024-11-09 | Y | 10 | (cccc), dddd, mmmm, nnnn, xxxxx, yyyyy, zzzzz, aaaaaa | Y |  |  | Integral Stainless Steel grooved spool between the #2 ck and #2 SOV - assembly length: min. 34" and max. 47 1/8"
DC | Apollo/Conbraco | DCLF4AR | 2.5 | VU | 2015-11-09 | 2024-11-09 | Y | 10 | (cccc), dddd, mmmm, nnnn, xxxxx, yyyyy, zzzzz, aaaaaa | Y |  |  | Integral Stainless Steel grooved spool between the #2 ck and #2 SOV - assembly length: min. 34" and max. 47 1/8"
DC | Apollo/Conbraco | DCLF4AR | 3 | H | 2015-11-09 | 2024-11-09 | Y | 10 | (cccc), dddd, mmmm, nnnn, xxxxx, yyyyy, zzzzz, aaaaaa | Y |  |  | Integral Stainless Steel grooved spool between the #2 ck and #2 SOV - assembly length: min. 35" and max. 48 1/8"
DC | Apollo/Conbraco | DCLF4AR | 3 | VU | 2015-11-09 | 2024-11-09 | Y | 10 | (cccc), dddd, mmmm, nnnn, xxxxx, yyyyy, zzzzz, aaaaaa | Y |  |  | Integral Stainless Steel grooved spool between the #2 ck and #2 SOV - assembly length: min. 35" and max. 48 1/8"
DC | Apollo/Conbraco | DCLF4AR | 4 | H | 2015-09-21 | 2024-09-21 | Y | 10 | (cccc), dddd, mmmm, nnnn, xxxxx, yyyyy, zzzzz, aaaaaa | Y |  |  | Integral Stainless Steel grooved spool between the #2 ck and #2 SOV - assembly length: min. 37 3/8" and max. 62 1/4"
DC | Apollo/Conbraco | DCLF4AR | 4 | VU | 2015-09-21 | 2024-09-21 | Y | 10 | (cccc), dddd, mmmm, nnnn, xxxxx, yyyyy, zzzzz, aaaaaa | Y |  |  | Integral Stainless Steel grooved spool between the #2 ck and #2 SOV - assembly length: min. 37 3/8" and max. 62 1/4"
DC | Apollo/Conbraco | DCLF4AR | 6 | H | 2015-09-21 | 2024-09-21 | Y | 10 | (cccc), dddd, mmmm, nnnn, xxxxx, yyyyy, zzzzz, aaaaaa | Y |  |  | Integral Stainless Steel grooved spool between the #2 ck and #2 SOV - assembly length: min. 46" and max. 71 1/4"
DC | Apollo/Conbraco | DCLF4AR | 6 | VU | 2015-09-21 | 2024-09-21 | Y | 10 | (cccc), dddd, mmmm, nnnn, xxxxx, yyyyy, zzzzz, aaaaaa | Y |  |  | Integral Stainless Steel grooved spool between the #2 ck and #2 SOV - assembly length: min. 46" and max. 71 1/4"
DC | Apollo/Conbraco | DCLF4AR | 8 | H | 2015-12-21 | 2024-12-21 | Y | 10 | (cccc), dddd, mmmm, nnnn, xxxxx, yyyyy, zzzzz, aaaaaa | Y |  |  | Integral Stainless Steel grooved spool between the #2 ck and #2 SOV - assembly length: min. 55 3/4" and max. 86"
DC | Apollo/Conbraco | DCLF4AR | 8 | VU | 2015-12-21 | 2024-12-21 | Y | 10 | (cccc), dddd, mmmm, nnnn, xxxxx, yyyyy, zzzzz, aaaaaa | Y |  |  | Integral Stainless Steel grooved spool between the #2 ck and #2 SOV - assembly length: min. 55 3/4" and max. 86"
DC | Apollo/Conbraco | DCLF4AR | 10 | H | 2021-11-05 | 2024-11-05 | Y | 10 | (zzzzz), zzz,cccc,dddd,kkkk,llll,mmmm,nnnn,xxxxx, yyyyy,aaaaaa | Y |  |  | Integral Stainless Steel grooved spool between the #2 ck and #2 SOV - assembly length: min. 65 3/4" and max. 100 5/8"
DC | Apollo/Conbraco | DCLF4AY | 0.75 | H | 2019-01-16 | 2022-01-16 | Y | 10 | (ttttt) | N |  |  | body axis oriented with test cocks pointing up and nameplate on the top surface
DC | Apollo/Conbraco | DCLF4AY | 0.75 | VU | 2018-10-24 | 2024-10-24 | Y | 10 | (ttttt) | N
DC | Apollo/Conbraco | DCLF4AY | 1 | H | 2019-01-16 | 2022-01-16 | Y | 10 | (ttttt) | N |  |  | body axis oriented with test cocks pointing up and nameplate on the top surface
DC | Apollo/Conbraco | DCLF4AY | 1 | VU | 2018-10-24 | 2024-10-24 | Y | 10 | (ttttt) | N
DC | Apollo/Conbraco | DCLF4SG | 2.5 | H | 2015-01-23 | 2024-01-23 | Y | 9 | (yyy), cccc, dddd, mmmm, nnnn, xxxxx, yyyyy, zzzzz, aaaaaa, xxxxxx | N
DC | Apollo/Conbraco | DCLF4SG | 2.5 | VU | 2015-01-23 | 2024-01-23 | Y | 9 | (yyy), cccc, dddd, mmmm, nnnn, xxxxx, yyyyy, zzzzz, aaaaaa, xxxxxx | N
DC | Apollo/Conbraco | DCLF4SG | 3 | H | 2015-01-23 | 2024-01-23 | Y | 9 | (yyy), cccc, dddd, mmmm, nnnn, xxxxx, yyyyy, zzzzz, aaaaaa, xxxxxx | N
DC | Apollo/Conbraco | DCLF4SG | 3 | VU | 2015-01-23 | 2024-01-23 | Y | 9 | (yyy), cccc, dddd, mmmm, nnnn, xxxxx, yyyyy, zzzzz, aaaaaa, xxxxxx | N
DC | Apollo/Conbraco | DCLF4SG | 4 | H | 2015-01-23 | 2024-01-23 | Y | 9 | (yyy), cccc, dddd, mmmm, nnnn, xxxxx, yyyyy, zzzzz, aaaaaa, xxxxxx | N
DC | Apollo/Conbraco | DCLF4SG | 4 | VU | 2015-01-23 | 2024-01-23 | Y | 9 | (yyy), cccc, dddd, mmmm, nnnn, xxxxx, yyyyy, zzzzz, aaaaaa, xxxxxx | N
DC | Apollo/Conbraco | DCLF4SG | 6 | H | 2015-01-23 | 2024-01-23 | Y | 9 | (yyy), cccc, dddd, mmmm, nnnn, xxxxx, yyyyy, zzzzz, aaaaaa, xxxxxx | N
DC | Apollo/Conbraco | DCLF4SG | 6 | VU | 2015-01-23 | 2024-01-23 | Y | 9 | (yyy), cccc, dddd, mmmm, nnnn, xxxxx, yyyyy, zzzzz, aaaaaa, xxxxxx | N
DC | Apollo/Conbraco | W432100 | 0.5 | H | 2007-10-18 | 2022-10-18 | N | 9 | (dd) | N |  |  | formerly 4S103
DC | Apollo/Conbraco | W432100 | 0.5 | VU | 2007-10-18 | 2022-10-18 | N | 9 | (dd) | N |  |  | formerly 4S103
DC | ARI | DC 500 | 0.5 | H | 2013-01-03 | 2022-01-03 | N | 9 | (ooooo), ii, ooo,ffffff | N
DC | ARI | DC 500 | 0.5 | H | 2014-02-18 | 2023-02-18 | Y | 9 | (ooooo),ffffff | N
DC | ARI | DC 500 | 0.75 | H | 2007-03-02 | 2022-03-02 | N | 9 | (ii),ooo, ooooo, ffffff | N
DC | ARI | DC 500 | 0.75 | H | 2014-02-18 | 2023-02-18 | Y | 9 | (ooooo), ffffff | N
DC | ARI | DC 500 | 1 | H | 2007-03-02 | 2022-03-02 | N | 9 | (ii),ooo, ooooo, ffffff | N
DC | ARI | DC 500 | 1 | H | 2014-02-18 | 2023-02-18 | Y | 9 | (ooooo), ffffff | N
DC | ARI | DC 500 | 1.25 | H | 2014-01-08 | 2023-01-08 | Y | 10 | (ooooo), ffffff | N
DC | ARI | DC 500 | 1.5 | H | 2014-01-08 | 2023-01-08 | Y | 10 | (ooooo), ffffff | N
DC | ARI | DC 500 | 2 | H | 2014-01-08 | 2023-01-08 | Y | 10 | (ooooo), ffffff | N
DC | ARI | DC 501 | 0.5 | H | 2018-09-06 | 2024-09-06 | Y | 10 | (int) | N
DC | ARI | DC 501 | 0.75 | H | 2017-03-20 | 2023-03-20 | Y | 10 | (int) | N
DC | ARI | DC 501 | 1 | H | 2018-03-15 | 2024-03-15 | Y | 10 | (int) | N
DC | ARI | DC 501 | 1.25 | H | 2017-03-20 | 2023-03-20 | Y | 10 | (int) | N
DC | ARI | DC 501 | 1.5 | H | 2017-03-20 | 2023-03-20 | Y | 10 | (int) | N
DC | ARI | DC 501 | 2 | H | 2017-03-20 | 2023-03-20 | Y | 10 | (int) | N
DC | Backflow Direct | Deringer 20 | 2.5 | H | 2015-12-21 | 2024-12-21 | Y | 10 | (int) | N
DC | Backflow Direct | Deringer 20 | 2.5 | VU | 2015-12-21 | 2024-12-21 | Y | 10 | (int) | N
DC | Backflow Direct | Deringer 20 | 3 | H | 2015-12-21 | 2024-12-21 | Y | 10 | (int) | N
DC | Backflow Direct | Deringer 20 | 3 | VU | 2015-12-21 | 2024-12-21 | Y | 10 | (int) | N
DC | Backflow Direct | Deringer 20 | 4 | H | 2015-09-30 | 2024-09-30 | Y | 10 | (int) | N
DC | Backflow Direct | Deringer 20 | 4 | VU | 2015-09-30 | 2024-09-30 | Y | 10 | (int) | N
DC | Backflow Direct | Deringer 20 | 6 | H | 2019-10-30 | 2022-10-30 | Y | 10 | (int) | N
DC | Backflow Direct | Deringer 20 | 6 | VU | 2019-10-30 | 2022-10-30 | Y | 10 | (int) | N
DC | Backflow Direct | Deringer 20 | 8 | H | 2016-12-23 | 2022-12-23 | Y | 10 | (int) | N
DC | Backflow Direct | Deringer 20 | 8 | VU | 2016-12-23 | 2022-12-23 | Y | 10 | (int) | N
DC | Backflow Direct | Deringer 20G | 2.5 | H | 2018-12-07 | 2024-12-07 | Y | 10 | (ssssss), tttttt | N
DC | Backflow Direct | Deringer 20G | 2.5 | VU | 2018-12-07 | 2024-12-07 | Y | 10 | (ssssss), tttttt | N
DC | Backflow Direct | Deringer 20G | 3 | H | 2018-12-07 | 2024-12-07 | Y | 10 | (ssssss), tttttt | N
DC | Backflow Direct | Deringer 20G | 3 | VU | 2018-12-07 | 2024-12-07 | Y | 10 | (ssssss), tttttt | N
DC | Backflow Direct | Deringer 20G | 4 | H | 2018-12-07 | 2024-12-07 | Y | 10 | (ssssss), tttttt | N
DC | Backflow Direct | Deringer 20G | 4 | VU | 2018-12-07 | 2024-12-07 | Y | 10 | (ssssss), tttttt | N
DC | Backflow Direct | Deringer 20G | 6 | H | 2020-01-16 | 2023-01-16 | Y | 10 | (ssssss), tttttt | N
DC | Backflow Direct | Deringer 20G | 6 | VU | 2020-01-16 | 2023-01-16 | Y | 10 | (ssssss), tttttt | N
DC | Backflow Direct | Deringer 20G | 8 | H | 2018-07-31 | 2024-07-31 | Y | 10 | (ssssss), tttttt | N
DC | Backflow Direct | Deringer 20G | 8 | VU | 2018-07-31 | 2024-07-31 | Y | 10 | (ssssss), tttttt | N
DC | Backflow Direct | Deringer 20GX | 4 | H | 2020-01-16 | 2023-01-16 | Y | 10 | (ssssss), tttttt | N
DC | Backflow Direct | Deringer 20GX | 4 | VU | 2020-01-16 | 2023-01-16 | Y | 10 | (ssssss), tttttt | N
DC | Backflow Direct | Deringer 20GX | 6 | H | 2018-07-31 | 2024-07-31 | Y | 10 | (ssssss), tttttt | N
DC | Backflow Direct | Deringer 20GX | 6 | VU | 2018-07-31 | 2024-07-31 | Y | 10 | (ssssss), tttttt | N
DC | Backflow Direct | Deringer 20X | 4 | H | 2019-10-30 | 2022-10-30 | Y | 10 | (int) | N
DC | Backflow Direct | Deringer 20X | 4 | VU | 2019-10-30 | 2022-10-30 | Y | 10 | (int) | N
DC | Backflow Direct | Deringer 20X | 6 | H | 2016-12-23 | 2022-12-23 | Y | 10 | (int) | N
DC | Backflow Direct | Deringer 20X | 6 | VU | 2016-12-23 | 2022-12-23 | Y | 10 | (int) | N
DC | Backflow Direct | Magnum 20 | 2.5 | H | 2018-03-15 | 2024-03-15 | Y | 10 | (int) | N
DC | Backflow Direct | Magnum 20 | 2.5 | VU | 2018-03-15 | 2024-03-15 | Y | 10 | (int) | N
DC | Backflow Direct | Magnum 20 | 3 | H | 2018-03-15 | 2024-03-15 | Y | 10 | (int) | N
DC | Backflow Direct | Magnum 20 | 3 | VU | 2018-03-15 | 2024-03-15 | Y | 10 | (int) | N
DC | Backflow Direct | Magnum 20 | 4 | H | 2018-03-15 | 2024-03-15 | Y | 10 | (int) | N
DC | Backflow Direct | Magnum 20 | 4 | VU | 2018-03-15 | 2024-03-15 | Y | 10 | (int) | N
DC | Backflow Direct | Magnum 20 | 8 | H | 2018-03-15 | 2024-03-15 | Y | 10 | (int) | N
DC | Backflow Direct | Magnum 20 | 8 | VU | 2018-03-15 | 2024-03-15 | Y | 10 | (int) | N
DC | Backflow Direct | Magnum 20G | 2.5 | H | 2018-12-07 | 2024-12-07 | Y | 10 | (qqqqqq), rrrrrr | N
DC | Backflow Direct | Magnum 20G | 2.5 | VU | 2018-12-07 | 2024-12-07 | Y | 10 | (qqqqqq), rrrrrr | N
DC | Backflow Direct | Magnum 20G | 3 | H | 2018-12-07 | 2024-12-07 | Y | 10 | (qqqqqq), rrrrrr | N
DC | Backflow Direct | Magnum 20G | 3 | VU | 2018-12-07 | 2024-12-07 | Y | 10 | (qqqqqq), rrrrrr | N
DC | Backflow Direct | Magnum 20G | 4 | H | 2018-12-07 | 2024-12-07 | Y | 10 | (qqqqqq), rrrrrr | N
DC | Backflow Direct | Magnum 20G | 4 | VU | 2018-12-07 | 2024-12-07 | Y | 10 | (qqqqqq), rrrrrr | N
DC | Backflow Direct | Magnum 20G | 8 | H | 2018-07-31 | 2024-07-31 | Y | 10 | (qqqqqq), rrrrrr | N
DC | Backflow Direct | Magnum 20G | 8 | VU | 2018-07-31 | 2024-07-31 | Y | 10 | (qqqqqq), rrrrrr | N
DC | Backflow Direct | Magnum 20G | 6 | H | 2020-01-16 | 2023-01-16 | Y | 10 | (qqqqqq), rrrrrr | N
DC | Backflow Direct | Magnum 20G | 6 | VU | 2020-01-16 | 2023-01-16 | Y | 10 | (qqqqqq), rrrrrr | N
DC | Backflow Direct | Magnum 20GX | 6 | H | 2018-07-31 | 2024-07-31 | Y | 10 | (qqqqqq), rrrrrr | N
DC | Backflow Direct | Magnum 20GX | 6 | VU | 2018-07-31 | 2024-07-31 | Y | 10 | (qqqqqq), rrrrrr | N
DC | Backflow Direct | Magnum 20X | 6 | H | 2018-03-15 | 2024-03-15 | Y | 10 | (int) | N
DC | Backflow Direct | Magnum 20X | 6 | VU | 2018-03-15 | 2024-03-15 | Y | 10 | (int) | N
DC | BEECO | Barracuda 20 | 2.5 | H | 2018-12-18 | 2024-12-18 | Y | 10 | (qqqqqq), rrrrrr, vvvvvv, wwwwww | N
DC | BEECO | Barracuda 20 | 2.5 | VU | 2018-12-18 | 2024-12-18 | Y | 10 | (qqqqqq), rrrrrr, vvvvvv, wwwwww | N
DC | BEECO | Barracuda 20 | 3 | H | 2018-12-18 | 2024-12-18 | Y | 10 | (qqqqqq), rrrrrr, vvvvvv, wwwwww | N
DC | BEECO | Barracuda 20 | 3 | VU | 2018-12-18 | 2024-12-18 | Y | 10 | (qqqqqq), rrrrrr, vvvvvv, wwwwww | N
DC | BEECO | Barracuda 20 | 4 | H | 2018-12-18 | 2024-12-18 | Y | 10 | (qqqqqq), rrrrrr, vvvvvv, wwwwww | N
DC | BEECO | Barracuda 20 | 4 | VU | 2018-12-18 | 2024-12-18 | Y | 10 | (qqqqqq), rrrrrr, vvvvvv, wwwwww | N
DC | BEECO | Barracuda 20 | 6 | H | 2021-07-26 | 2024-07-26 | Y | 10 | (qqqqqq), rrrrrr, vvvvvv, wwwwww | N
DC | BEECO | Barracuda 20 | 6 | VU | 2021-07-26 | 2024-07-26 | Y | 10 | (qqqqqq), rrrrrr, vvvvvv, wwwwww | N
DC | BEECO | Barracuda 20 | 8 | H | 2018-12-18 | 2024-12-18 | Y | 10 | (qqqqqq), rrrrrr | N
DC | BEECO | Barracuda 20 | 8 | VU | 2018-12-18 | 2024-12-18 | Y | 10 | (qqqqqq), rrrrrr | N
DC | BEECO | Barracuda 20X | 6 | H | 2018-12-18 | 2024-12-18 | Y | 10 | (qqqqqq), rrrrrr, vvvvvv, wwwwww | N
DC | BEECO | Barracuda 20X | 6 | VU | 2018-12-18 | 2024-12-18 | Y | 10 | (qqqqqq), rrrrrr, vvvvvv, wwwwww | N
DC | BEECO | FDC | 0.5 | H | 2022-01-21 |  | Y | 10 | (yyyyyy) | N
DC | BEECO | FDC | 0.5 | VU | 2022-01-21 |  | Y | 10 | (yyyyyy) | N
DC | BEECO | FDC | 0.75 | H | 2022-01-21 |  | Y | 10 | (yyyyyy) | N
DC | BEECO | FDC | 0.75 | VU | 2022-01-21 |  | Y | 10 | (yyyyyy) | N
DC | BEECO | FDC | 1 | H | 2022-10-11 |  | Y | 10 | (yyyyyy) | N
DC | BEECO | FDC | 1 | VU | 2022-10-11 |  | Y | 10 | (yyyyyy) | N
DC | BEECO | FDC | 1.25 | H | 2022-01-21 |  | Y | 10 | (yyyyyy) | N
DC | BEECO | FDC | 1.25 | VU | 2022-01-21 |  | Y | 10 | (yyyyyy) | N
DC | BEECO | FDC | 1.5 | H | 2022-01-21 |  | Y | 10 | (yyyyyy) | N
DC | BEECO | FDC | 1.5 | VU | 2022-01-21 |  | Y | 10 | (yyyyyy) | N
DC | BEECO | FDC | 2 | H | 2022-10-11 |  | Y | 10 | (yyyyyy) | N
DC | BEECO | FDC | 2 | VU | 2022-10-11 |  | Y | 10 | (yyyyyy) | N
DC | BEECO | FDC | 2.5 | H | 2018-12-18 | 2024-12-18 | Y | 10 | (vvvvvv), wwwwww | N
DC | BEECO | FDC | 2.5 | VU | 2018-12-18 | 2024-12-18 | Y | 10 | (vvvvvv), wwwwww | N
DC | BEECO | FDC | 3 | H | 2018-12-18 | 2024-12-18 | Y | 10 | (vvvvvv), wwwwww | N
DC | BEECO | FDC | 3 | VU | 2018-12-18 | 2024-12-18 | Y | 10 | (vvvvvv), wwwwww | N
DC | BEECO | FDC | 4 | H | 2018-12-18 | 2024-12-18 | Y | 10 | (vvvvvv), wwwwww | N
DC | BEECO | FDC | 4 | VU | 2018-12-18 | 2024-12-18 | Y | 10 | (vvvvvv), wwwwww | N
DC | BEECO | FDC | 6 | H | 2018-12-18 | 2024-12-18 | Y | 10 | (vvvvvv), wwwwww | N
DC | BEECO | FDC | 6 | VU | 2018-12-18 | 2024-12-18 | Y | 10 | (vvvvvv), wwwwww | N
DC | BEECO | FDC | 8 | H | 2024-02-28 |  | Y | 10 | (vvvvvv), wwwwww | N
DC | BEECO | FDC | 8 | VU | 2024-02-28 |  | Y | 10 | (vvvvvv), wwwwww | N
DC | BEECO | FDC | 10 | H | 2024-02-28 |  | Y | 10 | (vvvvvv), wwwwww | N
DC | BEECO | FDC | 10 | VU | 2024-02-28 |  | Y | 10 | (vvvvvv), wwwwww | N
DC | Cla-Val | D4 | 8 | H | 1989-06-22 | 2022-06-22 | N | 8 | (gg),hh,qq,rr | Y
DC | Cla-Val | D4 | 10 | H | 1989-06-22 | 2022-06-22 | N | 8 | (gg),hh,qq,rr | Y
DC | Conbraco | [5 empty] | N | [5 empty] | See Apollo/Conbraco
DC | Febco | 850 | 0.5 | H | 1997-11-21 | 2024-11-21 | N | 9 | (fff),ooo | N
DC | Febco | 850 | 0.5 | VD | 2000-04-13 | 2024-04-13 | N | 9 | (fff),ooo | N
DC | Febco | 850 | 0.5 | VU | 1999-12-17 | 2023-12-17 | N | 9 | (fff),ooo | N
DC | Febco | 850 | 0.75 | H | 1997-11-21 | 2024-11-21 | N | 9 | (fff),jjj,ooo | N
DC | Febco | 850 | 0.75 | VD | 2000-04-10 | 2024-04-10 | N | 9 | (fff),jjj,ooo | N
DC | Febco | 850 | 0.75 | VU | 1999-12-17 | 2023-12-17 | N | 9 | (fff),jjj,ooo | N
DC | Febco | 850 | 1 | H | 1997-11-21 | 2024-11-21 | N | 9 | (fff),jjj,ooo | N
DC | Febco | 850 | 1 | VD | 2000-01-14 | 2024-01-14 | N | 9 | (fff),jjj,ooo | N
DC | Febco | 850 | 1 | VU | 2000-09-07 | 2024-09-07 | N | 9 | (fff),jjj,ooo | N
DC | Febco | 850 | 1.25 | H | 1997-11-21 | 2024-11-21 | N | 9 | (fff),jjj,ooo | N
DC | Febco | 850 | 1.25 | VD | 2000-04-13 | 2024-04-13 | N | 9 | (fff),jjj,ooo | N
DC | Febco | 850 | 1.25 | VU | 1999-07-17 | 2023-07-17 | N | 9 | (fff),jjj,ooo | N
DC | Febco | 850 | 1.5 | H | 1998-02-19 | 2022-02-19 | N | 9 | (fff),jjj,ooo | N
DC | Febco | 850 | 1.5 | VD | 2000-04-13 | 2024-04-13 | N | 9 | (fff),jjj,ooo | N
DC | Febco | 850 | 1.5 | VU | 1999-07-17 | 2023-07-17 | N | 9 | (fff),jjj,ooo | N
DC | Febco | 850 | 2 | H | 1998-02-19 | 2022-02-19 | N | 9 | (fff),ooo | N
DC | Febco | 850 | 2 | VD | 2000-04-10 | 2024-04-10 | N | 9 | (fff),ooo | N
DC | Febco | 850 | 2 | VU | 1999-07-17 | 2023-07-17 | N | 9 | (fff),ooo | N
DC | Febco | 850 | 2.5 | H | 1997-03-14 | 2024-03-14 | N | 8 | (ee),ff,ll,mm,oo,pp,tt,uu,zzz,cccc,ffff,gggg | Y
DC | Febco | 850 | 2.5 | VU | 1997-03-19 | 2024-03-19 | N | 8 | (ee),ff,ll,mm,oo,pp,tt,uu,zzz,cccc,ffff,gggg | Y
DC | Febco | 850 | 3 | H | 1997-03-14 | 2024-03-14 | N | 8 | (ee),ff,ll,mm,oo,pp,tt,uu,zzz,cccc,ffff,gggg | Y
DC | Febco | 850 | 3 | VU | 1997-03-19 | 2024-03-19 | N | 8 | (ee),ff,ll,mm,oo,pp,tt,uu,zzz,cccc,ffff,gggg | Y
DC | Febco | 850 | 4 | H | 1994-05-04 | 2024-05-04 | N | 8 | (ee),ff,ll,mm,oo,pp,tt,uu,nnn,zzz,cccc,ffff,gggg | Y
DC | Febco | 850 | 4 | VU | 1995-02-07 | 2022-02-07 | N | 8 | (ee),ff,ll,mm,oo,pp,tt,uu,nnn,zzz,cccc,ffff,gggg | Y
DC | Febco | 850 | 6 | H | 1994-05-04 | 2024-05-04 | N | 8 | (ee),ff,ll,mm,oo,pp,tt,uu,nnn,zzz,cccc,ffff,gggg | Y
DC | Febco | 850 | 6 | VU | 1995-05-31 | 2022-05-31 | N | 8 | (ee),ff,ll,mm,oo,pp,tt,uu,nnn,zzz,cccc,ffff,gggg | Y
DC | Febco | 850 | 8 | H | 1995-10-04 | 2022-10-04 | N | 8 | (ee),ff,ll,mm,oo,pp,tt,uu,nnn,zzz,cccc,ffff,gggg | Y
DC | Febco | 850 | 8 | VU | 1996-10-14 | 2023-10-14 | N | 8 | (ee),ff,ll,mm,oo,pp,tt,uu,nnn,zzz,cccc,ffff,gggg | Y
DC | Febco | 857 | 2.5 | H | 2006-08-01 | 2024-08-01 | N | 8 | (oo), gg, hh,ll, mm, pp, tt, uu, yy, fff | Y
DC | Febco | 857 | 2.5 | VU | 2006-08-01 | 2024-08-01 | N | 8 | (oo), gg, hh,ll, mm, pp, tt, uu, yy, fff | Y
DC | Febco | 857 | 3 | H | 2006-08-01 | 2024-08-01 | N | 8 | (oo), gg, hh,ll, mm, pp, tt, uu, yy, fff | Y
DC | Febco | 857 | 3 | VU | 2006-08-01 | 2024-08-01 | N | 8 | (oo), gg, hh,ll, mm, pp, tt, uu, yy, fff | Y
DC | Febco | 870 | 2.5 | VUVD | 1995-03-10 | 2022-03-10 | N | 8 | ee,ff,ll,mm,oo,pp,tt,uu,zzz,ffff,gggg | Y
DC | Febco | 870 | 3 | VUVD | 1995-03-10 | 2022-03-10 | N | 8 | ee,ff,ll,mm,oo,pp,tt,uu,zzz,ffff,gggg | Y
DC | Febco | 870 | 4 | VUVD | 1994-05-04 | 2024-05-04 | N | 8 | ee,ff,ll,mm,oo,pp,tt,uu,zzz,ffff,gggg | Y
DC | Febco | 870 | 6 | VUVD | 1994-05-04 | 2024-05-04 | N | 8 | ee,ff,ll,mm,oo,pp,tt,uu,zzz,ffff,gggg | Y
DC | Febco | 870 | 8 | VUVD | 1994-05-24 | 2024-05-24 | N | 8 | ee,ff,ll,mm,oo,pp,tt,uu,zzz,ffff,gggg | Y
DC | Febco | 870 | 10 | VUVD | 1996-10-04 | 2023-10-04 | N | 8 | ee,ff,ll,mm,oo,pp,tt,uu,zzz,ffff,gggg | Y
DC | Febco | 805 Type YD | 2.5 | [9 empty] | model designation changed to 805YD
DC | Febco | 805 Type YD | 3 | [9 empty] | model designation changed to 805YD
DC | Febco | 805 Type YD | 4 | [9 empty] | model designation changed to 805YD
DC | Febco | 805 Type YD | 6 | [9 empty] | model designation changed to 805YD
DC | Febco | 805 Type YD | 8 | [9 empty] | model designation changed to 805YD
DC | Febco | 805 Type YD | 10 | [9 empty] | model designation changed to 805YD
DC | Febco | 805Y | 0.75 | H | 1982-05-13 | 2024-05-13 | N | 6 | ii,fff,jjj,ooo | Y
DC | Febco | 805Y | 1 | H | 1982-05-13 | 2024-05-13 | N | 6 | ii,fff,jjj,ooo | Y
DC | Febco | 805Y | 1.5 | H | 1983-01-05 | 2022-01-05 | N | 6 | ii,fff,jjj,ooo | Y
DC | Febco | 805Y | 2 | H | 1983-01-05 | 2022-01-05 | N | 6 | ii,fff,ooo | Y
DC | Febco | 805YB | 0.75 | H | 1994-05-04 | 2024-05-04 | N | 8 | (ii),fff,jjj,ooo | N |  |  | Replaceable seats beginning with Serial No. A105801
DC | Febco | 805YB | 0.75 | VU | 1996-04-16 | 2023-04-16 | N | 8 | (ii),fff,jjj,ooo | N |  |  | Replaceable seats beginning with Serial No. A105801
DC | Febco | 805YD | 2.5 | H | 1987-05-31 | 2023-05-31 | N | 7 | (ee),ff,ll,mm,oo,pp,tt,uu,zzz,ffff,gggg | Y |  |  | formerly 805 Type YD
DC | Febco | 805YD | 3 | H | 1987-05-31 | 2023-05-31 | N | 7 | (ee),ff,ll,mm,oo,pp,tt,uu,zzz,ffff,gggg | Y |  |  | formerly 805 Type YD
DC | Febco | 805YD | 4 | H | 1987-05-31 | 2023-05-31 | N | 7 | (ee),ff,ll,mm,oo,pp,tt,uu,zzz,ffff,gggg | Y |  |  | formerly 805 Type YD
DC | Febco | 805YD | 6 | H | 1987-05-31 | 2023-05-31 | N | 7 | (ee),ff,ll,mm,oo,pp,tt,uu,zzz,ffff,gggg | Y |  |  | formerly 805 Type YD
DC | Febco | 805YD | 8 | H | 1987-05-31 | 2023-05-31 | N | 7 | (ee),ff,ll,mm,oo,pp,tt,uu,zzz,ffff,gggg | Y |  |  | formerly 805 Type YD
DC | Febco | 805YD | 10 | H | 1987-05-31 | 2023-05-31 | N | 7 | (ee),ff,ll,mm,oo,pp,tt,uu,zzz,ffff,gggg | Y |  |  | formerly 805 Type YD
DC | Febco | 805YR | 0.75 | H | 1993-01-22 | 2023-01-22 | N | 8 | ii,fff,jjj,ooo | Y
DC | Febco | 805YR | 1 | H | 1993-01-22 | 2023-01-22 | N | 8 | ii,fff,jjj,ooo | Y
DC | Febco | 850F | 0.75 | H | 2001-09-28 | 2022-09-28 | N | 9 | fff,jjj | Y
DC | Febco | 850F | 0.75 | VD | 2001-09-28 | 2022-09-28 | N | 9 | (fff),jjj | N
DC | Febco | 850F | 0.75 | VU | 2001-09-28 | 2022-09-28 | N | 9 | (fff),jjj | N
DC | Febco | 850U | 0.5 | H | 1998-10-12 | 2022-10-12 | N | 9 | (kkk) | N
DC | Febco | 850U | 0.5 | VD | 2000-10-16 | 2024-10-16 | N | 9 | (kkk) | N
DC | Febco | 850U | 0.5 | VU | 1999-12-17 | 2023-12-17 | N | 9 | (kkk) | N
DC | Febco | 850U | 0.75 | H | 1999-03-08 | 2023-03-08 | N | 9 | (kkk) | N
DC | Febco | 850U | 0.75 | VD | 2000-10-16 | 2024-10-16 | N | 9 | (kkk) | N
DC | Febco | 850U | 0.75 | VU | 1999-12-17 | 2023-12-17 | N | 9 | (kkk) | N
DC | Febco | 850U | 1 | H | 1999-08-04 | 2023-08-04 | N | 9 | (kkk) | N
DC | Febco | 850U | 1 | VD | 2000-01-14 | 2024-01-14 | N | 9 | (kkk) | N
DC | Febco | 850U | 1 | VU | 2000-10-16 | 2024-10-16 | N | 9 | (kkk) | N
DC | Febco | 850U | 1.25 | H | 1998-10-12 | 2022-10-12 | N | 9 | (kkk) | N
DC | Febco | 850U | 1.25 | VD | 2000-10-16 | 2024-10-16 | N | 9 | (kkk) | N
DC | Febco | 850U | 1.25 | VU | 1999-08-04 | 2023-08-04 | N | 9 | (kkk) | N
DC | Febco | 850U | 1.5 | H | 1998-10-12 | 2022-10-12 | N | 9 | (kkk) | N
DC | Febco | 850U | 1.5 | VD | 2000-10-16 | 2024-10-16 | N | 9 | (kkk) | N
DC | Febco | 850U | 1.5 | VU | 1999-08-04 | 2023-08-04 | N | 9 | (kkk) | N
DC | Febco | 850U | 2 | H | 1998-10-12 | 2022-10-12 | N | 9 | (kkk) | N
DC | Febco | 850U | 2 | VD | 2000-10-16 | 2024-10-16 | N | 9 | (kkk) | N
DC | Febco | 850U | 2 | VU | 1999-08-04 | 2023-08-04 | N | 9 | (kkk) | N
DC | Febco | 870V | 2.5 | VUVD | 1996-03-08 | 2023-03-08 | N | 8 | (ee),ff,ll,mm,oo.pp,tt,uu,zzz,cccc,ffff,gggg | Y
DC | Febco | 870V | 2.5 | VUVU | 1996-03-08 | 2023-03-08 | N | 8 | (ee),ff,ll,mm,oo.pp,tt,uu,zzz,cccc,ffff,gggg | Y
DC | Febco | 870V | 3 | VUVD | 1996-03-08 | 2023-03-08 | N | 8 | (ee),ff,ll,mm,oo.pp,tt,uu,zzz,cccc,ffff,gggg | Y
DC | Febco | 870V | 3 | VUVU | 1996-03-08 | 2023-03-08 | N | 8 | (ee),ff,ll,mm,oo.pp,tt,uu,zzz,cccc,ffff,gggg | Y
DC | Febco | 870V | 4 | VUVD | 1996-03-08 | 2023-03-08 | N | 8 | (ee),ff,ll,mm,oo.pp,tt,uu,zzz,cccc,ffff,gggg | Y
DC | Febco | 870V | 4 | VUVU | 1996-03-08 | 2023-03-08 | N | 8 | (ee),ff,ll,mm,oo.pp,tt,uu,zzz,cccc,ffff,gggg | Y
DC | Febco | 870V | 6 | VUVD | 1996-03-08 | 2023-03-08 | N | 8 | (ee),ff,ll,mm,oo.pp,tt,uu,zzz,cccc,ffff,gggg | Y
DC | Febco | 870V | 6 | VUVU | 1996-03-08 | 2023-03-08 | N | 8 | (ee),ff,ll,mm,oo.pp,tt,uu,zzz,cccc,ffff,gggg | Y
DC | Febco | 870V | 8 | VUVD | 1997-01-06 | 2023-01-06 | N | 8 | (ee),ff,ll,mm,oo.pp,tt,uu,zzz,cccc,ffff,gggg | Y
DC | Febco | 870V | 8 | VUVU | 1997-01-06 | 2023-01-06 | N | 8 | (ee),ff,ll,mm,oo.pp,tt,uu,zzz,cccc,ffff,gggg | Y
DC | Febco | 870V | 10 | VUVD | 1997-07-11 | 2024-07-11 | N | 8 | (ee),ff,ll,mm,oo.pp,tt,uu,zzz,cccc,dddd,eeee,ffff,gggg,nnnnn | Y
DC | Febco | 870V | 10 | VUVU | 1997-07-11 | 2024-07-11 | N | 8 | (ee),ff,ll,mm,oo.pp,tt,uu,zzz,cccc,dddd,eeee,ffff,gggg,nnnnn | Y
DC | Febco | LF850 | 0.5 | H | 2010-02-18 | 2022-02-18 | Y | 9 | (qqqqq), hhhh | N
DC | Febco | LF850 | 0.5 | VD | 2019-07-31 | 2022-07-31 | Y | 9 | (qqqqq), hhhh | N
DC | Febco | LF850 | 0.5 | VU | 2019-07-31 | 2022-07-31 | Y | 9 | (qqqqq), hhhh | N
DC | Febco | LF850 | 0.75 | H | 2010-02-18 | 2022-02-18 | Y | 9 | (qqqqq), hhhh | N
DC | Febco | LF850 | 0.75 | VD | 2019-07-31 | 2022-07-31 | Y | 9 | (qqqqq), hhhh | N
DC | Febco | LF850 | 0.75 | VU | 2019-07-31 | 2022-07-31 | Y | 9 | (qqqqq), hhhh | N
DC | Febco | LF850 | 1 | H | 2010-02-18 | 2022-02-18 | Y | 9 | (qqqqq), hhhh | N
DC | Febco | LF850 | 1 | VD | 2019-07-31 | 2022-07-31 | Y | 9 | (qqqqq), hhhh | N
DC | Febco | LF850 | 1 | VU | 2019-07-31 | 2022-07-31 | Y | 9 | (qqqqq), hhhh | N
DC | Febco | LF850 | 1.25 | H | 2010-02-18 | 2022-02-18 | Y | 9 | (qqqqq), hhhh | N
DC | Febco | LF850 | 1.25 | VD | 2019-07-31 | 2022-07-31 | Y | 9 | (qqqqq), hhhh | N
DC | Febco | LF850 | 1.25 | VU | 2019-07-31 | 2022-07-31 | Y | 9 | (qqqqq), hhhh | N
DC | Febco | LF850 | 1.5 | H | 2010-02-18 | 2022-02-18 | Y | 9 | (qqqqq), hhhh | N
DC | Febco | LF850 | 1.5 | VD | 2019-07-31 | 2022-07-31 | Y | 9 | (qqqqq), hhhh | N
DC | Febco | LF850 | 1.5 | VU | 2019-07-31 | 2022-07-31 | Y | 9 | (qqqqq), hhhh | N
DC | Febco | LF850 | 2 | H | 2010-02-18 | 2022-02-18 | Y | 9 | (qqqqq), hhhh | N
DC | Febco | LF850 | 2 | VD | 2019-07-31 | 2022-07-31 | Y | 9 | (qqqqq), hhhh | N
DC | Febco | LF850 | 2 | VU | 2019-07-31 | 2022-07-31 | Y | 9 | (qqqqq), hhhh | N
DC | Febco | LF850 | 2.5 | H | 2012-05-22 | 2024-05-22 | Y | 9 | (mm),ll,oo,pp,zzz,cccc,dddd,eeee,ffff,gggg,nnnnn,zzzzzz,aaaaaaa | N
DC | Febco | LF850 | 2.5 | VU | 2012-05-22 | 2024-05-22 | Y | 9 | (mm),ll,oo,pp,zzz,cccc,dddd,eeee,ffff,gggg,nnnnn,zzzzzz,aaaaaaa | N
DC | Febco | LF850 | 3 | H | 2012-05-22 | 2024-05-22 | Y | 9 | (mm),ll,oo,pp,zzz,cccc,dddd,eeee,ffff,gggg,nnnnn,zzzzzz,aaaaaaa | N
DC | Febco | LF850 | 3 | VU | 2012-05-22 | 2024-05-22 | Y | 9 | (mm),ll,oo,pp,zzz,cccc,dddd,eeee,ffff,gggg,nnnnn,zzzzzz,aaaaaaa | N
DC | Febco | LF850 | 4 | H | 2012-05-22 | 2024-05-22 | Y | 9 | (mm),ll,oo,pp,zzz,cccc,dddd,eeee,ffff,gggg,nnnnn,zzzzzz,aaaaaaa | N
DC | Febco | LF850 | 4 | VU | 2012-05-22 | 2024-05-22 | Y | 9 | (mm),ll,oo,pp,zzz,cccc,dddd,eeee,ffff,gggg,nnnnn,zzzzzz,aaaaaaa | N
DC | Febco | LF850 | 6 | H | 2012-05-22 | 2024-05-22 | Y | 9 | (mm),ll,oo,pp,zzz,cccc,dddd,eeee,ffff,gggg,nnnnn,zzzzzz,aaaaaaa | N
DC | Febco | LF850 | 6 | VU | 2012-05-22 | 2024-05-22 | Y | 9 | (mm),ll,oo,pp,zzz,cccc,dddd,eeee,ffff,gggg,nnnnn,zzzzzz,aaaaaaa | N
DC | Febco | LF850 | 8 | H | 2012-05-22 | 2024-05-22 | Y | 9 | (mm),ll,oo,pp,zzz,cccc,dddd,eeee,ffff,gggg,nnnnn,zzzzzz,aaaaaaa | N
DC | Febco | LF850 | 8 | VU | 2012-05-22 | 2024-05-22 | Y | 9 | (mm),ll,oo,pp,zzz,cccc,dddd,eeee,ffff,gggg,nnnnn,zzzzzz,aaaaaaa | N
DC | Febco | LF850 | 10 | H | 2013-06-24 | 2022-06-24 | Y | 9 | (mm),ll,oo,pp,zzz,cccc,dddd,eeee,ffff,gggg,nnnnn | N
DC | Febco | LF850 | 10 | VU | 2013-06-24 | 2022-06-24 | Y | 9 | (mm),ll,oo,pp,zzz,cccc,dddd,eeee,ffff,gggg,nnnnn | N
DC | Febco | LF850U | 0.5 | H | 2013-09-03 | 2022-09-03 | Y | 9 | (ppppp), hhhh | N
DC | Febco | LF850U | 0.5 | VD | 2019-07-31 | 2022-07-31 | Y | 9 | (ppppp), hhhh | N
DC | Febco | LF850U | 0.5 | VU | 2019-07-31 | 2022-07-31 | Y | 9 | (ppppp), hhhh | N
DC | Febco | LF850U | 0.75 | H | 2013-09-03 | 2022-09-03 | Y | 9 | (ppppp), hhhh | N
DC | Febco | LF850U | 0.75 | VD | 2019-07-31 | 2022-07-31 | Y | 9 | (ppppp), hhhh | N
DC | Febco | LF850U | 0.75 | VU | 2019-07-31 | 2022-07-31 | Y | 9 | (ppppp), hhhh | N
DC | Febco | LF850U | 1 | H | 2013-09-03 | 2022-09-03 | Y | 9 | (ppppp), hhhh | N
DC | Febco | LF850U | 1 | VD | 2019-07-31 | 2022-07-31 | Y | 9 | (ppppp), hhhh | N
DC | Febco | LF850U | 1 | VU | 2019-07-31 | 2022-07-31 | Y | 9 | (ppppp), hhhh | N
DC | Febco | LF850U | 1.25 | H | 2013-09-03 | 2022-09-03 | Y | 9 | (ppppp), hhhh | N
DC | Febco | LF850U | 1.25 | VD | 2019-07-31 | 2022-07-31 | Y | 9 | (ppppp), hhhh | N
DC | Febco | LF850U | 1.25 | VU | 2019-07-31 | 2022-07-31 | Y | 9 | (ppppp), hhhh | N
DC | Febco | LF850U | 1.5 | H | 2013-09-03 | 2022-09-03 | Y | 9 | (ppppp), hhhh | N
DC | Febco | LF850U | 1.5 | VD | 2019-07-31 | 2022-07-31 | Y | 9 | (ppppp), hhhh | N
DC | Febco | LF850U | 1.5 | VU | 2019-07-31 | 2022-07-31 | Y | 9 | (ppppp), hhhh | N
DC | Febco | LF850U | 2 | H | 2013-09-03 | 2022-09-03 | Y | 9 | (ppppp), hhhh | N
DC | Febco | LF850U | 2 | VD | 2019-07-31 | 2022-07-31 | Y | 9 | (ppppp), hhhh | N
DC | Febco | LF850U | 2 | VU | 2019-07-31 | 2022-07-31 | Y | 9 | (ppppp), hhhh | N
DC | Febco | LF870V | 2.5 | VUVD | 2012-08-09 | 2024-08-09 | Y | 9 | (mm),ll,oo,pp,zzz,cccc,dddd,eeee,ffff,gggg,nnnnn,zzzzzz,aaaaaaa | N
DC | Febco | LF870V | 2.5 | VUVU | 2012-08-09 | 2024-08-09 | Y | 9 | (mm),ll,oo,pp,zzz,cccc,dddd,eeee,ffff,gggg,nnnnn,zzzzzz,aaaaaaa | N
DC | Febco | LF870V | 3 | VUVD | 2012-05-22 | 2024-05-22 | Y | 9 | (mm),ll,oo,pp,zzz,cccc,dddd,eeee,ffff,gggg,nnnnn,zzzzzz,aaaaaaa | N
DC | Febco | LF870V | 3 | VUVU | 2012-05-22 | 2024-05-22 | Y | 9 | (mm),ll,oo,pp,zzz,cccc,dddd,eeee,ffff,gggg,nnnnn,zzzzzz,aaaaaaa | N
DC | Febco | LF870V | 4 | VUVD | 2012-05-22 | 2024-05-22 | Y | 9 | (mm),ll,oo,pp,zzz,cccc,dddd,eeee,ffff,gggg,nnnnn,zzzzzz,aaaaaaa | N
DC | Febco | LF870V | 4 | VUVU | 2012-05-22 | 2024-05-22 | Y | 9 | (mm),ll,oo,pp,zzz,cccc,dddd,eeee,ffff,gggg,nnnnn,zzzzzz,aaaaaaa | N
DC | Febco | LF870V | 6 | VUVD | 2012-05-22 | 2024-05-22 | Y | 9 | (mm),ll,oo,pp,zzz,cccc,dddd,eeee,ffff,gggg,nnnnn,zzzzzz,aaaaaaa | N
DC | Febco | LF870V | 6 | VUVU | 2012-05-22 | 2024-05-22 | Y | 9 | (mm),ll,oo,pp,zzz,cccc,dddd,eeee,ffff,gggg,nnnnn,zzzzzz,aaaaaaa | N
DC | Febco | LF870V | 8 | VUVD | 2012-05-22 | 2024-05-22 | Y | 9 | (mm),ll,oo,pp,zzz,cccc,dddd,eeee,ffff,gggg,nnnnn,zzzzzz,aaaaaaa | N
DC | Febco | LF870V | 8 | VUVU | 2012-05-22 | 2024-05-22 | Y | 9 | (mm),ll,oo,pp,zzz,cccc,dddd,eeee,ffff,gggg,nnnnn,zzzzzz,aaaaaaa | N
DC | Febco | LF870V | 10 | VUVD | 2018-05-29 | 2024-05-29 | Y | 10 | (mm),ll,oo,pp,zzz,cccc,dddd,eeee,ffff,gggg,nnnnn | N
DC | Febco | LF870V | 10 | VUVU | 2018-05-29 | 2024-05-29 | Y | 10 | (mm),ll,oo,pp,zzz,cccc,dddd,eeee,ffff,gggg,nnnnn | N
DC | Febco | LF870W | 4 | VUVD | 2020-03-26 | 2023-03-26 | Y | 9 | (mm),ll,oo,pp,zzz,cccc,dddd,eeee,ffff,gggg,nnnnn,zzzzzz,aaaaaaa | N
DC | Febco | LF870W | 4 | VUVU | 2020-03-26 | 2023-03-26 | Y | 9 | (mm),ll,oo,pp,zzz,cccc,dddd,eeee,ffff,gggg,nnnnn,zzzzzz,aaaaaaa | N
DC | Febco | LF870W | 6 | VUVD | 2020-03-26 | 2023-03-26 | Y | 9 | (mm),ll,oo,pp,zzz,cccc,dddd,eeee,ffff,gggg,nnnnn,zzzzzz,aaaaaaa | N
DC | Febco | LF870W | 6 | VUVU | 2020-03-26 | 2023-03-26 | Y | 9 | (mm),ll,oo,pp,zzz,cccc,dddd,eeee,ffff,gggg,nnnnn,zzzzzz,aaaaaaa | N
DC | Febco | LF870W | 8 | VUVD | 2020-05-15 | 2023-05-15 | Y | 9 | (mm),ll,oo,pp,zzz,cccc,dddd,eeee,ffff,gggg,nnnnn,zzzzzz,aaaaaaa | N
DC | Febco | LF870W | 8 | VUVU | 2020-05-15 | 2023-05-15 | Y | 9 | (mm),ll,oo,pp,zzz,cccc,dddd,eeee,ffff,gggg,nnnnn,zzzzzz,aaaaaaa | N
DC | Febco | LF870W | 10 | VUVD | 2020-05-15 | 2023-05-15 | Y | 10 | (mm),ll,oo,pp,zzz,cccc,dddd,eeee,ffff,gggg,nnnnn | N
DC | Febco | LF870W | 10 | VUVU | 2020-05-15 | 2023-05-15 | Y | 10 | (mm),ll,oo,pp,zzz,cccc,dddd,eeee,ffff,gggg,nnnnn | N
DC | Febco | LF870WZ | 4 | VUVD | 2020-03-26 | 2023-03-26 | Y | 9 | (mm),ll,oo,pp,zzz,cccc,dddd,eeee,ffff,gggg,nnnnn,zzzzzz,aaaaaaa | N
DC | Febco | LF870WZ | 4 | VUVU | 2020-03-26 | 2023-03-26 | Y | 9 | (mm),ll,oo,pp,zzz,cccc,dddd,eeee,ffff,gggg,nnnnn,zzzzzz,aaaaaaa | N
DC | Febco | LF870WZ | 6 | VUVD | 2020-03-26 | 2023-03-26 | Y | 9 | (mm),ll,oo,pp,zzz,cccc,dddd,eeee,ffff,gggg,nnnnn,zzzzzz,aaaaaaa | N
DC | Febco | LF870WZ | 6 | VUVU | 2020-03-26 | 2023-03-26 | Y | 9 | (mm),ll,oo,pp,zzz,cccc,dddd,eeee,ffff,gggg,nnnnn,zzzzzz,aaaaaaa | N
DC | Febco | LF870WZ | 8 | VUVD | 2020-05-15 | 2023-05-15 | Y | 9 | (mm),ll,oo,pp,zzz,cccc,dddd,eeee,ffff,gggg,nnnnn,zzzzzz,aaaaaaa | N
DC | Febco | LF870WZ | 8 | VUVU | 2020-05-15 | 2023-05-15 | Y | 9 | (mm),ll,oo,pp,zzz,cccc,dddd,eeee,ffff,gggg,nnnnn,zzzzzz,aaaaaaa | N
DC | Febco | LF870WZ | 10 | VUVD | 2020-05-15 | 2023-05-15 | Y | 10 | (mm),ll,oo,pp,zzz,cccc,dddd,eeee,ffff,gggg,nnnnn | N
DC | Febco | LF870WZ | 10 | VUVU | 2020-05-15 | 2023-05-15 | Y | 10 | (mm),ll,oo,pp,zzz,cccc,dddd,eeee,ffff,gggg,nnnnn | N
DC | Neptune | [5 empty] | N | [5 empty] | See Wilkins
DC | Watts | 700 | 2.5 | H | 1981-01-10 | 2023-01-10 | N | 5 |  | Y
DC | Watts | 700 | 3 | H | 1981-01-10 | 2023-01-10 | N | 5 |  | Y
DC | Watts | 709 | 2.5 | H | 1986-06-12 | 2022-06-12 | N | 7 | (oo),gg,hh,ll,mm,pp,tt,uu,ww,yy,ffff,gggg | Y
DC | Watts | 709 | 3 | H | 1986-06-12 | 2022-06-12 | N | 7 | (oo),gg,hh,ll,mm,pp,tt,uu,ww,yy,eee,ffff,gggg | Y
DC | Watts | 709 | 4 | H | 1982-01-15 | 2024-01-15 | N | 6 | (oo),gg,hh,ll,mm,pp,tt,uu,ww,yy,eee,ffff,gggg | Y
DC | Watts | 709 | 4 | VU | 1996-03-11 | 2023-03-11 | N | 8 | (oo),gg,hh,ll,mm,pp,tt,uu,ww,yy,eee,ffff,gggg | Y
DC | Watts | 709 | 6 | H | 1982-05-18 | 2024-05-18 | N | 6 | (oo),gg,hh,ll,mm,pp,tt,uu,ww,yy,eee,ffff,gggg | Y
DC | Watts | 709 | 6 | VU | 1996-12-05 | 2023-12-05 | N | 8 | (oo),gg,hh,ll,mm,pp,tt,uu,ww,yy,eee,ffff,gggg | Y
DC | Watts | 709 | 8 | H | 1981-07-06 | 2023-07-06 | N | 6 | (oo),gg,hh,ll,mm,pp,tt,uu,ww,yy,eee,ffff,gggg | Y
DC | Watts | 709 | 8 | VU | 1996-12-05 | 2023-12-05 | N | 8 | (oo),gg,hh,ll,mm,pp,tt,uu,ww,yy,eee,ffff,gggg | Y
DC | Watts | 709 | 10 | H | 1983-03-16 | 2022-03-16 | N | 6 | (oo),gg,hh,ll,mm,pp,tt,uu,ww,yy,eee,ffff,gggg | Y
DC | Watts | 709 | 10 | VU | 1996-12-05 | 2023-12-05 | N | 8 | (oo),gg,hh,ll,mm,pp,tt,uu,ww,yy,eee,ffff,gggg | Y
DC | Watts | 757 | 2.5 | H | 2004-09-29 | 2022-09-29 | N | 9 | (ppp),qqq,aaaa,bbbb | N
DC | Watts | 757 | 2.5 | H | 2004-09-29 | 2022-09-29 | Y | 9 | yyy,zzz,dddd,eeee,gggg,kkkk,llll,mmmm,nnnn,nnnnn | N
DC | Watts | 757 | 2.5 | VU | 2004-09-29 | 2022-09-29 | N | 9 | (ppp),qqq,aaaa,bbbb | N
DC | Watts | 757 | 2.5 | VU | 2004-09-29 | 2022-09-29 | Y | 9 | yyy,zzz,dddd,eeee,gggg,kkkk,llll,mmmm,nnnn,nnnnn | N
DC | Watts | 757 | 3 | H | 2004-09-29 | 2022-09-29 | N | 9 | (ppp),qqq,aaaa,bbbb | N
DC | Watts | 757 | 3 | H | 2004-09-29 | 2022-09-29 | Y | 9 | yyy,zzz,dddd,eeee,gggg,kkkk,llll,mmmm,nnnn,nnnnn | N
DC | Watts | 757 | 3 | VU | 2004-09-29 | 2022-09-29 | N | 9 | (ppp),qqq,aaaa,bbbb | N
DC | Watts | 757 | 3 | VU | 2004-09-29 | 2022-09-29 | Y | 9 | yyy,zzz,dddd,eeee,gggg,kkkk,llll,mmmm,nnnn,nnnnn | N
DC | Watts | 757 | 4 | H | 2004-09-29 | 2022-09-29 | N | 9 | (ppp),qqq,aaaa,bbbb | N
DC | Watts | 757 | 4 | H | 2004-09-29 | 2022-09-29 | Y | 9 | yyy,zzz,dddd,eeee,gggg,kkkk,llll,mmmm,nnnn,nnnnn | N
DC | Watts | 757 | 4 | VU | 2004-09-29 | 2022-09-29 | N | 9 | (ppp),qqq,aaaa,bbbb | N
DC | Watts | 757 | 4 | VU | 2004-09-29 | 2022-09-29 | Y | 9 | yyy,zzz,dddd,eeee,gggg,kkkk,llll,mmmm,nnnn,nnnnn | N
DC | Watts | 757 | 6 | H | 2006-04-21 | 2024-04-21 | N | 9 | (ppp),qqq,aaaa,bbbb | N
DC | Watts | 757 | 6 | H | 2006-04-21 | 2024-04-21 | Y | 9 | yyy,zzz,dddd,eeee,gggg,kkkk,llll,mmmm,nnnn,nnnnn | N
DC | Watts | 757 | 6 | VU | 2006-04-21 | 2024-04-21 | N | 9 | (ppp),qqq,aaaa,bbbb | N
DC | Watts | 757 | 6 | VU | 2006-04-21 | 2024-04-21 | Y | 9 | yyy,zzz,dddd,eeee,gggg,kkkk,llll,mmmm,nnnn,nnnnn | N
DC | Watts | 757 | 8 | H | 2004-09-16 | 2022-09-16 | N | 9 | (ppp),qqq,aaaa,bbbb | N
DC | Watts | 757 | 8 | H | 2004-09-16 | 2022-09-16 | Y | 9 | yyy,zzz,dddd,eeee,gggg,kkkk,llll,mmmm,nnnn,nnnnn | N
DC | Watts | 757 | 8 | VU | 2006-02-10 | 2024-02-10 | N | 9 | (ppp),qqq,aaaa,bbbb | N
DC | Watts | 757 | 8 | VU | 2006-02-10 | 2024-02-10 | Y | 9 | yyy,zzz,dddd,eeee,gggg,kkkk,llll,mmmm,nnnn,nnnnn | N
DC | Watts | 757 | 10 | H | 2008-05-02 | 2023-05-02 | N | 9 | (ppp),qqq,aaaa,bbbb | N
DC | Watts | 757 | 10 | H | 2008-05-02 | 2023-05-02 | Y | 9 | yyy,zzz,dddd,eeee,gggg,kkkk,llll,mmmm,nnnn,nnnnn | N
DC | Watts | 757 | 10 | VU | 2008-05-02 | 2023-05-02 | N | 9 | (ppp),qqq,aaaa,bbbb | N
DC | Watts | 757 | 10 | VU | 2008-05-02 | 2023-05-02 | Y | 9 | yyy,zzz,dddd,eeee,gggg,kkkk,llll,mmmm,nnnn,nnnnn | N
DC | Watts | 767 | 2.5 | H | 2004-09-29 | 2022-09-29 | N | 9 | (ppp),qqq,yyy,zzz,aaaa,bbbb,dddd,eeee,gggg,kkkk,llll,mmmm,nnnn,nnnnn | N
DC | Watts | 767 | 2.5 | VU | 2004-09-29 | 2022-09-29 | N | 9 | (ppp),qqq,yyy,zzz,aaaa,bbbb,dddd,eeee,gggg,kkkk,llll,mmmm,nnnn,nnnnn | N
DC | Watts | 767 | 3 | H | 2004-09-29 | 2022-09-29 | N | 9 | (ppp),qqq,yyy,zzz,aaaa,bbbb,dddd,eeee,gggg,kkkk,llll,mmmm,nnnn,nnnnn | N
DC | Watts | 767 | 3 | VU | 2004-09-29 | 2022-09-29 | N | 9 | (ppp),qqq,yyy,zzz,aaaa,bbbb,dddd,eeee,gggg,kkkk,llll,mmmm,nnnn,nnnnn | N
DC | Watts | 767 | 4 | H | 2006-04-21 | 2024-04-21 | N | 9 | (ppp),qqq,yyy,zzz,aaaa,bbbb,dddd,eeee,gggg,kkkk,llll,mmmm,nnnn,nnnnn | N
DC | Watts | 767 | 4 | VU | 2006-04-21 | 2024-04-21 | N | 9 | (ppp),qqq,yyy,zzz,aaaa,bbbb,dddd,eeee,gggg,kkkk,llll,mmmm,nnnn,nnnnn | N
DC | Watts | 767 | 6 | H | 2004-09-16 | 2022-09-16 | N | 9 | (yyy),ppp,qqq,zzz,aaaa,bbbb,dddd,eeee,gggg,kkkk,llll,mmmm,nnnn,nnnnn | N
DC | Watts | 767 | 6 | VU | 2006-02-10 | 2024-02-10 | N | 9 | (yyy),ppp,qqq,zzz,aaaa,bbbb,dddd,eeee,gggg,kkkk,llll,mmmm,nnnn,nnnnn | N
DC | Watts | 767 | 8 | H | 2008-05-02 | 2023-05-02 | N | 9 | (yyy), ppp, qqq,zzz, aaaa, bbbb, dddd, eeee, ffff, gggg,nnnnn | N
DC | Watts | 767 | 8 | VU | 2008-05-02 | 2023-05-02 | N | 9 | (yyy), ppp, qqq,zzz, aaaa, bbbb, dddd, eeee, ffff, gggg,nnnnn | N
DC | Watts | 767 | 10 | H | 2008-10-20 | 2023-10-20 | N | 9 | (ppp),qqq,yyy,zzz,aaaa,bbbb,dddd,eeee,gggg | N
DC | Watts | 767 | 10 | VU | 2008-10-20 | 2023-10-20 | N | 9 | (ppp),qqq,yyy,zzz,aaaa,bbbb,dddd,eeee,gggg | N
DC | Watts | 770 | 8 | H | 1993-01-13 | 2023-01-13 | N | 8 | oo,gg,hh,ll,mm,pp,tt,uu,yy | Y
DC | Watts | 772 | 4 | H | 1992-07-01 | 2022-07-01 | N | 8 | oo,yy | Y
DC | Watts | 772 | 10 | H | 1993-01-13 | 2023-01-13 | N | 8 | oo,yy | Y
DC | Watts | 774 | 8 | H | 1996-09-16 | 2023-09-16 | N | 8 | (tt),ee,ff,gg,hh,pp,uu,ccc,ddd | N
DC | Watts | 774 | 8 | H | 1996-09-16 | 2023-09-16 | Y | 8 | ll,mm,oo,ffff,gggg | N
DC | Watts | 774 | 10 | H | 2001-02-16 | 2022-02-16 | Y | 8 | (ll),mm,ffff,gggg | N
DC | Watts | 774 | 12 | H | 2010-01-12 | 2022-01-12 | N | 9 | hh,gg | N
DC | Watts | 774 | 12 | H | 2010-01-12 | 2022-01-12 | Y | 9 | (ll),mm | N
DC | Watts | 774 | 12 | VU | 2011-03-21 | 2023-03-21 | N | 9 | pp, | N
DC | Watts | 774 | 12 | VU | 2011-03-21 | 2023-03-21 | Y | 9 | (ll),mm,oo | N
DC | Watts | 007 | 2.5 | H | 1990-09-30 | 2023-09-30 | N | 8 | (oo),gg,hh,ll,mm,pp,tt,uu,yy,ffff,gggg | Y
DC | Watts | 007 | 2.5 | VU | 1996-08-27 | 2023-08-27 | Y | 8 | (oo),gg,hh,ll,mm,pp,tt,uu,yy,ffff,gggg | Y
DC | Watts | 007 | 3 | H | 1990-09-30 | 2023-09-30 | N | 8 | (oo),gg,hh,ll,mm,pp,tt,uu,yy,eee,ffff,gggg | Y
DC | Watts | 007 | 3 | VU | 1996-08-27 | 2023-08-27 | Y | 8 | (oo),gg,hh,ll,mm,pp,tt,uu,yy,eee,ffff,gggg | Y
DC | Watts | 007M1-FP | 1 | H | 2009-09-01 | 2024-09-01 | Y | 9 | (eeeee) | N
DC | Watts | 007M1-FP | 2 | H | 2009-09-01 | 2024-09-01 | Y | 9 | (eeeee) | N
DC | Watts | 007M1PCQT | 0.75 | H | 1993-12-10 | 2023-12-10 | Y | 8 | (vv),xx,ooo,hhhh,pppp | N
DC | Watts | 007M1PCQT | 1 | H | 1993-12-10 | 2023-12-10 | Y | 8 | (vv),xx,ooo,hhhh,pppp | N
DC | Watts | 007M1PCQT | 1.5 | H | 1994-09-27 | 2024-09-27 | Y | 8 | vv,xx,ooo,hhhh,pppp | Y
DC | Watts | 007M1PCQT | 2 | H | 1994-09-27 | 2024-09-27 | N | 8 | (vv),xx,ooo,hhhh,pppp | N
DC | Watts | 007M1QT | 0.75 | H | 1991-02-26 | 2024-02-26 | N | 8 | vv,xx,ooo,hhhh,pppp | N |  |  | This assembly is only used as the by-pass assembly for DCDA assemblies
DC | Watts | 007M1QT | 1 | H | 1991-02-26 | 2024-02-26 | N | 8 | (vv),xx,ooo,hhhh,pppp | N |  |  | Upgraded to 9th Ed.
DC | Watts | 007M1QT | 1 | H | 1998-05-18 | 2022-05-18 | N | 9 | (vv),xx,ooo,hhhh,pppp | N |  |  | Previous 8th Ed. Approval
DC | Watts | 007M1QT | 1 | VU | 1998-05-18 | 2022-05-18 | N | 9 | (vv),xx,ooo,hhhh,pppp | N
DC | Watts | 007M1QT | 1.5 | H | 1992-06-30 | 2022-06-30 | N | 8 | vv,xx,ooo,hhhh,pppp | Y
DC | Watts | 007M1QT | 2 | H | 1992-06-30 | 2022-06-30 | N | 8 | (vv),xx,ooo,hhhh,pppp | N
DC | Watts | 007M1QT | 2 | VU | 1996-03-08 | 2023-03-08 | N | 8 | (vv),xx,ooo,hhhh,pppp | N
DC | Watts | 007M2-FP | 1.25 | H | 2009-09-01 | 2024-09-01 | N | 9 | (eeeee) | N
DC | Watts | 007M2-FP | 1.5 | H | 2009-09-01 | 2024-09-01 | N | 9 | (eeeee) | N
DC | Watts | 007M2PCQT | 1.25 | H | 1996-12-09 | 2023-12-09 | N | 8 | (vv),xx,ooo,hhhh,pppp | N
DC | Watts | 007M2PCQT | 1.25 | VU | 1996-12-09 | 2023-12-09 | N | 8 | (vv),xx,ooo,hhhh,pppp | N
DC | Watts | 007M2PCQT | 1.5 | H | 1994-09-12 | 2024-09-12 | N | 8 | (vv),xx,ooo,hhhh,pppp | N
DC | Watts | 007M2QT | 0.75 | H | 1993-04-05 | 2023-04-05 | N | 8 | (vv),xx,ooo,hhhh,pppp | N
DC | Watts | 007M2QT | 0.75 | VU | 1996-08-27 | 2023-08-27 | N | 8 | (vv),xx,ooo,hhhh,pppp | N
DC | Watts | 007M2QT | 1.25 | H | 1996-10-01 | 2023-10-01 | N | 8 | (vv),xx,ooo,hhhh,pppp | N
DC | Watts | 007M2QT | 1.25 | VU | 1996-10-01 | 2023-10-01 | N | 8 | (vv),xx,ooo,hhhh,pppp | N
DC | Watts | 007M2QT | 1.5 | H | 1994-05-24 | 2024-05-24 | N | 8 | (vv),xx,ooo,hhhh,pppp | N
DC | Watts | 007M2QT | 1.5 | VU | 1996-03-11 | 2023-03-11 | N | 8 | (vv),xx,ooo,hhhh,pppp | N
DC | Watts | 007M3-FP | 0.75 | H | 2009-09-01 | 2024-09-01 | N | 9 | (eeeee) | N
DC | Watts | 007M3QT | 0.75 | H | 1999-10-18 | 2023-10-18 | N | 9 | (vv),xx,ooo,hhhh,pppp | N
DC | Watts | 007M3QT | 0.75 | VU | 1999-10-18 | 2023-10-18 | N | 9 | (vv),xx,ooo,hhhh,pppp | N
DC | Watts | 007PCQT | 0.5 | H | 1995-02-17 | 2022-02-17 | N | 8 | (vv),xx,ooo,hhhh,pppp | N
DC | Watts | 007PCQT | 1.5 | H | 1994-09-27 | 2024-09-27 | N | 8 | vv,xx,ooo,hhhh,pppp | Y
DC | Watts | 007PCQT | 2 | H | 1994-09-27 | 2024-09-27 | N | 8 | vv,xx,ooo,hhhh,pppp | Y
DC | Watts | 007QT | 0.5 | H | 1993-12-06 | 2023-12-08 | N | 8 | (vv),xx,ooo,hhhh,pppp,rrrrr | N |  |  | Upgraded to 9th Ed.
DC | Watts | 007QT | 0.5 | H | 1997-06-16 | 2024-06-16 | N | 9 | (vv),xx,ooo,hhhh,pppp,rrrrr | N |  |  | Previous 8th Ed. Approval
DC | Watts | 007QT | 0.5 | VU | 1996-04-19 | 2023-04-19 | N | 8 | pppp,rrrrr | N |  |  | Upgraded to 9th Ed.
DC | Watts | 007QT | 0.5 | VU | 1997-06-16 | 2024-06-16 | N | 9 | (vv),xx,pppp,rrrrr | N |  |  | Previous 8th Ed. Approval
DC | Watts | 007QT | 0.75 | H | 1988-01-11 | 2024-01-11 | N | 7 | pppp,rrrrr | Y
DC | Watts | 007QT | 1 | H | 1988-01-11 | 2024-01-11 | N | 7 | pppp,rrrrr | Y
DC | Watts | 007QT | 1.5 | H | 1988-07-21 | 2024-07-21 | N | 7 | pppp,rrrrr | Y |  |  | Upgraded to 9th Ed.
DC | Watts | 007QT | 2 | H | 1988-07-21 | 2024-07-21 | N | 7 | pppp,rrrrr | Y |  |  | Upgraded to 9th Ed.
DC | Watts | 007SSM1PCQT | 0.75 | H | 1993-12-10 | 2023-12-10 | N | 8 | vv,xx,ooo,hhhh,pppp | Y
DC | Watts | 007SSM1PCQT | 1 | H | 1993-12-10 | 2023-12-10 | N | 8 | vv,xx,ooo,hhhh,pppp | Y
DC | Watts | 007SSM1QT | 0.75 | H | 1991-02-26 | 2024-02-26 | N | 8 | vv,xx,ooo,hhhh,pppp | Y
DC | Watts | 007SSM1QT | 1 | H | 1991-02-26 | 2024-02-26 | N | 8 | vv,xx,ooo,hhhh,pppp | Y
DC | Watts | 007SSPCQT | 1.5 | H | 1994-09-27 | 2024-09-27 | N | 8 | vv,xx,ooo,hhhh,pppp | Y
DC | Watts | 007SSPCQT | 2 | H | 1994-09-27 | 2024-09-27 | N | 8 | vv,xx,ooo,hhhh,pppp | Y
DC | Watts | 007SSQT | 0.75 | H | 1988-01-11 | 2024-01-11 | N | 7 | pppp | Y
DC | Watts | 007SSQT | 1 | H | 1988-01-11 | 2024-01-11 | N | 7 | pppp | Y
DC | Watts | 007SSQT | 1.5 | H | 1988-07-21 | 2024-07-21 | N | 7 | pppp | Y
DC | Watts | 007SSQT | 2 | H | 1988-07-21 | 2024-07-21 | N | 7 | pppp | Y
DC | Watts | 709BB | 2.5 | H | 1982-07-20 | 2024-07-20 | N | 6 | (oo),gg,hh,ll,mm,pp,tt,uu,yy,ffff,gggg | Y
DC | Watts | 709BB | 3 | H | 1982-07-20 | 2024-07-20 | N | 6 | (oo),gg,hh,ll,mm,pp,tt,uu,yy,ffff,gggg | Y
DC | Watts | 709QT | 0.75 | H | 1982-08-04 | 2024-08-04 | N | 6 | vv,xx,ooo,hhhh,pppp | Y |  |  | Formerly Model 709
DC | Watts | 709QT | 1 | H | 1982-08-04 | 2024-08-04 | N | 6 | vv,xx,ooo,hhhh,pppp | Y |  |  | Formerly Model 709
DC | Watts | 709QT | 1.5 | H | 1982-04-27 | 2024-04-21 | N | 6 | vv,xx,ooo,hhhh,pppp | Y |  |  | Formerly Model 709
DC | Watts | 709QT | 2 | H | 1982-04-27 | 2024-04-21 | N | 6 | vv,xx,ooo,hhhh,pppp | Y |  |  | Formerly Model 709
DC | Watts | 719AQT | 0.5 | VUVD | 2005-10-04 | 2023-10-04 | N | 9 | (vv),xx,ooo,hhhh,pppp,rrrrr | N
DC | Watts | 719AQT | 1 | VUVD | 2005-10-04 | 2023-10-04 | N | 9 | (vv),xx,ooo,hhhh,pppp,rrrrr | N
DC | Watts | 719AQT | 1.25 | VUVD | 2005-10-04 | 2023-10-04 | N | 9 | (vv),xx,ooo,hhhh,pppp,rrrrr | N
DC | Watts | 719AQT | 1.5 | VUVD | 2005-10-04 | 2023-10-04 | N | 9 | (vv),xx,ooo,hhhh,pppp,rrrrr | N
DC | Watts | 719AQT | 2 | VUVD | 2005-10-04 | 2023-10-04 | N | 9 | (vv),xx,ooo,hhhh,pppp,rrrrr | N
DC | Watts | 719AQTR10 | 0.5 | VUVD | 2013-07-03 | 2022-07-03 | N | 9 | (vv),xx,ooo,hhhh,pppp | Y
DC | Watts | 719AQTR10 | 0.75 | VUVD | 2013-07-03 | 2022-07-03 | N | 9 | (vv),xx,ooo,hhhh,pppp | Y
DC | Watts | 719QT | 0.5 | H | 2005-10-04 | 2023-10-04 | N | 9 | (vv),xx,ooo,hhhh,pppp,rrrrr | N
DC | Watts | 719QT | 0.5 | VD | 2005-10-04 | 2023-10-04 | N | 9 | (vv),xx,ooo,hhhh,pppp,rrrrr | N
DC | Watts | 719QT | 0.5 | VU | 2005-10-04 | 2023-10-04 | N | 9 | (vv),xx,ooo,hhhh,pppp,rrrrr | N
DC | Watts | 719QT | 0.75 | H | 2005-10-04 | 2023-10-04 | N | 9 | (vv),xx,ooo,hhhh,pppp,rrrrr | N
DC | Watts | 719QT | 0.75 | VD | 2005-10-04 | 2023-10-04 | N | 9 | (vv),xx,ooo,hhhh,pppp,rrrrr | N
DC | Watts | 719QT | 0.75 | VU | 2005-10-04 | 2023-10-04 | N | 9 | (vv),xx,ooo,hhhh,pppp,rrrrr | N
DC | Watts | 719QT | 1 | H | 2005-10-04 | 2023-10-04 | N | 9 | (vv),xx,ooo,hhhh,pppp,rrrrr | N
DC | Watts | 719QT | 1 | VD | 2005-10-04 | 2023-10-04 | N | 9 | (vv),xx,ooo,hhhh,pppp,rrrrr | N
DC | Watts | 719QT | 1 | VU | 2005-10-04 | 2023-10-04 | N | 9 | (vv),xx,ooo,hhhh,pppp,rrrrr | N
DC | Watts | 719QT | 1.25 | H | 2005-10-04 | 2023-10-04 | N | 9 | (vv),xx,ooo,hhhh,pppp,rrrrr | N
DC | Watts | 719QT | 1.25 | VD | 2005-10-04 | 2023-10-04 | N | 9 | (vv),xx,ooo,hhhh,pppp,rrrrr | N
DC | Watts | 719QT | 1.25 | VU | 2005-10-04 | 2023-10-04 | N | 9 | (vv),xx,ooo,hhhh,pppp,rrrrr | N
DC | Watts | 719QT | 1.5 | H | 2005-10-04 | 2023-10-04 | N | 9 | (vv),xx,ooo,hhhh,pppp,rrrrr | N
DC | Watts | 719QT | 1.5 | VD | 2005-10-04 | 2023-10-04 | N | 9 | (vv),xx,ooo,hhhh,pppp,rrrrr | N
DC | Watts | 719QT | 1.5 | VU | 2005-10-04 | 2023-10-04 | N | 9 | (vv),xx,ooo,hhhh,pppp,rrrrr | N
DC | Watts | 719QT | 2 | H | 2005-10-04 | 2023-10-04 | N | 9 | (vv),xx,ooo,hhhh,pppp,rrrrr | N
DC | Watts | 719QT | 2 | VD | 2005-10-04 | 2023-10-04 | N | 9 | (vv),xx,ooo,hhhh,pppp,rrrrr | N
DC | Watts | 719QT | 2 | VU | 2005-10-04 | 2023-10-04 | N | 9 | (vv),xx,ooo,hhhh,pppp,rrrrr | N
DC | Watts | 719QTR10 | 0.5 | H | 2005-10-04 | 2023-10-04 | N | 9 | (vv),xx,ooo,hhhh,pppp,rrrrrr | Y
DC | Watts | 719QTR10 | 0.5 | VD | 2005-10-04 | 2023-10-04 | N | 9 | (vv),xx,ooo,hhhh,pppp,rrrrrr | Y
DC | Watts | 719QTR10 | 0.5 | VU | 2005-10-04 | 2023-10-04 | N | 9 | (vv),xx,ooo,hhhh,pppp,rrrrrr | Y
DC | Watts | 719QTR10 | 0.75 | H | 2005-10-04 | 2023-10-04 | N | 9 | (vv),xx,ooo,hhhh,pppp,rrrrrr | Y
DC | Watts | 719QTR10 | 0.75 | VD | 2005-10-04 | 2023-10-04 | N | 9 | (vv),xx,ooo,hhhh,pppp,rrrrrr | Y
DC | Watts | 719QTR10 | 0.75 | VU | 2005-10-04 | 2023-10-04 | N | 9 | (vv),xx,ooo,hhhh,pppp,rrrrrr | Y
DC | Watts | 757a | 2.5 | H | 2002-10-07 | 2023-10-07 | N | 9 | (ppp),qqq,yyy,zzz,aaaa,bbbb,dddd,eeee,gggg,kkkk,llll,mmmm,nnnn,nnnnn | Y
DC | Watts | 757a | 2.5 | VU | 2002-10-07 | 2023-10-07 | N | 9 | (ppp),qqq,yyy,zzz,aaaa,bbbb,dddd,eeee,gggg,kkkk,llll,mmmm,nnnn,nnnnn | Y
DC | Watts | 757a | 3 | H | 2002-10-07 | 2023-10-07 | N | 9 | (ppp),qqq,yyy,zzz,aaaa,bbbb,dddd,eeee,gggg,kkkk,llll,mmmm,nnnn,nnnnn | Y
DC | Watts | 757a | 3 | VU | 2002-10-07 | 2023-10-07 | N | 9 | (ppp),qqq,yyy,zzz,aaaa,bbbb,dddd,eeee,gggg,kkkk,llll,mmmm,nnnn,nnnnn | Y
DC | Watts | 757a | 4 | H | 2002-10-07 | 2023-10-07 | N | 9 | (ppp),qqq,yyy,zzz,aaaa,bbbb,dddd,eeee,gggg,kkkk,llll,mmmm,nnnn,nnnnn | Y
DC | Watts | 757a | 4 | VU | 2002-10-07 | 2023-10-07 | N | 9 | (ppp),qqq,yyy,zzz,aaaa,bbbb,dddd,eeee,gggg,kkkk,llll,mmmm,nnnn,nnnnn | Y
DC | Watts | 757a | 6 | H | 2003-07-03 | 2024-07-03 | N | 9 | (ppp),qqq,yyy,zzz,aaaa,bbbb,dddd,eeee,gggg,kkkk,llll,mmmm,nnnn,nnnnn | Y
DC | Watts | 757a | 6 | VU | 2003-07-03 | 2024-07-03 | N | 9 | (ppp),qqq,yyy,zzz,aaaa,bbbb,dddd,eeee,gggg,kkkk,llll,mmmm,nnnn,nnnnn | Y
DC | Watts | 757N | 2.5 | VUVD | 2009-04-07 | 2024-04-07 | N | 9 | (ppp),qqq,nnnnn | N
DC | Watts | 757N | 2.5 | VUVD | 2009-04-07 | 2024-04-07 | Y | 9 | yyy,zzz,dddd,eeee,dddd,gggg,kkkk,llll,mmmm,nnnn | N
DC | Watts | 757N | 3 | VUVD | 2009-04-07 | 2024-04-07 | N | 9 | (ppp),qqq,nnnnn | N
DC | Watts | 757N | 3 | VUVD | 2009-04-07 | 2024-04-07 | Y | 9 | yyy,zzz,dddd,eeee,dddd,gggg,kkkk,llll,mmmm,nnnn | N
DC | Watts | 757N | 4 | VUVD | 2009-04-07 | 2024-04-07 | N | 9 | (ppp),qqq,nnnnn | N
DC | Watts | 757N | 4 | VUVD | 2009-04-07 | 2024-04-07 | Y | 9 | yyy,zzz,dddd,eeee,dddd,gggg,kkkk,llll,mmmm,nnnn | N
DC | Watts | 757N | 6 | VUVD | 2009-04-07 | 2024-04-07 | N | 9 | (ppp),qqq,nnnnn | N
DC | Watts | 757N | 6 | VUVD | 2009-04-07 | 2024-04-07 | Y | 9 | yyy,zzz,dddd,eeee,dddd,gggg,kkkk,llll,mmmm,nnnn | N
DC | Watts | 757N | 8 | VUVD | 2013-01-03 | 2022-01-03 | N | 9 | ppp,qqq,aaaa,bbbb | N
DC | Watts | 757N | 8 | VUVD | 2013-01-03 | 2022-01-03 | Y | 9 | yyy, zzz,dddd,eeee,gggg,kkkk,llll,mmmm,nnnn | N
DC | Watts | 757N | 10 | VUVD | 2009-09-01 | 2024-09-01 | N | 9 | (ppp),qqq | N
DC | Watts | 757N | 10 | VUVD | 2009-09-01 | 2024-09-01 | Y | 9 | yyy,zzz,dddd,eeee,dddd,gggg,kkkk,llll,mmmm,nnnn | N
DC | Watts | 757Na | 2.5 | VUVD | 2003-03-20 | 2024-03-20 | N | 9 | (ppp),qqq,yyy,zzz,aaaa,bbbb,dddd,eeee,gggg,kkkk,llll,mmmm,nnnn,nnnnn | Y
DC | Watts | 757Na | 3 | VUVD | 2003-03-20 | 2024-03-20 | N | 9 | (ppp),qqq,yyy,zzz,aaaa,bbbb,dddd,eeee,gggg,kkkk,llll,mmmm,nnnn,nnnnn | Y
DC | Watts | 757Na | 4 | VUVD | 2003-03-20 | 2024-03-20 | N | 9 | (ppp),qqq,yyy,zzz,aaaa,bbbb,dddd,eeee,gggg,kkkk,llll,mmmm,nnnn,nnnnn | Y
DC | Watts | 757Na | 6 | VUVD | 2003-07-03 | 2024-07-03 | N | 9 | (ppp),qqq,yyy,zzz,aaaa,bbbb,dddd,eeee,gggg,kkkk,llll,mmmm,nnnn,nnnnn | Y
DC | Watts | 757NQT | 2.5 | VUVD | 2009-12-04 | 2024-12-04 | Y | 9 | fffff | N
DC | Watts | 757NQT | 3 | VUVD | 2009-12-04 | 2024-12-04 | Y | 9 | fffff | N
DC | Watts | 757NQT | 4 | VUVD | 2009-12-04 | 2024-12-04 | Y | 9 | fffff | N
DC | Watts | 757QT | 2.5 | H | 2009-12-04 | 2024-12-04 | Y | 9 | fffff | N
DC | Watts | 757QT | 2.5 | VU | 2009-12-04 | 2024-12-04 | Y | 9 | fffff | N
DC | Watts | 757QT | 3 | H | 2009-12-04 | 2024-12-04 | Y | 9 | fffff | N
DC | Watts | 757QT | 3 | VU | 2009-12-04 | 2024-12-04 | Y | 9 | fffff | N
DC | Watts | 757QT | 4 | H | 2009-12-04 | 2024-12-04 | Y | 9 | fffff | N
DC | Watts | 757QT | 4 | VU | 2009-12-04 | 2024-12-04 | Y | 9 | fffff | N
DC | Watts | 767a | 2.5 | H | 2002-10-07 | 2023-10-07 | N | 9 | (ppp),qqq,yyy,zzz,aaaa,bbbb,dddd,eeee,gggg,kkkk,llll,mmmm,nnnn,nnnnn | Y
DC | Watts | 767a | 2.5 | VU | 2002-10-07 | 2023-10-07 | N | 9 | (ppp),qqq,yyy,zzz,aaaa,bbbb,dddd,eeee,gggg,kkkk,llll,mmmm,nnnn,nnnnn | Y
DC | Watts | 767a | 3 | H | 2002-10-07 | 2023-10-07 | N | 9 | (ppp),qqq,yyy,zzz,aaaa,bbbb,dddd,eeee,gggg,kkkk,llll,mmmm,nnnn,nnnnn | Y
DC | Watts | 767a | 3 | VU | 2002-10-07 | 2023-10-07 | N | 9 | (ppp),qqq,yyy,zzz,aaaa,bbbb,dddd,eeee,gggg,kkkk,llll,mmmm,nnnn,nnnnn | Y
DC | Watts | 767a | 4 | H | 2003-07-03 | 2024-07-03 | N | 9 | (ppp),qqq,yyy,zzz,aaaa,bbbb,dddd,eeee,gggg,kkkk,llll,mmmm,nnnn,nnnnn | Y
DC | Watts | 767a | 4 | VU | 2003-07-03 | 2024-07-03 | N | 9 | (ppp),qqq,yyy,zzz,aaaa,bbbb,dddd,eeee,gggg,kkkk,llll,mmmm,nnnn,nnnnn | Y
DC | Watts | 767N | 2.5 | VUVD | 2009-04-07 | 2024-04-07 | N | 9 | (ppp),qqq,yyy,zzz,dddd,eeee,dddd,gggg,kkkk,llll,mmmm,nnnn,nnnnn | N
DC | Watts | 767N | 3 | VUVD | 2009-04-07 | 2024-04-07 | N | 9 | (ppp),qqq,yyy,zzz,dddd,eeee,dddd,gggg,kkkk,llll,mmmm,nnnn,nnnnn | N
DC | Watts | 767N | 4 | VUVD | 2009-04-07 | 2024-04-07 | N | 9 | (ppp),qqq,yyy,zzz,dddd,eeee,dddd,gggg,kkkk,llll,mmmm,nnnn,nnnnn | N
DC | Watts | 767N | 6 | VUVD | 2013-01-03 | 2022-01-03 | N | 9 | ppp,qqq,aaaa,bbbb | N
DC | Watts | 767N | 6 | VUVD | 2013-01-03 | 2022-01-03 | Y | 9 | yyy,zzz,dddd,eeee,gggg,kkkk,llll,mmmm,nnnn | N
DC | Watts | 767N | 8 | VUVD | 2009-09-01 | 2024-09-01 | N | 9 | (ppp),qqq,yyy,zzz,dddd,eeee,dddd,gggg,kkkk,llll,mmmm,nnnn,nnnnn | N
DC | Watts | 767Na | 2.5 | VUVD | 2003-03-20 | 2024-03-20 | N | 9 | (ppp),qqq,yyy,zzz,aaaa,bbbb,dddd,eeee,gggg,kkkk,llll,mmmm,nnnn,nnnnn | Y
DC | Watts | 767Na | 3 | VUVD | 2003-03-20 | 2024-03-20 | N | 9 | (ppp),qqq,yyy,zzz,aaaa,bbbb,dddd,eeee,gggg,kkkk,llll,mmmm,nnnn,nnnnn | Y
DC | Watts | 767Na | 4 | VUVD | 2003-07-03 | 2024-07-03 | N | 9 | (ppp),qqq,yyy,zzz,aaaa,bbbb,dddd,eeee,gggg,kkkk,llll,mmmm,nnnn,nnnnn | Y
DC | Watts | 770 | 4 | H | 1992-05-20 | 2022-05-20 | N | 8 | oo,gg,hh,ll,mm,pp,tt,uu,yy | Y
DC | Watts | 770QTFDA | 4 | H | 1993-01-12 | 2023-01-12 | N | 8 | ww | Y
DC | Watts | 770QTFDA | 8 | H | 1993-01-12 | 2023-01-12 | N | 8 | ww | Y
DC | Watts | 774 | 2.5 | H | 1991-07-11 | 2024-07-11 | N | 8 | (tt),ee,ff,gg,hh,pp,uu,ccc,ddd | N
DC | Watts | 774 | 2.5 | H | 1991-07-11 | 2024-07-11 | Y | 8 | ll,mm,oo,ffff,gggg | N
DC | Watts | 774 | 3 | H | 1991-07-11 | 2024-07-11 | N | 8 | (tt),ee,ff,gg,hh,pp,uu,ccc,ddd | N
DC | Watts | 774 | 3 | H | 1991-07-11 | 2024-07-11 | Y | 8 | ll,mm,oo,ffff,gggg | N
DC | Watts | 774 | 4 | H | 1991-07-11 | 2024-07-11 | N | 8 | (tt),ee,ff,gg,hh,pp,uu,ccc,ddd | N
DC | Watts | 774 | 4 | H | 1991-07-11 | 2024-07-11 | Y | 8 | ll,mm,oo,ffff,gggg | N
DC | Watts | 774 | 6 | H | 1992-09-09 | 2022-09-09 | N | 8 | (tt),ee,ff,gg,hh,pp,uu,ccc,ddd | N
DC | Watts | 774 | 6 | H | 1992-09-09 | 2022-09-09 | Y | 8 | ll,mm,oo,ffff,gggg | N
DC | Watts | 774X | 2.5 | H | 1996-09-10 | 2023-09-10 | N | 8 | (mm),ee,ff,gg,hh,ll,oo,pp,tt,uu,ccc,ddd,ffff,gggg | Y
DC | Watts | 774X | 6 | H | 1993-11-22 | 2023-11-22 | N | 8 | tt,ee,ff,gg,hh,ll,mm,oo,pp,uu,ccc,ddd,ffff,gggg | Y
DC | Watts | 774X | 8 | H | 1992-09-09 | 2022-09-09 | N | 8 | tt,ee,ff,gg,hh,ll,mm,oo,pp,uu,ccc,ddd,ffff,gggg | Y
DC | Watts | 775QT | 0.5 | H | 2000-02-01 | 2024-02-01 | N | 9 | int | Y
DC | Watts | 775QT | 0.5 | VU | 2000-02-01 | 2024-02-01 | N | 9 | int | Y
DC | Watts | 775QT | 0.75 | H | 2000-02-01 | 2024-02-01 | N | 9 | int | Y
DC | Watts | 775QT | 0.75 | VU | 2000-02-01 | 2024-02-01 | N | 9 | int | Y
DC | Watts | 775QT | 1 | H | 1999-08-12 | 2023-08-12 | N | 9 | int | Y
DC | Watts | 775QT | 1 | VU | 1999-08-12 | 2023-08-12 | N | 9 | int | Y
DC | Watts | 775QT | 1.25 | H | 2000-09-07 | 2024-09-07 | N | 9 | int | Y
DC | Watts | 775QT | 1.25 | VU | 2000-09-07 | 2024-09-07 | N | 9 | int | Y
DC | Watts | 775QT | 1.5 | H | 2000-09-07 | 2024-09-07 | N | 9 | int | Y
DC | Watts | 775QT | 1.5 | VU | 2000-09-07 | 2024-09-07 | N | 9 | int | Y
DC | Watts | 775QT | 2 | H | 2002-03-28 | 2023-03-28 | N | 9 | int | Y
DC | Watts | 775QT | 2 | VU | 2002-03-28 | 2023-03-28 | N | 9 | int | Y
DC | Watts | LF007 | 2.5 | H | 2010-01-12 | 2022-01-12 | Y | 9 | (oo) | N
DC | Watts | LF007 | 3 | H | 2010-01-12 | 2022-01-12 | Y | 9 | (oo) | N
DC | Watts | LF007IOT | 2.5 | H | 2022-12-08 |  | Y | 9 | (oo) | N
DC | Watts | LF007IOT | 3 | H | 2022-12-08 |  | Y | 9 | (oo) | N
DC | Watts | LF007IOTQT | 0.5 | H | 2021-02-25 | 2024-02-25 | Y | 9 | (hhhh),rrrrr | N
DC | Watts | LF007IOTQT | 0.5 | VU | 2021-02-25 | 2024-02-25 | Y | 9 | (hhhh),rrrrr | N
DC | Watts | LF007M1IOTQT | 1 | H | 2021-02-25 | 2024-02-25 | Y | 9 | (hhhh),rrrrr | N
DC | Watts | LF007M1IOTQT | 1 | VU | 2021-02-25 | 2024-02-25 | Y | 9 | (hhhh),rrrrr | N
DC | Watts | LF007M1IOTQT | 2 | H | 2021-02-25 | 2024-02-25 | Y | 9 | (hhhh),rrrrr | N
DC | Watts | LF007M1IOTQT | 2 | VU | 2021-02-25 | 2024-02-25 | Y | 9 | (hhhh),rrrrr | N
DC | Watts | LF007M1PCQT | 1 | H | 2015-03-13 | 2024-03-13 | Y | 9 | (hhhh),rrrrr | N
DC | Watts | LF007M1PCQT | 1 | VU | 2015-03-13 | 2024-03-13 | Y | 9 | (hhhh),rrrrr | N
DC | Watts | LF007M1PCQT | 2 | H | 2015-03-13 | 2024-03-13 | Y | 9 | (hhhh),rrrrr | N
DC | Watts | LF007M1PCQT | 2 | VU | 2015-03-13 | 2024-03-13 | Y | 9 | (hhhh),rrrrr | N
DC | Watts | LF007M1QT | 1 | H | 2008-01-11 | 2023-01-11 | Y | 9 | (hhhh),rrrrr | N
DC | Watts | LF007M1QT | 1 | VU | 2008-01-11 | 2023-01-11 | Y | 9 | (hhhh),rrrrr | N
DC | Watts | LF007M1QT | 2 | H | 2008-01-11 | 2023-01-11 | Y | 9 | (hhhh),rrrrr | N
DC | Watts | LF007M1QT | 2 | VU | 2008-01-11 | 2023-01-11 | Y | 9 | (hhhh),rrrrr | N
DC | Watts | LF007M2QT | 1.25 | H | 2008-01-11 | 2023-01-11 | Y | 8 | (hhhh),rrrrr | N
DC | Watts | LF007M2QT | 1.25 | VU | 2008-01-11 | 2023-01-11 | Y | 8 | (hhhh),rrrrr | N
DC | Watts | LF007M2QT | 1.5 | H | 2008-01-11 | 2023-01-11 | Y | 8 | (hhhh),rrrrr | N
DC | Watts | LF007M2QT | 1.5 | VU | 2008-01-11 | 2023-01-11 | Y | 8 | (hhhh),rrrrr | N
DC | Watts | LF007M3IOTQT | 0.75 | H | 2021-02-25 | 2024-02-25 | Y | 9 | (hhhh),rrrrr | N
DC | Watts | LF007M3IOTQT | 0.75 | VU | 2021-02-25 | 2024-02-25 | Y | 9 | (hhhh),rrrrr | N
DC | Watts | LF007M3PCQT | 0.75 | H | 2015-03-13 | 2024-03-13 | Y | 9 | (hhhh),rrrrr | N
DC | Watts | LF007M3PCQT | 0.75 | VU | 2015-03-13 | 2024-03-13 | Y | 9 | (hhhh),rrrrr | N
DC | Watts | LF007M3QT | 0.75 | H | 2008-01-11 | 2023-01-11 | Y | 9 | (hhhh),rrrrr | N
DC | Watts | LF007M3QT | 0.75 | VU | 2008-01-11 | 2023-01-11 | Y | 9 | (hhhh),rrrrr | N
DC | Watts | LF007PCQT | 0.5 | H | 2015-03-13 | 2024-03-13 | Y | 9 | (hhhh),rrrrr | N
DC | Watts | LF007PCQT | 0.5 | VU | 2015-03-13 | 2024-03-13 | Y | 9 | (hhhh),rrrrr | N
DC | Watts | LF007QT | 0.5 | H | 2008-01-11 | 2023-01-11 | Y | 9 | (hhhh),rrrrr | N
DC | Watts | LF007QT | 0.5 | VU | 2008-01-11 | 2023-01-11 | Y | 9 | (hhhh),rrrrr | N
DC | Watts | LF709 | 2.5 | H | 2010-01-12 | 2022-01-12 | Y | 9 | (ll),mm,oo,pp,zzz,cccc,dddd,eeee,ffff,gggg,nnnnn,zzzzzz,aaaaaaa | N
DC | Watts | LF709 | 3 | H | 2010-01-12 | 2022-01-12 | Y | 9 | (ll),mm,oo,pp,zzz,cccc,dddd,eeee,ffff,gggg,nnnnn,zzzzzz,aaaaaaa | N
DC | Watts | LF709 | 4 | H | 2012-07-27 | 2024-07-27 | Y | 9 | (ll),mm,oo,pp,zzz,cccc,dddd,eeee,ffff,gggg,nnnnn,zzzzzz,aaaaaaa | N
DC | Watts | LF709 | 4 | VU | 2012-07-27 | 2024-07-27 | Y | 9 | (ll),mm,oo,pp,zzz,cccc,dddd,eeee,ffff,gggg,nnnnn,zzzzzz,aaaaaaa | N
DC | Watts | LF709 | 6 | H | 2012-07-27 | 2024-07-27 | Y | 9 | (ll),mm,oo,pp,zzz,cccc,dddd,eeee,ffff,gggg,nnnnn,zzzzzz,aaaaaaa | N
DC | Watts | LF709 | 6 | VU | 2012-07-27 | 2024-07-27 | Y | 9 | (ll),mm,oo,pp,zzz,cccc,dddd,eeee,ffff,gggg,nnnnn,zzzzzz,aaaaaaa | N
DC | Watts | LF709 | 8 | H | 2010-07-01 | 2022-07-01 | Y | 9 | (ll),mm,oo,pp,zzz,cccc,dddd,eeee,ffff,gggg,nnnnn,zzzzzz,aaaaaaa | N
DC | Watts | LF709 | 8 | VU | 2010-07-01 | 2022-07-01 | Y | 9 | (ll),mm,oo,pp,zzz,cccc,dddd,eeee,ffff,gggg,nnnnn,zzzzzz,aaaaaaa | N
DC | Watts | LF709 | 10 | H | 2010-07-01 | 2022-07-01 | Y | 9 | (ll),mm,oo,pp,zzz,cccc,dddd,eeee,ffff,gggg,nnnnn | N
DC | Watts | LF709 | 10 | VU | 2010-07-01 | 2022-07-01 | Y | 9 | (ll),mm,oo,pp,zzz,cccc,dddd,eeee,ffff,gggg,nnnnn | N
DC | Watts | LF709IOT | 2.5 | H | 2022-12-08 |  | Y | 9 | (ll),oo,dddd,eeee,nnnnn,zzzzzz,aaaaaaa | N
DC | Watts | LF709IOT | 3 | H | 2022-12-08 |  | Y | 9 | (ll),oo,dddd,eeee,nnnnn,zzzzzz,aaaaaaa | N
DC | Watts | LF709IOT | 4 | H | 2022-12-08 |  | Y | 9 | (ll),oo,dddd,eeee,nnnnn,zzzzzz,aaaaaaa | N
DC | Watts | LF709IOT | 4 | VU | 2022-12-08 |  | Y | 9 | (ll),oo,dddd,eeee,nnnnn,zzzzzz,aaaaaaa | N
DC | Watts | LF709IOT | 6 | H | 2022-12-08 |  | Y | 9 | (ll),oo,dddd,eeee,nnnnn,zzzzzz,aaaaaaa | N
DC | Watts | LF709IOT | 6 | VU | 2022-12-08 |  | Y | 9 | (ll),oo,dddd,eeee,nnnnn,zzzzzz,aaaaaaa | N
DC | Watts | LF709IOT | 8 | H | 2022-12-08 |  | Y | 9 | (ll),oo,dddd,eeee,nnnnn,zzzzzz,aaaaaaa | N
DC | Watts | LF709IOT | 8 | VU | 2022-12-08 |  | Y | 9 | (ll),oo,dddd,eeee,nnnnn,zzzzzz,aaaaaaa | N
DC | Watts | LF709IOT | 10 | H | 2022-12-08 |  | Y | 9 | (ll),oo,dddd,eeee,nnnnn | N
DC | Watts | LF709IOT | 10 | VU | 2022-12-08 |  | Y | 9 | (ll),oo,dddd,eeee,nnnnn | N
DC | Watts | LF719AQT | 1 | VUVD | 2005-08-22 | 2023-08-22 | N | 9 | (vv),xx,ooo,pppp,rrrrr | N
DC | Watts | LF719AQT | 1 | VUVD | 2005-08-22 | 2023-08-22 | Y | 9 | hhhh,rrrrr | N
DC | Watts | LF719AQT | 1.25 | VUVD | 2005-08-22 | 2023-08-22 | N | 9 | (vv),xx,ooo,pppp,rrrrr | N
DC | Watts | LF719AQT | 1.25 | VUVD | 2005-08-22 | 2023-08-22 | Y | 9 | hhhh,rrrrr | N
DC | Watts | LF719AQT | 1.5 | VUVD | 2005-08-22 | 2023-08-22 | N | 9 | (vv),xx,ooo,pppp,rrrrr | N
DC | Watts | LF719AQT | 1.5 | VUVD | 2005-08-22 | 2023-08-22 | Y | 9 | hhhh,rrrrr | N
DC | Watts | LF719AQT | 2 | VUVD | 2005-08-22 | 2023-08-22 | N | 9 | (vv),xx,ooo,pppp,rrrrr | N
DC | Watts | LF719AQT | 2 | VUVD | 2005-08-22 | 2023-08-22 | Y | 9 | hhhh,rrrrr | N
DC | Watts | LF719QT | 0.5 | H | 2013-07-03 | 2022-07-03 | Y | 9 | (hhhh) | N
DC | Watts | LF719QT | 0.5 | VD | 2013-07-03 | 2022-07-03 | Y | 9 | (hhhh) | N
DC | Watts | LF719QT | 0.5 | VU | 2013-07-03 | 2022-07-03 | Y | 9 | (hhhh) | N
DC | Watts | LF719QT | 0.75 | H | 2013-07-03 | 2022-07-03 | Y | 9 | (hhhh) | N
DC | Watts | LF719QT | 0.75 | VD | 2013-07-03 | 2022-07-03 | Y | 9 | (hhhh) | N
DC | Watts | LF719QT | 0.75 | VU | 2013-07-03 | 2022-07-03 | Y | 9 | (hhhh) | N
DC | Watts | LF719QT | 1 | H | 2005-08-22 | 2023-08-22 | N | 9 | (vv),xx,ooo,pppp,rrrrr | N
DC | Watts | LF719QT | 1 | H | 2005-08-22 | 2023-08-22 | Y | 9 | hhhh,rrrrr | N
DC | Watts | LF719QT | 1 | VD | 2005-08-22 | 2023-08-22 | N | 9 | (vv),xx,ooo,pppp,rrrrr | N
DC | Watts | LF719QT | 1 | VD | 2005-08-22 | 2023-08-22 | Y | 9 | hhhh,rrrrr | N
DC | Watts | LF719QT | 1 | VU | 2005-08-22 | 2023-08-22 | N | 9 | (vv),xx,ooo,pppp,rrrrr | N
DC | Watts | LF719QT | 1 | VU | 2005-08-22 | 2023-08-22 | Y | 9 | hhhh,rrrrr | N
DC | Watts | LF719QT | 1.25 | H | 2005-08-22 | 2023-08-22 | N | 9 | (vv),xx,ooo,pppp,rrrrr | N
DC | Watts | LF719QT | 1.25 | H | 2005-08-22 | 2023-08-22 | Y | 9 | hhhh,rrrrr | N
DC | Watts | LF719QT | 1.25 | VD | 2005-08-22 | 2023-08-22 | N | 9 | (vv),xx,ooo,pppp,rrrrr | N
DC | Watts | LF719QT | 1.25 | VD | 2005-08-22 | 2023-08-22 | Y | 9 | hhhh,rrrrr | N
DC | Watts | LF719QT | 1.25 | VU | 2005-08-22 | 2023-08-22 | N | 9 | (vv),xx,ooo,pppp,rrrrr | N
DC | Watts | LF719QT | 1.25 | VU | 2005-08-22 | 2023-08-22 | Y | 9 | hhhh,rrrrr | N
DC | Watts | LF719QT | 1.5 | H | 2005-08-22 | 2023-08-22 | N | 9 | (vv),xx,ooo,pppp,rrrrr | N
DC | Watts | LF719QT | 1.5 | H | 2005-08-22 | 2023-08-22 | Y | 9 | hhhh,rrrrr | N
DC | Watts | LF719QT | 1.5 | VD | 2005-08-22 | 2023-08-22 | N | 9 | (vv),xx,ooo,pppp,rrrrr | N
DC | Watts | LF719QT | 1.5 | VD | 2005-08-22 | 2023-08-22 | Y | 9 | hhhh,rrrrr | N
DC | Watts | LF719QT | 1.5 | VU | 2005-08-22 | 2023-08-22 | N | 9 | (vv),xx,ooo,pppp,rrrrr | N
DC | Watts | LF719QT | 1.5 | VU | 2005-08-22 | 2023-08-22 | Y | 9 | hhhh,rrrrr | N
DC | Watts | LF719QT | 2 | H | 2005-08-22 | 2023-08-22 | N | 9 | (vv),xx,ooo,pppp,rrrrr | N
DC | Watts | LF719QT | 2 | H | 2005-08-22 | 2023-08-22 | Y | 9 | hhhh,rrrrr | N
DC | Watts | LF719QT | 2 | VD | 2005-08-22 | 2023-08-22 | N | 9 | (vv),xx,ooo,pppp,rrrrr | N
DC | Watts | LF719QT | 2 | VD | 2005-08-22 | 2023-08-22 | Y | 9 | hhhh,rrrrr | N
DC | Watts | LF719QT | 2 | VU | 2005-08-22 | 2023-08-22 | N | 9 | (vv),xx,ooo,pppp,rrrrr | N
DC | Watts | LF719QT | 2 | VU | 2005-08-22 | 2023-08-22 | Y | 9 | hhhh,rrrrr | N
DC | Watts | LF719QTR10 | 0.5 | H | 2005-08-22 | 2023-08-22 | N | 9 | (vv),xx,ooo,hhhh,pppp,rrrrr | Y
DC | Watts | LF719QTR10 | 0.5 | VD | 2005-08-22 | 2023-08-22 | N | 9 | (vv),xx,ooo,hhhh,pppp,rrrrr | Y
DC | Watts | LF719QTR10 | 0.5 | VU | 2005-08-22 | 2023-08-22 | N | 9 | (vv),xx,ooo,hhhh,pppp,rrrrr | Y
DC | Watts | LF719QTR10 | 0.75 | H | 2005-08-22 | 2023-08-22 | N | 9 | (vv),xx,ooo,hhhh,pppp,rrrrr | Y
DC | Watts | LF719QTR10 | 0.75 | VD | 2005-08-22 | 2023-08-22 | N | 9 | (vv),xx,ooo,hhhh,pppp,rrrrr | Y
DC | Watts | LF719QTR10 | 0.75 | VU | 2005-08-22 | 2023-08-22 | N | 9 | (vv),xx,ooo,hhhh,pppp,rrrrr | Y
DC | Watts | LFU719QT | 1 | H | 2005-08-22 | 2023-08-22 | N | 9 | (vv),xx,ooo,pppp | N
DC | Watts | LFU719QT | 1 | H | 2005-08-22 | 2023-08-22 | Y | 9 | hhhh | N
DC | Watts | LFU719QT | 1 | VD | 2005-08-22 | 2023-08-22 | N | 9 | (vv),xx,ooo,pppp | N
DC | Watts | LFU719QT | 1 | VD | 2005-08-22 | 2023-08-22 | Y | 9 | hhhh | N
DC | Watts | LFU719QT | 1 | VU | 2005-08-22 | 2023-08-22 | N | 9 | (vv),xx,ooo,pppp | N
DC | Watts | LFU719QT | 1 | VU | 2005-08-22 | 2023-08-22 | Y | 9 | hhhh | N
DC | Watts | LFU719QT | 1.25 | H | 2005-08-22 | 2023-08-22 | N | 9 | (vv),xx,ooo,pppp | N
DC | Watts | LFU719QT | 1.25 | H | 2005-08-22 | 2023-08-22 | Y | 9 | hhhh | N
DC | Watts | LFU719QT | 1.25 | VD | 2005-08-22 | 2023-08-22 | N | 9 | (vv),xx,ooo,pppp | N
DC | Watts | LFU719QT | 1.25 | VD | 2005-08-22 | 2023-08-22 | Y | 9 | hhhh | N
DC | Watts | LFU719QT | 1.25 | VU | 2005-08-22 | 2023-08-22 | N | 9 | (vv),xx,ooo,pppp | N
DC | Watts | LFU719QT | 1.25 | VU | 2005-08-22 | 2023-08-22 | Y | 9 | hhhh | N
DC | Watts | LFU719QT | 1.5 | H | 2005-08-22 | 2023-08-22 | N | 9 | (vv),xx,ooo,pppp | N
DC | Watts | LFU719QT | 1.5 | H | 2005-08-22 | 2023-08-22 | Y | 9 | hhhh | N
DC | Watts | LFU719QT | 1.5 | VD | 2005-08-22 | 2023-08-22 | N | 9 | (vv),xx,ooo,pppp | N
DC | Watts | LFU719QT | 1.5 | VD | 2005-08-22 | 2023-08-22 | Y | 9 | hhhh | N
DC | Watts | LFU719QT | 1.5 | VU | 2005-08-22 | 2023-08-22 | N | 9 | (vv),xx,ooo,pppp | N
DC | Watts | LFU719QT | 1.5 | VU | 2005-08-22 | 2023-08-22 | Y | 9 | hhhh | N
DC | Watts | LFU719QT | 2 | H | 2005-08-22 | 2023-08-22 | N | 9 | (vv),xx,ooo,pppp | N
DC | Watts | LFU719QT | 2 | H | 2005-08-22 | 2023-08-22 | Y | 9 | hhhh | N
DC | Watts | LFU719QT | 2 | VD | 2005-08-22 | 2023-08-22 | N | 9 | (vv),xx,ooo,pppp | N
DC | Watts | LFU719QT | 2 | VD | 2005-08-22 | 2023-08-22 | Y | 9 | hhhh | N
DC | Watts | LFU719QT | 2 | VU | 2005-08-22 | 2023-08-22 | N | 9 | (vv),xx,ooo,pppp | N
DC | Watts | LFU719QT | 2 | VU | 2005-08-22 | 2023-08-22 | Y | 9 | hhhh | N
DC | Watts | Magnum 20 | 2.5 | H | 2020-05-15 | 2023-05-15 | Y | 10 | (int) | N
DC | Watts | Magnum 20 | 2.5 | VU | 2020-05-15 | 2023-05-15 | Y | 10 | (int) | N
DC | Watts | Magnum 20 | 3 | H | 2020-05-15 | 2023-05-15 | Y | 10 | (int) | N
DC | Watts | Magnum 20 | 3 | VU | 2020-05-15 | 2023-05-15 | Y | 10 | (int) | N
DC | Watts | Magnum 20 | 4 | H | 2020-05-15 | 2023-05-15 | Y | 10 | (int) | N
DC | Watts | Magnum 20 | 4 | VU | 2020-05-15 | 2023-05-15 | Y | 10 | (int) | N
DC | Watts | Magnum 20 | 6 | H | 2020-08-03 | 2023-08-03 | Y | 10 | (int) | N
DC | Watts | Magnum 20 | 6 | VU | 2020-08-03 | 2023-08-03 | Y | 10 | (int) | N
DC | Watts | Magnum 20 | 8 | H | 2020-05-15 | 2023-05-15 | Y | 10 | (int) | N
DC | Watts | Magnum 20 | 8 | VU | 2020-05-15 | 2023-05-15 | Y | 10 | (int) | N
DC | Watts | Magnum 20G | 2.5 | H | 2020-05-15 | 2023-05-15 | Y | 10 | (qqqqqq), rrrrrr | N
DC | Watts | Magnum 20G | 2.5 | VU | 2020-05-15 | 2023-05-15 | Y | 10 | (qqqqqq), rrrrrr | N
DC | Watts | Magnum 20G | 3 | H | 2020-05-15 | 2023-05-15 | Y | 10 | (qqqqqq), rrrrrr | N
DC | Watts | Magnum 20G | 3 | VU | 2020-05-15 | 2023-05-15 | Y | 10 | (qqqqqq), rrrrrr | N
DC | Watts | Magnum 20G | 4 | H | 2020-05-15 | 2023-05-15 | Y | 10 | (qqqqqq), rrrrrr | N
DC | Watts | Magnum 20G | 4 | VU | 2020-05-15 | 2023-05-15 | Y | 10 | (qqqqqq), rrrrrr | N
DC | Watts | Magnum 20G | 6 | H | 2020-05-15 | 2023-05-15 | Y | 10 | (qqqqqq), rrrrrr | N
DC | Watts | Magnum 20G | 6 | VU | 2020-05-15 | 2023-05-15 | Y | 10 | (qqqqqq), rrrrrr | N
DC | Watts | Magnum 20G | 8 | H | 2020-05-15 | 2023-05-15 | Y | 10 | (qqqqqq), rrrrrr | N
DC | Watts | Magnum 20G | 8 | VU | 2020-05-15 | 2023-05-15 | Y | 10 | (qqqqqq), rrrrrr | N
DC | Watts | SS007M1QT | 1 | H | 1998-05-18 | 2022-05-18 | Y | 9 | (hhh) | N
DC | Watts | SS007M1QT | 1 | VU | 1998-05-18 | 2022-05-18 | Y | 9 | (hhh) | N
DC | Watts | SS007M3QT | 0.5 | H | 2000-09-11 | 2024-09-11 | Y | 9 | (hhh) | N
DC | Watts | SS007M3QT | 0.5 | VU | 2000-09-11 | 2024-09-11 | Y | 9 | (hhh) | N
DC | Watts | SS007M3QT | 0.75 | H | 2000-09-07 | 2024-09-07 | Y | 9 | (hhh) | N
DC | Watts | SS007M3QT | 0.75 | VU | 2000-09-07 | 2024-09-07 | Y | 9 | (hhh) | N
DC | Watts | U007M1APCQT | 0.75 | VDVD | 1994-12-10 | 2024-12-10 | N | 8 | (vv),xx,ooo,hhhh,pppp | N
DC | Watts | U007M1APCQT | 0.75 | VDVU | 1994-12-10 | 2024-12-10 | N | 8 | (vv),xx,ooo,hhhh,pppp | N
DC | Watts | U007M1APCQT | 0.75 | VUVD | 1994-12-10 | 2024-12-10 | N | 8 | (vv),xx,ooo,hhhh,pppp | N
DC | Watts | U007M1APCQT | 0.75 | VUVU | 1994-12-10 | 2024-12-10 | N | 8 | (vv),xx,ooo,hhhh,pppp | N
DC | Watts | U007M1APCQT | 2 | VDVD | 1994-09-27 | 2024-09-27 | N | 8 | (vv),xx,ooo,hhhh,pppp | N
DC | Watts | U007M1APCQT | 2 | VDVU | 1994-09-27 | 2024-09-27 | N | 8 | (vv),xx,ooo,hhhh,pppp | N
DC | Watts | U007M1APCQT | 2 | VUVD | 1994-09-27 | 2024-09-27 | N | 8 | (vv),xx,ooo,hhhh,pppp | N
DC | Watts | U007M1APCQT | 2 | VUVU | 1994-09-27 | 2024-09-27 | N | 8 | (vv),xx,ooo,hhhh,pppp | N
DC | Watts | U007M1AQT | 0.75 | VDVD | 1994-02-24 | 2024-02-24 | N | 8 | (vv),xx,ooo,hhhh,pppp | N
DC | Watts | U007M1AQT | 0.75 | VDVU | 1994-02-24 | 2024-02-24 | N | 8 | (vv),xx,ooo,hhhh,pppp | N
DC | Watts | U007M1AQT | 0.75 | VUVD | 1994-02-24 | 2024-02-24 | N | 8 | (vv),xx,ooo,hhhh,pppp | N
DC | Watts | U007M1AQT | 0.75 | VUVU | 1994-02-24 | 2024-02-24 | N | 8 | (vv),xx,ooo,hhhh,pppp | N
DC | Watts | U007M1AQT | 2 | VDVD | 1994-02-24 | 2024-02-24 | N | 8 | (vv),xx,ooo,hhhh,pppp | N
DC | Watts | U007M1AQT | 2 | VDVU | 1994-02-24 | 2024-02-24 | N | 8 | (vv),xx,ooo,hhhh,pppp | N
DC | Watts | U007M1AQT | 2 | VUVD | 1994-02-24 | 2024-02-24 | N | 8 | (vv),xx,ooo,hhhh,pppp | N
DC | Watts | U007M1AQT | 2 | VUVU | 1994-02-24 | 2024-02-24 | N | 8 | (vv),xx,ooo,hhhh,pppp | N
DC | Watts | U007M1PCQT | 0.75 | H | 1993-12-10 | 2023-12-10 | N | 8 | (vv),xx,ooo,hhhh,pppp | N
DC | Watts | U007M1PCQT | 1 | H | 1993-12-10 | 2023-12-10 | N | 8 | (vv),xx,ooo,hhhh,pppp | N
DC | Watts | U007M1PCQT | 1.5 | H | 1994-09-27 | 2024-09-27 | N | 8 | (vv),xx,ooo,hhhh,pppp | N
DC | Watts | U007M1PCQT | 2 | H | 1994-09-27 | 2024-09-27 | N | 8 | (vv),xx,ooo,hhhh,pppp | N
DC | Watts | U007M1QT | 0.75 | H | 1993-08-30 | 2023-08-28 | N | 8 | (vv),xx,ooo,hhhh,pppp | N
DC | Watts | U007M1QT | 1 | H | 1993-08-30 | 2023-08-30 | N | 8 | (vv),xx,ooo,hhhh,pppp | N
DC | Watts | U007M1QT | 1.5 | H | 1993-10-20 | 2023-10-20 | N | 8 | vv,xx,ooo,hhhh,pppp | Y
DC | Watts | U007M1QT | 2 | H | 1993-10-20 | 2023-10-20 | N | 8 | (vv),xx,ooo,hhhh,pppp | N
DC | Watts | U007M2AQT | 1.5 | VDVD | 1994-09-06 | 2024-09-06 | N | 8 | (vv),xx,ooo,hhhh,pppp | N
DC | Watts | U007M2AQT | 1.5 | VDVU | 1994-09-06 | 2024-09-06 | N | 8 | (vv),xx,ooo,hhhh,pppp | N
DC | Watts | U007M2AQT | 1.5 | VUVD | 1994-09-06 | 2024-09-06 | N | 8 | (vv),xx,ooo,hhhh,pppp | N
DC | Watts | U007M2AQT | 1.5 | VUVU | 1994-09-06 | 2024-09-06 | N | 8 | (vv),xx,ooo,hhhh,pppp | N
DC | Watts | U007M2QT | 1.25 | H | 1996-10-01 | 2023-10-01 | N | 8 | (vv),xx,ooo,hhhh,pppp | N
DC | Watts | U007M2QT | 1.5 | H | 1994-09-06 | 2024-09-06 | N | 8 | (vv),xx,ooo,hhhh,pppp | N
DC | Watts | U007PCQT | 0.75 | H | 1993-12-10 | 2023-12-10 | N | 8 | vv,xx,ooo,hhhh,pppp | Y
DC | Watts | U007PCQT | 1 | H | 1993-12-10 | 2023-12-10 | N | 8 | vv,xx,ooo,hhhh,pppp | Y
DC | Watts | U007PCQT | 1.5 | H | 1994-09-27 | 2024-09-27 | N | 8 | vv,xx,ooo,hhhh,pppp | Y
DC | Watts | U007PCQT | 2 | H | 1994-09-27 | 2024-09-27 | N | 8 | vv,xx,ooo,hhhh,pppp | Y
DC | Watts | U007QT | 0.5 | H | 1999-03-08 | 2023-03-08 | N | 9 | (vv),xx,ooo,hhhh,pppp | N
DC | Watts | U007QT | 0.5 | VU | 1999-03-08 | 2023-03-08 | N | 9 | (vv),xx,ooo,hhhh,pppp | N
DC | Watts | U007QT | 0.75 | H | 1988-01-11 | 2024-01-11 | N | 7 | vv,xx,ooo,hhhh,pppp | Y
DC | Watts | U007QT | 1 | H | 1988-01-11 | 2024-01-11 | N | 7 | vv,xx,ooo,hhhh,pppp | Y
DC | Watts | U007QT | 1.5 | H | 1988-07-21 | 2024-07-21 | N | 7 | vv,xx,ooo,hhhh,pppp | Y
DC | Watts | U007QT | 2 | H | 1988-07-21 | 2024-07-21 | N | 7 | vv,xx,ooo,hhhh,pppp | Y
DC | Watts | U007SSPCQT | 0.75 | H | 1993-12-10 | 2023-12-10 | N | 8 | vv,xx,pppp | Y
DC | Watts | U007SSPCQT | 1 | H | 1993-12-10 | 2023-12-10 | N | 8 | vv,xx,pppp | Y
DC | Watts | U007SSPCQT | 1.5 | H | 1994-09-27 | 2024-09-27 | N | 8 | vv,xx,pppp | Y
DC | Watts | U007SSPCQT | 2 | H | 1994-09-27 | 2024-09-27 | N | 8 | vv,xx,pppp | Y
DC | Watts | U007SSQT | 0.75 | H | 1988-01-11 | 2024-01-11 | N | 7 | vv,xx,pppp | Y
DC | Watts | U007SSQT | 1 | H | 1988-01-11 | 2024-01-11 | N | 7 | vv,xx,pppp | Y
DC | Watts | U007SSQT | 1.5 | H | 1988-07-21 | 2024-07-21 | N | 7 | vv,xx,pppp | Y
DC | Watts | U007SSQT | 2 | H | 1988-07-21 | 2024-07-21 | N | 7 | vv,xx,pppp | Y
DC | Watts | U719QT | 0.5 | [9 empty] | model designation changed to U719QTR10
DC | Watts | U719QT | 0.5 | [9 empty] | model designation changed to U719QTR10
DC | Watts | U719QT | 0.5 | [9 empty] | model designation changed to U719QTR10
DC | Watts | U719QT | 0.75 | [9 empty] | model designation changed to U719QTR10
DC | Watts | U719QT | 0.75 | [9 empty] | model designation changed to U719QTR10
DC | Watts | U719QT | 0.75 | [9 empty] | model designation changed to U719QTR10
DC | Watts | U719QT | 1 | H | 2005-10-04 | 2023-10-04 | N | 9 | (vv),xx,ooo,hhhh,pppp | N
DC | Watts | U719QT | 1 | VD | 2005-10-04 | 2023-10-04 | N | 9 | (vv),xx,ooo,hhhh,pppp | N
DC | Watts | U719QT | 1 | VU | 2005-10-04 | 2023-10-04 | N | 9 | (vv),xx,ooo,hhhh,pppp | N
DC | Watts | U719QT | 1.25 | H | 2005-10-04 | 2023-10-04 | N | 9 | (vv),xx,ooo,hhhh,pppp | N
DC | Watts | U719QT | 1.25 | VD | 2005-10-04 | 2023-10-04 | N | 9 | (vv),xx,ooo,hhhh,pppp | N
DC | Watts | U719QT | 1.25 | VU | 2005-10-04 | 2023-10-04 | N | 9 | (vv),xx,ooo,hhhh,pppp | N
DC | Watts | U719QT | 1.5 | H | 2005-10-04 | 2023-10-04 | N | 9 | (vv),xx,ooo,hhhh,pppp | N
DC | Watts | U719QT | 1.5 | VD | 2005-10-04 | 2023-10-04 | N | 9 | (vv),xx,ooo,hhhh,pppp | N
DC | Watts | U719QT | 1.5 | VU | 2005-10-04 | 2023-10-04 | N | 9 | (vv),xx,ooo,hhhh,pppp | N
DC | Watts | U719QT | 2 | H | 2005-10-04 | 2023-10-04 | N | 9 | (vv),xx,ooo,hhhh,pppp | N
DC | Watts | U719QT | 2 | VD | 2005-10-04 | 2023-10-04 | N | 9 | (vv),xx,ooo,hhhh,pppp | N
DC | Watts | U719QT | 2 | VU | 2005-10-04 | 2023-10-04 | N | 9 | (vv),xx,ooo,hhhh,pppp | N
DC | Watts | U719QTR10 | 0.5 | H | 2005-10-04 | 2023-10-04 | N | 9 | (vv),xx,ooo,hhhh,pppp | Y |  |  | formerly U719QT
DC | Watts | U719QTR10 | 0.5 | VD | 2005-10-04 | 2023-10-04 | N | 9 | (vv),xx,ooo,hhhh,pppp | Y |  |  | formerly U719QT
DC | Watts | U719QTR10 | 0.5 | VU | 2005-10-04 | 2023-10-04 | N | 9 | (vv),xx,ooo,hhhh,pppp | Y |  |  | formerly U719QT
DC | Watts | U719QTR10 | 0.75 | H | 2005-10-04 | 2023-10-04 | N | 9 | (vv),xx,ooo,hhhh,pppp | Y |  |  | formerly U719QT
DC | Watts | U719QTR10 | 0.75 | VD | 2005-10-04 | 2023-10-04 | N | 9 | (vv),xx,ooo,hhhh,pppp | Y |  |  | formerly U719QT
DC | Watts | U719QTR10 | 0.75 | VU | 2005-10-04 | 2023-10-04 | N | 9 | (vv),xx,ooo,hhhh,pppp | Y |  |  | formerly U719QT
DC | Wilkins | 350 | 0.75 | H | 2005-07-06 | 2023-07-06 | N | 9 | (ii),ooo | N |  |  | Testcocks: Female Threaded End or 45 degree male SAE flare
DC | Wilkins | 350 | 0.75 | VU | 2005-07-06 | 2023-07-06 | N | 9 | (ii),ooo | N |  |  | Testcocks: Female Threaded End or 45 degree male SAE flare
DC | Wilkins | 350 | 1 | H | 2006-04-21 | 2024-04-21 | N | 9 | (ii),ooo | N |  |  | Testcocks: Female Threaded End or 45 degree male SAE flare
DC | Wilkins | 350 | 1 | VU | 2006-04-21 | 2024-04-21 | N | 9 | (ii),ooo | N |  |  | Testcocks: Female Threaded End or 45 degree male SAE flare
DC | Wilkins | 350 | 1.25 | H | 2009-01-08 | 2024-01-08 | N | 9 | (int) | N
DC | Wilkins | 350 | 1.25 | VU | 2009-01-08 | 2024-01-08 | N | 9 | (int) | N
DC | Wilkins | 350 | 1.5 | H | 2009-01-08 | 2024-01-08 | N | 9 | (int) | N
DC | Wilkins | 350 | 1.5 | VU | 2009-01-08 | 2024-01-08 | N | 9 | (int) | N
DC | Wilkins | 350 | 2 | H | 2009-01-08 | 2024-01-08 | N | 9 | (int) | N
DC | Wilkins | 350 | 2 | VU | 2009-01-08 | 2024-01-08 | N | 9 | (int) | N
DC | Wilkins | 350 | 2.5 | H | 2001-09-05 | 2022-09-05 | N | 9 | (gg),ee,ff,hh,ll,mm,tt,uu,yy,zz,ppp,qqq,zzz,dddd,ssss,tttt,vvvv,wwww,yyyy,zzzz,kkkkk,gggggg,hhhhhh,jjjjjj,kkkkkk,mmmmmm,nnnnnn | N |  |  | Up to serial number J35214
DC | Wilkins | 350 | 2.5 | H | 2010-09-09 | 2022-09-09 | Y | 9 | (gg),hh,ppp,qqq,ssss,tttt,vvvv,wwww,yyyy,zzzz,kkkkk,gggggg,hhhhhh,jjjjjj,kkkkkk,mmmmmm,nnnnnn | N |  |  | Serial number J35214 and higher
DC | Wilkins | 350 | 2.5 | VU | 2002-04-03 | 2023-04-03 | N | 9 | (gg),hh,ppp,qqq,ssss,tttt,vvvv,wwww,yyyy,zzzz,kkkkk,gggggg,hhhhhh,jjjjjj,kkkkkk,mmmmmm,nnnnnn | N |  |  | Up to serial number J35214
DC | Wilkins | 350 | 2.5 | VU | 2010-09-09 | 2022-09-09 | Y | 9 | (gg),ee,ff,hh,ll,mm,tt,uu,yy,zz,ppp,qqq,zzz,dddd,ssss,tttt,vvvv,wwww,yyyy,zzzz,kkkkk,gggggg,hhhhhh,jjjjjj,kkkkkk,mmmmmm,nnnnnn | N |  |  | Serial number J35214 and higher
DC | Wilkins | 350 | 3 | H | 2001-09-05 | 2022-09-05 | N | 9 | (gg),ee,ff,hh,ll,mm,tt,uu,yy,zz,ppp,qqq,zzz,dddd,ssss,tttt,vvvv,wwww,yyyy,zzzz,kkkkk,gggggg,hhhhhh,jjjjjj,kkkkkk,mmmmmm,nnnnnn | N |  |  | Up to serial number J35214
DC | Wilkins | 350 | 3 | H | 2010-09-09 | 2022-09-09 | Y | 9 | (gg),hh,ppp,qqq,ssss,tttt,vvvv,wwww,yyyy,zzzz,kkkkk,gggggg,hhhhhh,jjjjjj,kkkkkk,mmmmmm,nnnnnn | N |  |  | Serial number J35214 and higher
DC | Wilkins | 350 | 3 | VU | 2002-04-03 | 2023-04-03 | N | 9 | (gg),ee,ff,hh,ll,mm,tt,uu,yy,zz,ppp,qqq,zzz,dddd,ssss,tttt,vvvv,wwww,yyyy,zzzz,kkkkk,gggggg,hhhhhh,jjjjjj,kkkkkk,mmmmmm,nnnnnn | N |  |  | Up to serial number J35214
DC | Wilkins | 350 | 3 | VU | 2010-09-09 | 2022-09-09 | Y | 9 | (gg),hh,ppp,qqq,ssss,tttt,vvvv,wwww,yyyy,zzzz,kkkkk,gggggg,hhhhhh,jjjjjj,kkkkkk,mmmmmm,nnnnnn | N |  |  | Serial number J35214 and higher
DC | Wilkins | 350 | 4 | H | 1999-09-15 | 2023-09-15 | N | 9 | (gg),ee,ff,hh,ll,mm,tt,uu,yy,zz,ppp,qqq,vvv,www,zzz,dddd,eeee,ssss,tttt,vvvv,wwww,yyyy,zzzz,kkkkk,gggggg,hhhhhh,jjjjjj,kkkkkk,mmmmmm,nnnnnn | N |  |  | Up to serial number J35214
DC | Wilkins | 350 | 4 | H | 2010-09-09 | 2022-09-09 | Y | 9 | (gg),hh,ppp,qqq,vvv,www,ssss,tttt,vvvv,wwww,yyyy,zzzz,kkkkk,gggggg,hhhhhh,jjjjjj,kkkkkk,mmmmmm,nnnnnn | N |  |  | Serial number J35214 and higher
DC | Wilkins | 350 | 4 | VU | 2000-09-07 | 2024-09-07 | N | 9 | (gg),ee,ff,hh,ll,mm,tt,uu,yy,zz,ppp,qqq,vvv,www,zzz,dddd,eeee,ssss,tttt,vvvv,wwww,yyyy,zzzz,kkkkk,gggggg,hhhhhh,jjjjjj,kkkkkk,mmmmmm,nnnnnn | N |  |  | Up to serial number J35214
DC | Wilkins | 350 | 4 | VU | 2010-09-09 | 2022-09-09 | Y | 9 | (gg),hh,ppp,qqq,vvv,www,ssss,tttt,vvvv,wwww,yyyy,zzzz,kkkkk,gggggg,hhhhhh,jjjjjj,kkkkkk,mmmmmm,nnnnnn | N |  |  | Serial number J35214 and higher
DC | Wilkins | 350 | 6 | H | 1999-10-18 | 2023-10-18 | N | 9 | (gg),ee,ff,hh,ll,mm,tt,uu,yy,zz,ppp,qqq,vvv,www,zzz,dddd,eeee,ssss,tttt,vvvv,wwww,yyyy,zzzz,kkkkk,gggggg,hhhhhh,jjjjjj,kkkkkk,mmmmmm,nnnnnn | N |  |  | Up to serial number J35214
DC | Wilkins | 350 | 6 | H | 2010-09-09 | 2022-09-09 | Y | 9 | (gg),hh,ppp,qqq,vvv,www,ssss,tttt,vvvv,wwww,yyyy,zzzz,kkkkk,gggggg,hhhhhh,jjjjjj,kkkkkk,mmmmmm,nnnnnn | N |  |  | Serial number J35214 and higher
DC | Wilkins | 350 | 6 | VU | 1999-12-17 | 2023-12-17 | N | 9 | (gg),ee,ff,hh,ll,mm,tt,uu,yy,zz,ppp,qqq,vvv,www,zzz,dddd,eeee,ssss,tttt,vvvv,wwww,yyyy,zzzz,kkkkk,gggggg,hhhhhh,jjjjjj,kkkkkk,mmmmmm,nnnnnn | N |  |  | Up to serial number J35214
DC | Wilkins | 350 | 6 | VU | 2010-09-09 | 2022-09-09 | Y | 9 | (gg),hh,ppp,qqq,vvv,www,ssss,tttt,vvvv,wwww,yyyy,zzzz,kkkkk,gggggg,hhhhhh,jjjjjj,kkkkkk,mmmmmm,nnnnnn | N |  |  | Serial number J35214 and higher
DC | Wilkins | 350 | 8 | H | 2002-03-08 | 2023-03-08 | N | 9 | (gg),ee,ff,hh,ll,mm,tt,uu,yy,zz,ppp,qqq,vvv,www,zzz,dddd,eeee,ssss,tttt,vvvv,wwww,yyyy,zzzz,kkkkk,gggggg,hhhhhh,jjjjjj,kkkkkk,mmmmmm,nnnnnn | N |  |  | Up to serial number J35214
DC | Wilkins | 350 | 8 | H | 2010-09-09 | 2022-09-09 | Y | 9 | (gg),hh,ppp,qqq,vvv,www,ssss,tttt,vvvv,wwww,yyyy,zzzz,kkkkk,gggggg,hhhhhh,jjjjjj,kkkkkk,mmmmmm,nnnnnn | N |  |  | Serial number J35214 and higher
DC | Wilkins | 350 | 8 | VU | 2003-01-16 | 2024-01-16 | N | 9 | (gg),ee,ff,hh,ll,mm,tt,uu,yy,zz,ppp,qqq,vvv,www,zzz,dddd,eeee,ssss,tttt,vvvv,wwww,yyyy,zzzz,kkkkk,gggggg,hhhhhh,jjjjjj,kkkkkk,mmmmmm,nnnnnn | N |  |  | Up to serial number J35214
DC | Wilkins | 350 | 8 | VU | 2010-09-09 | 2022-09-09 | Y | 9 | (gg),hh,ppp,qqq,vvv,www,ssss,tttt,vvvv,wwww,yyyy,zzzz,kkkkk,gggggg,hhhhhh,jjjjjj,kkkkkk,mmmmmm,nnnnnn | N |  |  | Serial number J35214 and higher
DC | Wilkins | 350 | 10 | H | 2002-08-28 | 2023-08-28 | N | 9 | (gg),ee,ff,hh,ll,mm,tt,uu,yy,zz,ppp,qqq,vvv,www,zzz,dddd,eeee,ssss,tttt,vvvv,wwww,yyyy,zzzz,kkkkk,gggggg,hhhhhh,jjjjjj,kkkkkk,mmmmmm,nnnnnn | N |  |  | Up to serial number J35214
DC | Wilkins | 350 | 10 | H | 2010-09-09 | 2022-09-09 | Y | 9 | (gg),hh,ppp,qqq,vvv,www,ssss,tttt,vvvv,wwww,yyyy,zzzz,kkkkk,gggggg,hhhhhh,jjjjjj,kkkkkk,mmmmmm,nnnnnn | N |  |  | Serial number J35214 and higher
DC | Wilkins | 350 | 10 | VU | 2003-03-14 | 2024-03-14 | N | 9 | (gg),ee,ff,hh,ll,mm,tt,uu,yy,zz,ppp,qqq,vvv,www,zzz,dddd,eeee,ssss,tttt,vvvv,wwww,yyyy,zzzz,kkkkk,gggggg,hhhhhh,jjjjjj,kkkkkk,mmmmmm,nnnnnn | N |  |  | Up to serial number J35214
DC | Wilkins | 350 | 10 | VU | 2010-09-09 | 2022-09-09 | Y | 9 | (gg),hh,ppp,qqq,vvv,www,ssss,tttt,vvvv,wwww,yyyy,zzzz,kkkkk,gggggg,hhhhhh,jjjjjj,kkkkkk,mmmmmm,nnnnnn | N |  |  | Serial number J35214 and higher
DC | Wilkins | 350 | 12 | H | 2009-02-10 | 2024-02-10 | N | 9 | (hh),ssss,tttt,vvvv,wwww,yyyy,zzzz,kkkkk,gggggg,hhhhhh,jjjjjj,kkkkkk,mmmmmm,nnnnnn | N |  |  | Up to serial number J35214
DC | Wilkins | 350 | 12 | H | 2010-09-09 | 2022-09-09 | Y | 9 | (hh),ssss,tttt,vvvv,wwww,yyyy,zzzz,kkkkk,gggggg,hhhhhh,jjjjjj,kkkkkk,mmmmmm,nnnnnn | N |  |  | Serial number J35214 and higher
DC | Wilkins | 450 | 2.5 | VUVD | 2002-01-24 | 2023-01-24 | N | 9 | (gg),ee,ff,hh,ll,mm,tt,uu,yy,zz,ppp,qqq,zzz,dddd,ssss,tttt,vvvv,wwww,yyyy,zzzz,kkkkk,gggggg,hhhhhh,jjjjjj,kkkkkk,mmmmmm,nnnnnn | N |  |  | Up to serial number K01185
DC | Wilkins | 450 | 2.5 | VUVD | 2010-09-09 | 2022-09-09 | Y | 9 | (gg),hh,ppp,qqq,ssss,tttt,vvvv,wwww,yyyy,zzzz,kkkkk,gggggg,hhhhhh,jjjjjj,kkkkkk,mmmmmm,nnnnnn | N |  |  | Serial number K01185 and higher
DC | Wilkins | 450 | 3 | VUVD | 2002-01-24 | 2023-01-24 | N | 9 | (gg),ee,ff,hh,ll,mm,tt,uu,yy,zz,ppp,qqq,zzz,dddd,ssss,tttt,vvvv,wwww,yyyy,zzzz,kkkkk,gggggg,hhhhhh,jjjjjj,kkkkkk,mmmmmm,nnnnnn | N |  |  | Up to serial number K01185
DC | Wilkins | 450 | 3 | VUVD | 2010-09-09 | 2022-09-09 | Y | 9 | (gg),hh,ppp,qqq,ssss,tttt,vvvv,wwww,yyyy,zzzz,kkkkk,gggggg,hhhhhh,jjjjjj,kkkkkk,mmmmmm,nnnnnn | N |  |  | Serial number K01185 and higher
DC | Wilkins | 450 | 4 | VUVD | 2000-04-12 | 2024-04-12 | N | 9 | (ppp),qqq,sss,ttt,www,yyy,zzz,dddd,eeee,ssss,uuuu,vvvv,xxxx,yyyy,aaaaa,kkkkk,lllll,gggggg,iiiiii,jjjjjj,llllll,mmmmmm,oooooo | N |  |  | Up to serial number K01185
DC | Wilkins | 450 | 4 | VUVD | 2010-09-09 | 2022-09-09 | Y | 9 | (ppp),qqq,sss,ttt,www,yyy,ssss,uuuu,vvvv,xxxx,yyyy,aaaaa,kkkkk,lllll,gggggg,iiiiii,jjjjjj,llllll,mmmmmm,oooooo | N |  |  | Serial number K01185 and higher
DC | Wilkins | 450 | 6 | VUVD | 2000-05-24 | 2024-05-24 | N | 9 | (ppp),qqq,sss,ttt,www,yyy,zzz,dddd,eeee,ssss,uuuu,vvvv,xxxx,yyyy,aaaaa,kkkkk,lllll,gggggg,iiiiii,jjjjjj,llllll,mmmmmm,oooooo | N |  |  | Up to serial number K01185
DC | Wilkins | 450 | 6 | VUVD | 2010-09-09 | 2022-09-09 | Y | 9 | (ppp),qqq,sss,ttt,www,yyy,ssss,uuuu,vvvv,xxxx,yyyy,aaaaa,kkkkk,lllll,gggggg,iiiiii,jjjjjj,llllll,mmmmmm,oooooo | N |  |  | Serial number K01185 and higher
DC | Wilkins | 450 | 8 | VUVD | 2003-04-14 | 2024-04-14 | N | 9 | (ppp),qqq,sss,ttt,www,yyy,zzz,dddd,eeee,ssss,uuuu,vvvv,xxxx,yyyy,aaaaa,kkkkk,lllll,gggggg,iiiiii,jjjjjj,llllll,mmmmmm,oooooo | N |  |  | Up to serial number K01185
DC | Wilkins | 450 | 8 | VUVD | 2010-09-09 | 2022-09-09 | Y | 9 | (ppp),qqq,sss,ttt,www,yyy,ssss,uuuu,vvvv,xxxx,yyyy,aaaaa,kkkkk,lllll,gggggg,iiiiii,jjjjjj,llllll,mmmmmm,oooooo | N |  |  | Serial number K01185 and higher
DC | Wilkins | 450 | 10 | VUVD | 2003-09-11 | 2024-09-11 | N | 9 | (ppp),qqq,sss,ttt,www,zzz,dddd,eeee,ssss,uuuu,vvvv,xxxx,yyyy,aaaaa,kkkkk,lllll,gggggg,iiiiii,jjjjjj,llllll,mmmmmm,oooooo | N |  |  | Up to serial number K01185
DC | Wilkins | 450 | 10 | VUVD | 2010-09-09 | 2022-09-09 | Y | 9 | (ppp),qqq,sss,ttt,www,ssss,uuuu,vvvv,xxxx,yyyy,aaaaa,kkkkk,lllll,gggggg,iiiiii,jjjjjj,llllll,mmmmmm,oooooo | N |  |  | Serial number K01185 and higher
DC | Wilkins | 550 | 0.75 | H | 1976-10-11 | 2024-10-11 | N | 5 | (ppp),qqq,sss,ttt,yyy,ssss,uuuu,vvvv,xxxx,yyyy,aaaaa | Y
DC | Wilkins | 550 | 1 | H | 1976-10-11 | 2024-10-11 | N | 5 | (ppp),qqq,sss,ttt,yyy,ssss,uuuu,vvvv,xxxx,yyyy,aaaaa | Y
DC | Wilkins | 550 | 1.25 | H | 1976-10-11 | 2024-10-11 | N | 5 | (ppp),qqq,sss,ttt,yyy,ssss,uuuu,vvvv,xxxx,yyyy,aaaaa | Y
DC | Wilkins | 550 | 1.5 | H | 1976-10-11 | 2024-10-11 | N | 5 | (ppp),qqq,sss,ttt,yyy,ssss,uuuu,vvvv,xxxx,yyyy,aaaaa | Y
DC | Wilkins | 550 | 1.5 | H | 1976-10-11 | 2024-10-11 | N | 5 | (ppp),qqq,sss,ttt,yyy,ssss,uuuu,vvvv,xxxx,yyyy,aaaaa | Y
DC | Wilkins | 550 | 2 | H | 1976-10-11 | 2024-10-11 | N | 5 | (ppp),qqq,sss,ttt,yyy,ssss,uuuu,vvvv,xxxx,yyyy,aaaaa | Y
DC | Wilkins | 550 | 3 | H | 1979-08-20 | 2024-08-20 | N | 5 | (ppp),qqq,sss,ttt,yyy,ssss,uuuu,vvvv,xxxx,yyyy,aaaaa | Y
DC | Wilkins | 550 | 4 | H | 1980-06-20 | 2022-06-20 | N | 5 | (ppp),qqq,sss,ttt,www,yyy,ssss,uuuu,vvvv,xxxx,yyyy,aaaaa | Y
DC | Wilkins | 550 | 6 | H | 1981-07-06 | 2023-07-06 | N | 6 | (ppp),qqq,sss,ttt,www,yyy,ssss,uuuu,vvvv,xxxx,yyyy,aaaaa | Y
DC | Wilkins | 950 | 0.75 | H | 1991-07-18 | 2024-07-18 | N | 8 | (ppp),sss,ttt,qqq,yyy,zzz,dddd,ssss,uuuu,vvvv,xxxx,yyyy,aaaaa | Y
DC | Wilkins | 950 | 1 | H | 1991-07-18 | 2024-07-18 | N | 8 | (ppp),sss,ttt,qqq,yyy,zzz,dddd,ssss,uuuu,vvvv,xxxx,yyyy,aaaaa | Y
DC | Wilkins | 950 | 1.25 | H | 1991-04-05 | 2024-04-05 | N | 8 | (ppp),qqq,sss,ttt,www,yyy,zzz,dddd,eeee,ssss,uuuu,vvvv,xxxx,yyyy,aaaaa | Y
DC | Wilkins | 950 | 1.5 | H | 1991-04-05 | 2024-04-05 | N | 8 | (ppp),qqq,sss,ttt,www,yyy,zzz,dddd,eeee,ssss,uuuu,vvvv,xxxx,yyyy,aaaaa | Y
DC | Wilkins | 950 | 2 | H | 1991-04-05 | 2024-04-05 | N | 8 | (ppp),qqq,sss,ttt,www,yyy,zzz,dddd,eeee,ssss,uuuu,vvvv,xxxx,yyyy,aaaaa | Y
DC | Wilkins | 950 | 2.5 | H | 1991-11-26 | 2024-11-26 | N | 8 | (ppp),qqq,sss,ttt,www,yyy,zzz,dddd,eeee,ssss,uuuu,vvvv,xxxx,yyyy,aaaaa | Y
DC | Wilkins | 950 | 3 | H | 1991-11-08 | 2024-11-08 | N | 8 | (ppp),qqq,sss,ttt,www,yyy,zzz,dddd,eeee,ssss,uuuu,vvvv,xxxx,yyyy,aaaaa | Y
DC | Wilkins | 950 | 4 | H | 1991-11-08 | 2024-11-08 | N | 8 | (ppp),qqq,sss,ttt,www,yyy,zzz,dddd,eeee,ssss,uuuu,vvvv,xxxx,yyyy,aaaaa | Y
DC | Wilkins | 950 | 4 | VU | 1995-08-29 | 2022-08-29 | N | 8 | (ppp),qqq,sss,ttt,www,yyy,zzz,dddd,eeee,ssss,uuuu,vvvv,xxxx,yyyy,aaaaa | Y
DC | Wilkins | 950 | 6 | H | 1992-03-18 | 2022-03-18 | N | 8 | (ppp),qqq,sss,ttt,www,yyy,zzz,dddd,eeee,ssss,uuuu,vvvv,xxxx,yyyy,aaaaa | Y
DC | Wilkins | 950 | 6 | VU | 1995-08-29 | 2022-08-29 | N | 8 | (gg),hh,ppp,qqq,ssss,uuuu,vvvv,xxxx,yyyy,aaaaa | Y
DC | Wilkins | 950 | 8 | H | 1989-03-18 | 2022-03-18 | N | 8 | (gg),hh,ppp,qqq,ssss,uuuu,vvvv,xxxx,yyyy,aaaaa | Y
DC | Wilkins | 950 | 8 | VU | 1995-08-29 | 2022-08-29 | N | 8 | (ppp),qqq,sss,ttt,www,yyy,ssss,uuuu,vvvv,xxxx,yyyy,aaaaa | Y
DC | Wilkins | 950 | 10 | H | 1994-04-12 | 2024-04-12 | N | 8 | (ppp),qqq,sss,ttt,www,yyy,ssss,uuuu,vvvv,xxxx,yyyy,aaaaa | Y
DC | Wilkins | 350A | 2.5 | H | 2005-06-22 | 2023-06-22 | N | 9 | (ppp),sss,ttt,qqq,yyy,zzz,dddd,ssss,uuuu,vvvv,xxxx,yyyy,aaaaa,kkkkk,lllll,gggggg,iiiiii,jjjjjj,llllll,mmmmmm,oooooo | N |  |  | Up to serial number U26097
DC | Wilkins | 350A | 2.5 | H | 2010-09-09 | 2022-09-09 | Y | 9 | (ppp),qqq,sss,ttt,yyy,ssss,uuuu,vvvv,xxxx,yyyy,aaaaa,kkkkk,gggggg,iiiiii,jjjjjj,llllll,mmmmmm,oooooo | N |  |  | Serial number J35214 and higher
DC | Wilkins | 350A | 2.5 | VU | 2005-06-22 | 2023-06-22 | N | 9 | (ppp),sss,ttt,qqq,yyy,zzz,dddd,ssss,uuuu,vvvv,xxxx,yyyy,aaaaa,kkkkk,lllll,gggggg,iiiiii,jjjjjj,llllll,mmmmmm,oooooo | N |  |  | Up to serial number U26097
DC | Wilkins | 350A | 2.5 | VU | 2010-09-09 | 2022-09-09 | Y | 9 | (ppp),qqq,sss,ttt,yyy,ssss,uuuu,vvvv,xxxx,yyyy,aaaaa,kkkkk,gggggg,iiiiii,jjjjjj,llllll,mmmmmm,oooooo | N |  |  | Serial number U26097 and higher
DC | Wilkins | 350A | 3 | H | 2005-06-22 | 2023-06-22 | N | 9 | (ppp),sss,ttt,qqq,yyy,zzz,dddd,ssss,uuuu,vvvv,xxxx,yyyy,aaaaa,kkkkk,lllll,gggggg,iiiiii,jjjjjj,llllll,mmmmmm,oooooo | N |  |  | Up to serial number U26097
DC | Wilkins | 350A | 3 | H | 2010-09-09 | 2022-09-09 | Y | 9 | (ppp),qqq,sss,ttt,yyy,ssss,uuuu,vvvv,xxxx,yyyy,aaaaa,kkkkk,lllll,gggggg,iiiiii,jjjjjj,llllll,mmmmmm,oooooo | N |  |  | Serial number U26097 and higher
DC | Wilkins | 350A | 3 | VU | 2005-06-22 | 2023-06-22 | N | 9 | (ppp),sss,ttt,qqq,yyy,zzz,dddd,ssss,uuuu,vvvv,xxxx,yyyy,aaaaa,kkkkk,lllll,gggggg,iiiiii,jjjjjj,llllll,mmmmmm,oooooo | N |  |  | Up to serial number U26097
DC | Wilkins | 350A | 3 | VU | 2010-09-09 | 2022-09-09 | Y | 9 | (ppp),qqq,sss,ttt,yyy,ssss,uuuu,vvvv,xxxx,yyyy,aaaaa,kkkkk,lllll,gggggg,iiiiii,jjjjjj,llllll,mmmmmm,oooooo | N |  |  | Serial number U26097 and higher
DC | Wilkins | 350A | 4 | H | 2004-03-16 | 2022-03-16 | N | 9 | (ppp),qqq,sss,ttt,www,yyy,zzz,dddd,eeee,ssss,uuuu,vvvv,xxxx,yyyy,aaaaa,kkkkk,lllll,gggggg,iiiiii,jjjjjj,llllll,mmmmmm,oooooo | N |  |  | Up to serial number U26097
DC | Wilkins | 350A | 4 | H | 2010-09-09 | 2022-09-09 | Y | 9 | (ppp),qqq,sss,ttt,yyy,ssss,uuuu,vvvv,xxxx,yyyy,aaaaa,kkkkk,lllll,gggggg,iiiiii,jjjjjj,llllll,mmmmmm,oooooo | N |  |  | Serial number U26097 and higher
DC | Wilkins | 350A | 4 | VU | 2004-03-16 | 2022-03-16 | N | 9 | (ppp),qqq,sss,ttt,www,yyy,zzz,dddd,eeee,ssss,uuuu,vvvv,xxxx,yyyy,aaaaa,kkkkk,lllll,gggggg,iiiiii,jjjjjj,llllll,mmmmmm,oooooo | N |  |  | Up to serial number U26097
DC | Wilkins | 350A | 4 | VU | 2010-09-09 | 2022-09-09 | Y | 9 | (ppp),qqq,sss,ttt,yyy,ssss,uuuu,vvvv,xxxx,yyyy,aaaaa,kkkkk,lllll,gggggg,iiiiii,jjjjjj,llllll,mmmmmm,oooooo | N |  |  | Serial number U26097 and higher
DC | Wilkins | 350A | 6 | H | 2003-11-25 | 2024-11-25 | N | 9 | (ppp),qqq,sss,ttt,www,yyy,zzz,dddd,eeee,ssss,uuuu,vvvv,xxxx,yyyy,aaaaa,kkkkk,lllll,gggggg,iiiiii,jjjjjj,llllll,mmmmmm,oooooo | N |  |  | Up to serial number U26097
DC | Wilkins | 350A | 6 | H | 2010-09-09 | 2022-09-09 | Y | 9 | (ppp),qqq,sss,ttt,yyy,ssss,uuuu,vvvv,xxxx,yyyy,aaaaa,kkkkk,lllll,gggggg,iiiiii,jjjjjj,llllll,mmmmmm,oooooo | N |  |  | Serial number U26097 and higher
DC | Wilkins | 350A | 6 | VU | 2003-11-25 | 2024-11-25 | N | 9 | (ppp),qqq,sss,ttt,www,yyy,zzz,dddd,eeee,ssss,uuuu,vvvv,xxxx,yyyy,aaaaa,kkkkk,lllll,gggggg,iiiiii,jjjjjj,llllll,mmmmmm,oooooo | N |  |  | Up to serial number U26097
DC | Wilkins | 350A | 6 | VU | 2010-09-09 | 2022-09-09 | Y | 9 | (ppp),qqq,sss,ttt,yyy,ssss,uuuu,vvvv,xxxx,yyyy,aaaaa,kkkkk,lllll,gggggg,iiiiii,jjjjjj,llllll,mmmmmm,oooooo | N |  |  | Serial number U26097 and higher
DC | Wilkins | 350A | 8 | H | 2004-02-12 | 2022-02-12 | N | 9 | (ppp),qqq,sss,ttt,www,yyy,zzz,dddd,eeee,ssss,uuuu,vvvv,xxxx,yyyy,aaaaa,kkkkk,lllll,gggggg,iiiiii,jjjjjj,llllll,mmmmmm,oooooo | N |  |  | Up to serial number U26097
DC | Wilkins | 350A | 8 | H | 2010-09-09 | 2022-09-09 | Y | 9 | (ppp),qqq,sss,ttt,yyy,ssss,uuuu,vvvv,xxxx,yyyy,aaaaa,kkkkk,lllll,gggggg,iiiiii,jjjjjj,llllll,mmmmmm,oooooo | N |  |  | Serial number U26097 and higher
DC | Wilkins | 350A | 8 | VU | 2004-02-12 | 2022-02-12 | N | 9 | (ppp),qqq,sss,ttt,www,yyy,zzz,dddd,eeee,ssss,uuuu,vvvv,xxxx,yyyy,aaaaa,kkkkk,lllll,gggggg,iiiiii,jjjjjj,llllll,mmmmmm,oooooo | N |  |  | Up to serial number U26097
DC | Wilkins | 350A | 8 | VU | 2010-09-09 | 2022-09-09 | Y | 9 | (ppp),qqq,sss,ttt,yyy,ssss,uuuu,vvvv,xxxx,yyyy,aaaaa,kkkkk,lllll,gggggg,iiiiii,jjjjjj,llllll,mmmmmm,oooooo | N |  |  | Serial number U26097 and higher
DC | Wilkins | 350A | 10 | H | 2006-04-06 | 2024-04-06 | N | 9 | (ppp),qqq,sss,ttt,yyy,ssss,uuuu,vvvv,xxxx,yyyy,aaaaa,kkkkk,lllll,gggggg,iiiiii,jjjjjj,llllll,mmmmmm,oooooo | N |  |  | Up to serial number U26097
DC | Wilkins | 350A | 10 | H | 2010-09-09 | 2022-09-09 | Y | 9 | (ppp),qqq,sss,ttt,yyy,ssss,uuuu,vvvv,xxxx,yyyy,aaaaa,kkkkk,lllll,gggggg,iiiiii,jjjjjj,llllll,mmmmmm,oooooo | N |  |  | Serial number U26097 and higher
DC | Wilkins | 350A | 10 | VU | 2006-04-06 | 2024-04-06 | N | 9 | (ppp),qqq,sss,ttt,yyy,ssss,uuuu,vvvv,xxxx,yyyy,aaaaa,kkkkk,lllll,gggggg,iiiiii,jjjjjj,llllll,mmmmmm,oooooo | N |  |  | Up to serial number U26097
DC | Wilkins | 350A | 10 | VU | 2010-09-09 | 2022-09-09 | Y | 9 | (ppp),qqq,sss,ttt,yyy,ssss,uuuu,vvvv,xxxx,yyyy,aaaaa,kkkkk,lllll,gggggg,iiiiii,jjjjjj,llllll,mmmmmm,oooooo | N |  |  | Serial number U26097 and higher
DC | Wilkins | 350AR | 2.5 | H | 2010-06-16 | 2022-06-16 | N | 9 | (ppp),sss,ttt,qqq,yyy,zzz,dddd,ssss,uuuu,vvvv,xxxx,yyyy,aaaaa,kkkkk,lllll,gggggg,iiiiii,jjjjjj,llllll,mmmmmm,oooooo | N |  |  | Integral grooved spool between the #2 ck and #2 SOV - assembly length: min. 34 1/4" and max. 47 1/8" Up to serial number U26097
DC | Wilkins | 350AR | 2.5 | H | 2010-09-09 | 2022-09-09 | Y | 9 | (ppp),sss,ttt,qqq,yyy,zzz,dddd,ssss,uuuu,vvvv,xxxx,yyyy,aaaaa,kkkkk,lllll,gggggg,iiiiii,jjjjjj,llllll,mmmmmm,oooooo | N |  |  | Only Serial No. C00102 and higher approved. These have an Integral grooved spool between the #2 ck and #2 SOV with length: min. 34 1/4" and max. 47 1/8"
DC | Wilkins | 350AR | 2.5 | VU | 2010-06-16 | 2022-06-16 | N | 9 | (ppp),sss,ttt,qqq,yyy,zzz,dddd,ssss,uuuu,vvvv,xxxx,yyyy,aaaaa,kkkkk,lllll,gggggg,iiiiii,jjjjjj,llllll,mmmmmm,oooooo | N |  |  | Only Serial No. C00102 and higher approved. These have an Integral grooved spool between the #2 ck and #2 SOV with length: min. 34 1/4" and max. 47 1/8"
DC | Wilkins | 350AR | 2.5 | VU | 2010-09-09 | 2022-09-09 | Y | 9 | (ppp),sss,ttt,qqq,yyy,zzz,dddd,ssss,uuuu,vvvv,xxxx,yyyy,aaaaa,kkkkk,lllll,gggggg,iiiiii,jjjjjj,llllll,mmmmmm,oooooo | N |  |  | Only Serial No. C00102 and higher approved. These have an Integral grooved spool between the #2 ck and #2 SOV with length: min. 34 1/4" and max. 47 1/8"
DC | Wilkins | 350AR | 3 | H | 2010-06-16 | 2022-06-16 | N | 9 | (ppp),sss,ttt,qqq,yyy,zzz,dddd,ssss,uuuu,vvvv,xxxx,yyyy,aaaaa,kkkkk,lllll,gggggg,iiiiii,jjjjjj,llllll,mmmmmm,oooooo | N |  |  | Only Serial No. C00102 and higher approved. These have an Integral grooved spool between the #2 ck and #2 SOV with length: min. 34 3/4" and max. 48 1/8"
DC | Wilkins | 350AR | 3 | H | 2010-09-09 | 2022-09-09 | Y | 9 | (ppp),sss,ttt,qqq,yyy,zzz,dddd,ssss,uuuu,vvvv,xxxx,yyyy,aaaaa,kkkkk,lllll,gggggg,iiiiii,jjjjjj,llllll,mmmmmm,oooooo | N |  |  | Only Serial No. C00102 and higher approved. These have an Integral grooved spool between the #2 ck and #2 SOV with length: min. 34 3/4" and max. 48 1/8"
DC | Wilkins | 350AR | 3 | VU | 2010-06-16 | 2022-06-16 | N | 9 | (ppp),sss,ttt,qqq,yyy,zzz,dddd,ssss,uuuu,vvvv,xxxx,yyyy,aaaaa,kkkkk,lllll,gggggg,iiiiii,jjjjjj,llllll,mmmmmm,oooooo | N |  |  | Only Serial No. C00102 and higher approved. These have an Integral grooved spool between the #2 ck and #2 SOV with length: min. 35 3/4" and max. 62 1/4"
DC | Wilkins | 350AR | 3 | VU | 2010-09-09 | 2022-09-09 | Y | 9 | (ppp),sss,ttt,qqq,yyy,zzz,dddd,ssss,uuuu,vvvv,xxxx,yyyy,aaaaa,kkkkk,lllll,gggggg,iiiiii,jjjjjj,llllll,mmmmmm,oooooo | N |  |  | Only Serial No. C00102 and higher approved. These have an Integral grooved spool between the #2 ck and #2 SOV with length: min. 34 3/4" and max. 48 1/8"
DC | Wilkins | 350AR | 4 | H | 2010-03-25 | 2022-03-25 | N | 9 | (ppp),qqq,sss,ttt,www,yyy,zzz,dddd,eeee,ssss,uuuu,vvvv,xxxx,yyyy,aaaaa,kkkkk,lllll,gggggg,iiiiii,jjjjjj,llllll,mmmmmm,oooooo | N |  |  | Only Serial No. C00102 and higher approved. These have an Integral grooved spool between the #2 ck and #2 SOV with length: min. 42 1/2" and max. 71 1/4"
DC | Wilkins | 350AR | 4 | H | 2010-09-09 | 2022-09-09 | Y | 9 | (ppp),qqq,sss,ttt,www,yyy,zzz,dddd,eeee,ssss,uuuu,vvvv,xxxx,yyyy,aaaaa,kkkkk,lllll,gggggg,iiiiii,jjjjjj,llllll,mmmmmm,oooooo | N |  |  | Only Serial No. C00102 and higher approved. These have an Integral grooved spool between the #2 ck and #2 SOV with length: min. 35 3/4" and max. 62 1/4"
DC | Wilkins | 350AR | 4 | VU | 2010-03-25 | 2022-03-25 | N | 9 | (ppp),qqq,sss,ttt,www,yyy,zzz,dddd,eeee,ssss,uuuu,vvvv,xxxx,yyyy,aaaaa,kkkkk,lllll,gggggg,iiiiii,jjjjjj,llllll,mmmmmm,oooooo | N |  |  | Only Serial No. C00102 and higher approved. These have an Integral grooved spool between the #2 ck and #2 SOV with length: min. 57 7/8" and max. 86"
DC | Wilkins | 350AR | 4 | VU | 2010-09-09 | 2022-09-09 | Y | 9 | (ppp),qqq,sss,ttt,www,yyy,zzz,dddd,eeee,ssss,uuuu,vvvv,xxxx,yyyy,aaaaa,kkkkk,lllll,gggggg,iiiiii,jjjjjj,llllll,mmmmmm,oooooo | N |  |  | Only Serial No. C00102 and higher approved. These have an Integral grooved spool between the #2 ck and #2 SOV with length: min. 35 3/4" and max. 62 1/4"
DC | Wilkins | 350AR | 6 | H | 2010-03-25 | 2022-03-25 | N | 9 | (ppp),qqq,sss,ttt,www,yyy,zzz,dddd,eeee,ssss,uuuu,vvvv,xxxx,yyyy,aaaaa,kkkkk,lllll,gggggg,iiiiii,jjjjjj,llllll,mmmmmm,oooooo | N |  |  | Only Serial No. C00102 and higher approved. These have an Integral grooved spool between the #2 ck and #2 SOV with length: min. 61 3/8" and max. 100 5/8"
DC | Wilkins | 350AR | 6 | H | 2010-09-09 | 2022-09-09 | Y | 9 | (ppp),qqq,sss,ttt,www,yyy,zzz,dddd,eeee,ssss,uuuu,vvvv,xxxx,yyyy,aaaaa,kkkkk,lllll,gggggg,iiiiii,jjjjjj,llllll,mmmmmm,oooooo | N |  |  | Only Serial No. C00102 and higher approved. These have an Integral grooved spool between the #2 ck and #2 SOV with length: min. 42 1/2" and max. 71 1/4"
DC | Wilkins | 350AR | 6 | VU | 2010-03-25 | 2022-03-25 | N | 9 | (ppp),qqq,sss,ttt,www,yyy,zzz,dddd,eeee,ssss,uuuu,vvvv,xxxx,yyyy,aaaaa,kkkkk,lllll,gggggg,iiiiii,jjjjjj,llllll,mmmmmm,oooooo | N |  |  | Only Serial No. C00102 and higher approved. These have an Integral grooved spool between the #2 ck and #2 SOV with length: min. 34 1/4" and max. 47 1/8"
DC | Wilkins | 350AR | 6 | VU | 2010-09-09 | 2022-09-09 | Y | 9 | (ppp),qqq,sss,ttt,www,yyy,zzz,dddd,eeee,ssss,uuuu,vvvv,xxxx,yyyy,aaaaa,kkkkk,lllll,gggggg,iiiiii,jjjjjj,llllll,mmmmmm,oooooo | N |  |  | Only Serial No. C00102 and higher approved. These have an Integral grooved spool between the #2 ck and #2 SOV with length: min. 42 1/2" and max. 71 1/4"
DC | Wilkins | 350AR | 8 | H | 2010-03-25 | 2022-03-25 | N | 9 | (ppp),qqq,sss,ttt,www,yyy,zzz,dddd,eeee,ssss,uuuu,vvvv,xxxx,yyyy,aaaaa,kkkkk,lllll,gggggg,iiiiii,jjjjjj,llllll,mmmmmm,oooooo | N |  |  | Only Serial No. C00102 and higher approved. These have an Integral grooved spool between the #2 ck and #2 SOV with length: min. 34 1/4" and max. 47 1/8"
DC | Wilkins | 350AR | 8 | H | 2010-09-09 | 2022-09-09 | Y | 9 | (ppp),qqq,sss,ttt,www,yyy,zzz,dddd,eeee,ssss,uuuu,vvvv,xxxx,yyyy,aaaaa,kkkkk,lllll,gggggg,iiiiii,jjjjjj,llllll,mmmmmm,oooooo | N |  |  | Only Serial No. C00102 and higher approved. These have an Integral grooved spool between the #2 ck and #2 SOV with length: min. 57 7/8" and max. 86"
DC | Wilkins | 350AR | 8 | VU | 2010-03-25 | 2022-03-25 | N | 9 | (ppp),qqq,sss,ttt,www,yyy,zzz,dddd,eeee,ssss,uuuu,vvvv,xxxx,yyyy,aaaaa,kkkkk,lllll,gggggg,iiiiii,jjjjjj,llllll,mmmmmm,oooooo | N |  |  | Only Serial No. C00102 and higher approved. These have an Integral grooved spool between the #2 ck and #2 SOV with length: min. 34 1/4" and max. 47 1/8"
DC | Wilkins | 350AR | 8 | VU | 2010-09-09 | 2022-09-09 | Y | 9 | (ppp),qqq,sss,ttt,www,yyy,zzz,dddd,eeee,ssss,uuuu,vvvv,xxxx,yyyy,aaaaa,kkkkk,lllll,gggggg,iiiiii,jjjjjj,llllll,mmmmmm,oooooo | N |  |  | Only Serial No. C00102 and higher approved. These have an Integral grooved spool between the #2 ck and #2 SOV with length: min. 57 7/8" and max. 86"
DC | Wilkins | 350AR | 10 | H | 2010-03-25 | 2022-03-25 | N | 9 | (ppp),qqq,sss,ttt,www,yyy,zzz,dddd,eeee,ssss,uuuu,vvvv,xxxx,yyyy,aaaaa,kkkkk,lllll,gggggg,iiiiii,jjjjjj,llllll,mmmmmm,oooooo | N |  |  | Only Serial No. C00102 and higher approved. These have an Integral grooved spool between the #2 ck and #2 SOV with length: min. 34 1/4" and max. 47 1/8"
DC | Wilkins | 350AR | 10 | H | 2010-09-09 | 2022-09-09 | Y | 9 | (ppp),qqq,sss,ttt,www,yyy,zzz,dddd,eeee,ssss,uuuu,vvvv,xxxx,yyyy,aaaaa,kkkkk,lllll,gggggg,iiiiii,jjjjjj,llllll,mmmmmm,oooooo | N |  |  | Only Serial No. C00102 and higher approved. These have an Integral grooved spool between the #2 ck and #2 SOV with length: min. 61 3/8" and max. 100 5/8"
DC | Wilkins | 350AR | 10 | VU | 2010-03-25 | 2022-03-25 | N | 9 | (ppp),qqq,sss,ttt,www,yyy,zzz,dddd,eeee,ssss,uuuu,vvvv,xxxx,yyyy,aaaaa,kkkkk,lllll,gggggg,iiiiii,jjjjjj,llllll,mmmmmm,oooooo | N |  |  | Only Serial No. C00102 and higher approved. These have an Integral grooved spool between the #2 ck and #2 SOV with length: min. 34 1/4" and max. 47 1/8"
DC | Wilkins | 350AR | 10 | VU | 2010-09-09 | 2022-09-09 | Y | 9 | (ppp),qqq,sss,ttt,www,yyy,zzz,dddd,eeee,ssss,uuuu,vvvv,xxxx,yyyy,aaaaa,kkkkk,lllll,gggggg,iiiiii,jjjjjj,llllll,mmmmmm,oooooo | N |  |  | Only Serial No. C00102 and higher approved. These have an Integral grooved spool between the #2 ck and #2 SOV with length: min. 61 3/8" and max. 100 5/8"
DC | Wilkins | 350AST | 2.5 | H | 2011-11-29 | 2023-11-29 | Y | 10 | (ppp),qqq,yyy,ssss,uuuu,vvvv,xxxx,yyyy,aaaaa,kkkkk,lllll,gggggg,iiiiii,jjjjjj,llllll,mmmmmm,oooooo | N
DC | Wilkins | 350AST | 2.5 | VU | 2012-11-09 | 2024-11-09 | Y | 10 | (ppp),qqq,yyy,ssss,uuuu,vvvv,xxxx,yyyy,aaaaa,kkkkk,lllll,gggggg,iiiiii,jjjjjj,llllll,mmmmmm,oooooo | N
DC | Wilkins | 350AST | 3 | H | 2011-11-29 | 2023-11-29 | Y | 10 | (ppp),qqq,yyy,ssss,uuuu,vvvv,xxxx,yyyy,aaaaa,kkkkk,lllll,gggggg,iiiiii,jjjjjj,llllll,mmmmmm,oooooo | N
DC | Wilkins | 350AST | 3 | VU | 2012-11-09 | 2024-11-09 | Y | 10 | (ppp),qqq,yyy,ssss,uuuu,vvvv,xxxx,yyyy,aaaaa,kkkkk,lllll,gggggg,iiiiii,jjjjjj,llllll,mmmmmm,oooooo | N
DC | Wilkins | 350AST | 4 | H | 2011-11-29 | 2023-11-29 | Y | 10 | (ppp),qqq,yyy,ssss,uuuu,vvvv,xxxx,yyyy,aaaaa,kkkkk,lllll,gggggg,iiiiii,jjjjjj,llllll,mmmmmm,oooooo | N
DC | Wilkins | 350AST | 4 | VU | 2012-11-09 | 2024-11-09 | Y | 10 | (ppp),qqq,yyy,ssss,uuuu,vvvv,xxxx,yyyy,aaaaa,kkkkk,lllll,gggggg,iiiiii,jjjjjj,llllll,mmmmmm,oooooo | N
DC | Wilkins | 350AST | 6 | H | 2012-03-27 | 2024-03-27 | Y | 10 | (yyy),ssss,uuuu,vvvv,xxxx,yyyy,aaaaa,kkkkk,lllll,gggggg,iiiiii,jjjjjj,llllll,mmmmmm,oooooo | N
DC | Wilkins | 350AST | 6 | VU | 2012-10-24 | 2024-10-24 | Y | 10 | (yyy),ssss,uuuu,vvvv,xxxx,yyyy,aaaaa,kkkkk,lllll,gggggg,iiiiii,jjjjjj,llllll,mmmmmm,oooooo | N
DC | Wilkins | 350AST | 8 | H | 2014-02-20 | 2023-02-20 | Y | 10 | (yyy),ssss,uuuu,vvvv,xxxx,yyyy,aaaaa,kkkkk,lllll,gggggg,iiiiii,jjjjjj,llllll,mmmmmm,oooooo | N
DC | Wilkins | 350AST | 8 | VU | 2014-02-20 | 2023-02-20 | Y | 10 | (yyy),ssss,uuuu,vvvv,xxxx,yyyy,aaaaa,kkkkk,lllll,gggggg,iiiiii,jjjjjj,llllll,mmmmmm,oooooo | N
DC | Wilkins | 350AST | 10 | H | 2014-02-20 | 2023-02-20 | Y | 10 | (yyy),ssss,uuuu,vvvv,xxxx,yyyy,aaaaa,kkkkk,lllll,gggggg,iiiiii,jjjjjj,llllll,mmmmmm,oooooo | N
DC | Wilkins | 350AST | 10 | VU | 2014-02-20 | 2023-02-20 | Y | 10 | (yyy),ssss,uuuu,vvvv,xxxx,yyyy,aaaaa,kkkkk,lllll,gggggg,iiiiii,jjjjjj,llllll,mmmmmm,oooooo | N
DC | Wilkins | 350ASTR | 2.5 | H | 2015-06-12 | 2024-06-12 | Y | 10 | (ppp),qqq,yyy,ssss,uuuu,vvvv,xxxx,yyyy,aaaaa,kkkkk,lllll,gggggg,iiiiii,jjjjjj,llllll,mmmmmm,oooooo | N |  |  | Integral Stainless Steel grooved spool between the #2 ck and #2 SOV - assembly length: min. 34 1/4" and max. 47 1/8"
DC | Wilkins | 350ASTR | 2.5 | VU | 2015-06-12 | 2024-06-12 | Y | 10 | (ppp),qqq,yyy,ssss,uuuu,vvvv,xxxx,yyyy,aaaaa,kkkkk,lllll,gggggg,iiiiii,jjjjjj,llllll,mmmmmm,oooooo | N |  |  | Integral Stainless Steel grooved spool between the #2 ck and #2 SOV - assembly length: min. 34 1/4" and max. 47 1/8"
DC | Wilkins | 350ASTR | 3 | H | 2015-06-12 | 2024-06-12 | Y | 10 | (ppp),qqq,yyy,ssss,uuuu,vvvv,xxxx,yyyy,aaaaa,kkkkk,lllll,gggggg,iiiiii,jjjjjj,llllll,mmmmmm,oooooo | N |  |  | Integral Stainless Steel grooved spool between the #2 ck and #2 SOV - assembly length: min. 34 3/4" and max. 48 1/8"
DC | Wilkins | 350ASTR | 3 | VU | 2015-06-12 | 2024-06-12 | Y | 10 | (ppp),qqq,yyy,ssss,uuuu,vvvv,xxxx,yyyy,aaaaa,kkkkk,lllll,gggggg,iiiiii,jjjjjj,llllll,mmmmmm,oooooo | N |  |  | Integral Stainless Steel grooved spool between the #2 ck and #2 SOV - assembly length: min. 34 3/4" and max. 48 1/8"
DC | Wilkins | 350ASTR | 4 | H | 2015-06-12 | 2024-06-12 | Y | 10 | (ppp),qqq,yyy,ssss,uuuu,vvvv,xxxx,yyyy,aaaaa,kkkkk,lllll,gggggg,iiiiii,jjjjjj,llllll,mmmmmm,oooooo | N |  |  | Integral Stainless Steel grooved spool between the #2 ck and #2 SOV - assembly length: min. 35 3/4" and max. 62 1/4"
DC | Wilkins | 350ASTR | 4 | VU | 2015-06-12 | 2024-06-12 | Y | 10 | (ppp),qqq,yyy,ssss,uuuu,vvvv,xxxx,yyyy,aaaaa,kkkkk,lllll,gggggg,iiiiii,jjjjjj,llllll,mmmmmm,oooooo | N |  |  | Integral Stainless Steel grooved spool between the #2 ck and #2 SOV - assembly length: min. 35 3/4" and max. 62 1/4"
DC | Wilkins | 350ASTR | 6 | H | 2015-06-12 | 2024-06-12 | Y | 10 | (yyy),ssss,uuuu,vvvv,xxxx,yyyy,aaaaa,kkkkk,lllll,gggggg,iiiiii,jjjjjj,llllll,mmmmmm,oooooo | N |  |  | Integral Stainless Steel grooved spool between the #2 ck and #2 SOV - assembly length: min. 42 1/2" and max. 71 1/4"
DC | Wilkins | 350ASTR | 6 | VU | 2015-06-12 | 2024-06-12 | Y | 10 | (yyy),ssss,uuuu,vvvv,xxxx,yyyy,aaaaa,kkkkk,lllll,gggggg,iiiiii,jjjjjj,llllll,mmmmmm,oooooo | N |  |  | Integral Stainless Steel grooved spool between the #2 ck and #2 SOV - assembly length: min. 42 1/2" and max. 71 1/4"
DC | Wilkins | 350ASTR | 8 | H | 2014-02-25 | 2023-02-25 | Y | 10 | (yyy),ssss,uuuu,vvvv,xxxx,yyyy,aaaaa,kkkkk,lllll,gggggg,iiiiii,jjjjjj,llllll,mmmmmm,oooooo | N |  |  | Integral Stainless Steel grooved spool between the #2 ck and #2 SOV - assembly length: min. 48 3/4" and max. 86"
DC | Wilkins | 350ASTR | 8 | VU | 2014-02-25 | 2023-02-25 | Y | 10 | (yyy),ssss,uuuu,vvvv,xxxx,yyyy,aaaaa,kkkkk,lllll,gggggg,iiiiii,jjjjjj,llllll,mmmmmm,oooooo | N |  |  | Integral Stainless Steel grooved spool between the #2 ck and #2 SOV - assembly length: min. 48 3/4" and max. 86"
DC | Wilkins | 350ASTR | 10 | H | 2014-02-25 | 2023-02-25 | Y | 10 | (yyy),ssss,uuuu,vvvv,xxxx,yyyy,aaaaa,kkkkk,lllll,gggggg,iiiiii,jjjjjj,llllll,mmmmmm,oooooo | N |  |  | Integral Stainless Steel grooved spool between the #2 ck and #2 SOV - assembly length: min. 52 5/8" and max. 100 5/8"
DC | Wilkins | 350ASTR | 10 | VU | 2014-02-25 | 2023-02-25 | Y | 10 | (yyy),ssss,uuuu,vvvv,xxxx,yyyy,aaaaa,kkkkk,lllll,gggggg,iiiiii,jjjjjj,llllll,mmmmmm,oooooo | N |  |  | Integral Stainless Steel grooved spool between the #2 ck and #2 SOV - assembly length: min. 52 5/8" and max. 100 5/8"
DC | Wilkins | 350D | 0.75 | H | 2009-05-19 | 2024-05-19 | N | 9 | (ii), ooo | N
DC | Wilkins | 350D | 0.75 | VU | 2009-06-22 | 2024-06-22 | N | 9 | (ii), ooo | N
DC | Wilkins | 350XL | 0.75 | H | 2006-08-30 | 2024-08-30 | Y | 9 | (iiii) | N |  |  | Testcocks: Female Threaded End or 45 degree male SAE flare
DC | Wilkins | 350XL | 0.75 | VU | 2006-08-30 | 2024-08-30 | Y | 9 | (iiii) | N |  |  | Testcocks: Female Threaded End or 45 degree male SAE flare
DC | Wilkins | 350XL | 1 | H | 2006-10-27 | 2024-10-27 | Y | 9 | (iiii) | N |  |  | Testcocks: Female Threaded End or 45 degree male SAE flare
DC | Wilkins | 350XL | 1 | VU | 2006-10-27 | 2024-10-27 | Y | 9 | (iiii) | N |  |  | Testcocks: Female Threaded End or 45 degree male SAE flare
DC | Wilkins | 350XL | 1.25 | H | 2009-01-08 | 2024-01-08 | Y | 9 | (int) | N
DC | Wilkins | 350XL | 1.25 | VU | 2009-01-08 | 2024-01-08 | Y | 9 | (int) | N
DC | Wilkins | 350XL | 1.5 | H | 2009-01-08 | 2024-01-08 | Y | 9 | (int) | N
DC | Wilkins | 350XL | 1.5 | VU | 2009-01-08 | 2024-01-08 | Y | 9 | (int) | N
DC | Wilkins | 350XL | 2 | H | 2009-01-08 | 2024-01-08 | Y | 9 | (int) | N
DC | Wilkins | 350XL | 2 | VU | 2009-01-08 | 2024-01-08 | Y | 9 | (int) | N
DC | Wilkins | 450ST | 4 | VUVD | 2018-06-13 | 2024-06-13 | Y | 10 | (kkkkk),yyy,ssss,uuuu,vvvv,xxxx,yyyy,aaaaa,lllll,gggggg,iiiiii,jjjjjj,llllll,mmmmmm,oooooo | N
DC | Wilkins | 450ST | 6 | VUVD | 2018-06-13 | 2024-06-13 | Y | 10 | (kkkkk),yyy,ssss,uuuu,vvvv,xxxx,yyyy,aaaaa,lllll,gggggg,iiiiii,jjjjjj,llllll,mmmmmm,oooooo | N
DC | Wilkins | 450ST | 8 | VUVD | 2018-12-18 | 2024-12-18 | Y | 10 | (kkkkk),yyy,ssss,uuuu,vvvv,xxxx,yyyy,aaaaa,lllll,gggggg,iiiiii,jjjjjj,llllll,mmmmmm,oooooo | N
DC | Wilkins | 450ST | 10 | VUVD | 2018-12-18 | 2024-12-18 | Y | 10 | (kkkkk),yyy,ssss,uuuu,vvvv,xxxx,yyyy,aaaaa,lllll,gggggg,iiiiii,jjjjjj,llllll,mmmmmm,oooooo | N
DC | Wilkins | 450STR | 4 | VUVD | 2018-06-13 | 2024-06-13 | Y | 10 | (kkkkk),yyy,ssss,uuuu,vvvv,xxxx,yyyy,aaaaa,lllll,gggggg,iiiiii,jjjjjj,llllll,mmmmmm,oooooo | N
DC | Wilkins | 450STR | 6 | VUVD | 2018-06-13 | 2024-06-13 | Y | 10 | (kkkkk),yyy,ssss,uuuu,vvvv,xxxx,yyyy,aaaaa,lllll,gggggg,iiiiii,jjjjjj,llllll,mmmmmm,oooooo | N
DC | Wilkins | 450STR | 8 | VUVD | 2018-12-18 | 2024-12-18 | Y | 10 | (kkkkk),yyy,ssss,uuuu,vvvv,xxxx,yyyy,aaaaa,lllll,gggggg,iiiiii,jjjjjj,llllll,mmmmmm,oooooo | N
DC | Wilkins | 450STR | 10 | VUVD | 2018-12-18 | 2024-12-18 | Y | 10 | (kkkkk),yyy,ssss,uuuu,vvvv,xxxx,yyyy,aaaaa,lllll,gggggg,iiiiii,jjjjjj,llllll,mmmmmm,oooooo | N
DC | Wilkins | 550 | 2.5 | H | 1986-09-25 | 2022-09-25 | N | 7 | (ppp),qqq,sss,ttt,yyy,ssss,uuuu,vvvv,xxxx,yyyy,aaaaa | Y
DC | Wilkins | 550A | 0.75 | H | 1987-04-17 | 2023-04-17 | N | 7 | (ppp),qqq,sss,ttt,yyy,ssss,uuuu,vvvv,xxxx,yyyy,aaaaa | Y
DC | Wilkins | 550A | 1 | H | 1987-04-17 | 2023-04-17 | N | 7 | (ppp),qqq,sss,ttt,yyy,ssss,uuuu,vvvv,xxxx,yyyy,aaaaa | Y
DC | Wilkins | 550M | 8 | H | 1989-03-15 | 2022-03-15 | N | 8 | (ppp),sss,ttt,qqq,yyy,zzz,dddd,ssss,uuuu,vvvv,xxxx,yyyy,aaaaa | Y |  |  | 4"x4"x8" Manifold Formerly MBD
DC | Wilkins | 550M | 10 | H | 1983-04-11 | 2022-04-11 | N | 6 | (ppp),sss,ttt,qqq,yyy,zzz,dddd,ssss,uuuu,vvvv,xxxx,yyyy,aaaaa | Y |  |  | 6"x6"x10" Manifold Formerly MBD
DC | Wilkins | 950A | 0.75 | H | 1991-07-18 | 2024-07-18 | N | 8 | (ppp),qqq,sss,ttt,www,yyy,ssss,uuuu,vvvv,xxxx,yyyy,aaaaa | Y
DC | Wilkins | 950A | 1 | H | 1991-07-18 | 2024-07-18 | N | 8 | (ppp),qqq,sss,ttt,www,yyy,ssss,uuuu,vvvv,xxxx,yyyy,aaaaa | Y
DC | Wilkins | 950A | 1.25 | H | 1991-07-18 | 2024-07-18 | N | 8 | ii | Y
DC | Wilkins | 950A | 1.5 | H | 1991-07-18 | 2024-07-18 | N | 8 | ii | Y
DC | Wilkins | 950A | 2 | H | 1991-07-18 | 2024-07-18 | N | 8 | ii | Y
DC | Wilkins | 950XL | 0.75 | H | 1992-11-02 | 2022-11-02 | N | 8 | (ii),ooo | N |  |  | Testcocks: Female Threaded End or 45 degree male SAE flare
DC | Wilkins | 950XL | 0.75 | VU | 1996-12-12 | 2023-12-12 | N | 8 | (ii),ooo | N |  |  | Testcocks: Female Threaded End or 45 degree male SAE flare
DC | Wilkins | 950XL | 1 | H | 1992-11-02 | 2022-11-02 | N | 8 | (ii),ooo | N |  |  | Testcocks: Female Threaded End or 45 degree male SAE flare
DC | Wilkins | 950XL | 1.25 | H | 1992-11-02 | 2022-11-02 | N | 8 | (ii),ooo,ggg | N
DC | Wilkins | 950XL | 1.5 | H | 1992-11-02 | 2022-11-02 | N | 8 | (ii),ooo | N
DC | Wilkins | 950XL | 2 | H | 1992-11-02 | 2022-11-02 | N | 8 | (ii),bbb,ooo | N
DC | Wilkins | 950XL3 | 0.75 | H | 2022-09-06 |  | Y | 10 | (iiii) | N
DC | Wilkins | 950XL3 | 0.75 | VU | 2022-09-06 |  | Y | 10 | (iiii) | N
DC | Wilkins | 950XL3 | 1 | H | 2022-09-06 |  | Y | 10 | (iiii) | N
DC | Wilkins | 950XL3 | 1 | VU | 2022-09-06 |  | Y | 10 | (iiii) | N
DC | Wilkins | 950XL3 | 1.25 | H | 2022-09-06 |  | Y | 10 | (iiii) | N
DC | Wilkins | 950XL3 | 1.25 | VU | 2022-09-06 |  | Y | 10 | (iiii) | N
DC | Wilkins | 950XL3 | 1.5 | H | 2022-09-06 |  | Y | 10 | (iiii) | N
DC | Wilkins | 950XL3 | 1.5 | VU | 2022-09-06 |  | Y | 10 | (iiii) | N
DC | Wilkins | 950XL3 | 2 | H | 2022-09-06 |  | Y | 10 | (iiii) | N
DC | Wilkins | 950XL3 | 2 | VU | 2022-09-06 |  | Y | 10 | (iiii) | N
DC | Wilkins | 950XL3BFSS | 2 | H | 2023-05-23 |  | Y | 10 | (pppppp) | N
DC | Wilkins | 950XL3BFSS | 2 | VU | 2023-05-23 |  | Y | 10 | (pppppp) | N
DC | Wilkins | 950XL3U | 0.75 | H | 2022-09-06 |  | Y | 10 | (mmmmm) | N
DC | Wilkins | 950XL3U | 0.75 | VU | 2022-09-06 |  | Y | 10 | (mmmmm) | N
DC | Wilkins | 950XL3U | 1 | H | 2022-09-06 |  | Y | 10 | (mmmmm) | N
DC | Wilkins | 950XL3U | 1 | VU | 2022-09-06 |  | Y | 10 | (mmmmm) | N
DC | Wilkins | 950XL3U | 1.25 | H | 2022-09-06 |  | Y | 10 | (mmmmm) | N
DC | Wilkins | 950XL3U | 1.25 | VU | 2022-09-06 |  | Y | 10 | (mmmmm) | N
DC | Wilkins | 950XL3U | 1.5 | H | 2022-09-06 |  | Y | 10 | (mmmmm) | N
DC | Wilkins | 950XL3U | 1.5 | VU | 2022-09-06 |  | Y | 10 | (mmmmm) | N
DC | Wilkins | 950XL3U | 2 | H | 2022-09-06 |  | Y | 10 | (mmmmm) | N
DC | Wilkins | 950XL3U | 2 | VU | 2022-09-06 |  | Y | 10 | (mmmmm) | N
DC | Wilkins | 950XLD | 0.75 | H | 1999-09-15 | 2023-09-15 | N | 9 | (ii),ooo, iiii, mmmmm | N |  |  | Up to Serial # 3863324 Testcocks: Female Threaded End or 45 degree male SAE flare
DC | Wilkins | 950XLD | 0.75 | H | 1999-09-15 | 2023-09-15 | Y | 9 | (ii),ooo, iiii, mmmmm | N |  |  | Starting at Serial # 3863325 Testcocks: Female Threaded End or 45 degree male SAE flare
DC | Wilkins | 950XLD | 0.75 | H | 2013-07-03 | 2022-07-03 | N | 10 | (iiii), mmmmm | N |  |  | Up to Serial # 3863324 Testcocks: Female Threaded End or 45 degree male SAE flare
DC | Wilkins | 950XLD | 0.75 | H | 2013-07-03 | 2022-07-03 | Y | 10 | (iiii), mmmmm | N |  |  | Starting at Serial # 3863325 Testcocks: Female Threaded End or 45 degree male SAE flare
DC | Wilkins | 950XLD | 0.75 | VU | 2000-01-05 | 2023-01-05 | N | 9 | (ii),ooo, iiii, mmmmm | N |  |  | Up to Serial # 3863324 Testcocks: Female Threaded End or 45 degree male SAE flare
DC | Wilkins | 950XLD | 0.75 | VU | 2000-01-05 | 2023-01-05 | Y | 9 | (ii),ooo, iiii, mmmmm | N |  |  | Starting at Serial # 3863325 Testcocks: Female Threaded End or 45 degree male SAE flare
DC | Wilkins | 950XLD | 0.75 | VU | 2013-07-03 | 2022-07-03 | N | 10 | (iiii), mmmmm | N |  |  | Up to Serial # 3863324 Testcocks: Female Threaded End or 45 degree male SAE flare
DC | Wilkins | 950XLD | 0.75 | VU | 2013-07-03 | 2022-07-03 | Y | 10 | (iiii), mmmmm | N |  |  | Starting at Serial # 3863325 Testcocks: Female Threaded End or 45 degree male SAE flare
DC | Wilkins | 950XLDTCU | 0.75 | H | 2018-12-18 | 2024-12-18 | Y | 10 | (iiii), mmmmm | N
DC | Wilkins | 950XLT | 0.75 | H | 1997-05-09 | 2024-05-09 | N | 9 | (ii),ooo | N |  |  | Testcocks: Female Threaded End or 45 degree male SAE flare
DC | Wilkins | 950XLT | 1 | H | 1997-05-09 | 2024-05-09 | N | 9 | (ii),ooo | N |  |  | Testcocks: Female Threaded End or 45 degree male SAE flare
DC | Wilkins | 950XLT | 1.25 | H | 1998-06-19 | 2022-06-19 | N | 9 | (ii),ooo | N
DC | Wilkins | 950XLT | 1.5 | H | 1998-04-09 | 2022-04-09 | N | 9 | (ii),ooo | N
DC | Wilkins | 950XLT | 2 | H | 1998-04-09 | 2022-04-09 | N | 9 | (ii),ooo,bbbbb,ccccc,pppppp | N
DC | Wilkins | 950XLT2 | 0.75 | H | 2009-08-21 | 2024-08-21 | Y | 9 | (iiii) | N |  |  | Testcocks: Female Threaded End or 45 degree male SAE flare
DC | Wilkins | 950XLT2 | 1 | H | 2009-08-21 | 2024-08-21 | Y | 9 | (iiii) | N |  |  | Testcocks: Female Threaded End or 45 degree male SAE flare
DC | Wilkins | 950XLT2 | 1.25 | H | 2009-08-21 | 2024-08-21 | Y | 9 | (iiii) | N
DC | Wilkins | 950XLT2 | 1.5 | H | 2009-08-21 | 2024-08-21 | Y | 9 | (iiii) | N
DC | Wilkins | 950XLT2 | 2 | H | 2009-08-21 | 2024-08-21 | Y | 9 | (iiii),pppppp | N
DC | Wilkins | 950XLT2BFSS | 2 | H | 2021-11-05 | 2024-11-05 | Y | 9 | (pppppp) | N
DC | Wilkins | 950XLT2U | 0.75 | H | 2011-02-22 | 2023-02-22 | Y | 9 | (mmmmm) | N |  |  | Testcocks: Female Threaded End or 45 degree male SAE flare
DC | Wilkins | 950XLTBF | 2 | H | 2011-02-22 | 2023-02-22 | N | 9 | (bbbbb),pppppp | N
DC | Wilkins | 950XLTBFSS | 2 | H | 2011-02-22 | 2023-02-22 | N | 9 | (ccccc),pppppp | N
DC | Wilkins | 950XLTU | 0.75 | H | 2006-08-14 | 2024-08-14 | N | 9 | (ggg),xxx | N
DC | Wilkins | 950XLTU | 1 | H | 2006-08-14 | 2024-08-14 | N | 9 | (ggg),xxx | N
DC | Wilkins | 950XLU | 0.75 | H | 1994-02-15 | 2024-02-15 | N | 8 | (ggg),xxx | N |  |  | Testcocks: Female Threaded End or 45 degree male SAE flare
DC | Wilkins | 950XLU | 1 | H | 1994-02-15 | 2024-02-15 | N | 8 | (ggg),xxx | N |  |  | Testcocks: Female Threaded End or 45 degree male SAE flare
DC | Wilkins | 950XLU | 1.5 | H | 1994-02-15 | 2024-02-15 | N | 8 | (ggg),xxx | N
DC | Wilkins | 950XLU | 2 | H | 1994-02-15 | 2024-02-15 | N | 8 | (ggg),xxx | N
DC | Wilkins | MBD | 8 | [9 empty] | 4"x4"x8" Manifold, Model designation changed to 550M
DC | Wilkins | MBD | 10 | [9 empty] | 6"x6"x10" Manifold, Model designation changed to 550M
DCDA | Ames | 3000-1SS | 12 | H | 2009-12-04 | 2024-12-04 | N | 9 | (mm), ll | N | Ames 200B 3/4" (H); Watts 719QT 3/4" (H) | (N), H,I,J,K,L,M,O,P,Q
DCDA | Ames | 3000-1SS | 12 | VU | 2011-02-22 | 2023-02-22 | N | 9 | (mm), ll | N | Ames 200B 3/4" (VU); Watts 719QT 3/4" (VU) | (N), H,I,J,K,L,M,O,P,Q
DCDA | Ames | 3000B | 2 | H | 1997-06-16 | 2024-06-16 | N | 9 | (bbb),jjjj,rrrrr | N | Ames 2000B 1/2" (H), Watts 007QT 1/2" (H) | (H),A,B,C,D,E,F,G,I,J,K,L,M,N,O,P,Q,T
DCDA | Ames | 3000B | 2 | VU | 1997-06-16 | 2024-06-16 | N | 9 | (bbb),jjjj,rrrrr | N | Ames 2000B 1/2" (VU), Watts 007QT 1/2" (VU) | (H),A,B,C,D,E,F,G,I,J,K,L,M,N,O,P,Q,T
DCDA | Ames | 3000B-FP | 2 | H | 2009-09-01 | 2024-09-01 | N | 9 | (eeeee) | N | Ames 2000B 1/2" (H), Watts 007QT 1/2" (H) | (H),A,B,C,D,E,F,G,I,J,K,L,M,N,O,P,Q,T
DCDA | Ames | 3000BM1 | 2 | H | 2015-06-19 | 2024-06-19 | N | 9 | (eeeee), bbb, jjjj,rrrrr | N | Ames 2000B 1/2" (H), Watts 007QT 1/2" (H) | (H),A,B,C,D,E,F,G,I,J,K,L,M,N,O,P,Q,T
DCDA | Ames | 3000BM1 | 2 | VU | 2015-06-19 | 2024-06-19 | N | 9 | (eeeee), bbb, jjjj,rrrrr | N | Ames 2000B 1/2" (VU), Watts 007QT 1/2" (VU) | (H),A,B,C,D,E,F,G,I,J,K,L,M,N,O,P,Q,T
DCDA | Ames | 3000CIV | 4 | H | 1987-07-27 | 2023-07-27 | N | 6 | (pp),hh,uu,eee | Y | Ames 2000B 1/2"(H),Watts 007QT 1/2"(H) | (N),A,B,C,D,E,F,G,H,I,J,K,L,M,O,P,Q,T
DCDA | Ames | 3000CIV | 4 | VU | 1996-08-27 | 2023-08-27 | N | 8 | (pp),hh,uu,eee | Y | Ames 2000B 1/2"(VU),Watts 007QT 1/2"(VU) | (N),A,B,C,D,E,F,G,H,I,J,K,L,M,O,P,Q,T
DCDA | Ames | 3000CIV | 6 | H | 1987-07-27 | 2023-07-27 | N | 6 | (pp),hh,uu,eee | Y | Ames 2000B 1/2"(H),Watts 007QT 1/2"(H) | (N),A,B,C,D,E,F,G,H,I,J,K,L,M,O,P,Q,T
DCDA | Ames | 3000CIV | 6 | VU | 1996-12-05 | 2023-12-05 | N | 8 | (pp),hh,mm,uu,eee | Y | Ames 2000B 1/2" (VU), Watts 007QT 1/2" (VU) | (H),A,B,C,D,E,F,G,I,J,K,L,M,N,O,P,Q,T
DCDA | Ames | 3000CIV | 8 | H | 1987-04-19 | 2023-04-19 | N | 6 | (pp),hh,mm,uu,eee | Y | Ames 2000B 1/2"(H),Watts 007QT 1/2"(H) | (N),A,B,C,D,E,F,G,H,I,J,K,L,M,O,P,Q,T
DCDA | Ames | 3000CIV | 8 | VU | 1996-12-05 | 2023-12-05 | N | 8 | (pp),hh,mm,uu,eee | Y | Ames 2000B 1/2" (VU), Watts 007QT 1/2" (VU) | (H),A,B,C,D,E,F,G,I,J,K,L,M,N,O,P,Q,T
DCDA | Ames | 3000CIV | 10 | H | 1987-07-27 | 2023-07-27 | N | 6 | (pp),hh,mm,uu,eee | Y | Ames 2000B 1/2"(H),Watts 007QT 1/2"(H) | (N),E,F,G,H,I,J,K,L,M,O,P,Q,T
DCDA | Ames | 3000CIV | 10 | VU | 1996-12-05 | 2023-12-05 | N | 8 | (pp),hh,mm,uu,eee | Y | Ames 2000B 1/2" (VU), Watts 007QT 1/2" (VU) | (H),A,B,C,D,E,F,G,I,J,K,L,M,N,O,P,Q,T
DCDA | Ames | 3000DCDA | 4 | H | 1988-01-11 | 2024-01-11 | N | 7 | uu,ee,ff,gg,hh,mm,oo,pp,ccc,ddd,ffff,gggg | Y | Watts 007QT 3/4" (H) | (M),B,C,D,E,F,G,H,I,J,K,L,N,O,P,Q,T | formerly DCDA
DCDA | Ames | 3000DCDA | 6 | H | 1988-01-11 | 2024-01-11 | N | 7 | uu,ee,ff,gg,hh,mm,oo,pp,ccc,ddd,ffff,gggg | Y | Watts 709QT 3/4" (H) | (M),B,C,D,E,F,G,H,I,J,K,L,N,O,P,Q,T | formerly DCDA-I
DCDA | Ames | 3000DCDA | 8 | H | 1988-01-11 | 2024-01-11 | N | 7 | uu,ee,ff,gg,hh,mm,oo,pp,ccc,ddd,ffff,gggg | Y | Watts 007QT 3/4" (H) | (M),B,C,D,E,F,G,H,I,J,K,L,N,O,P,Q,T | formerly DCDA
DCDA | Ames | 3000DCDC | 10 | H | 1987-08-04 | 2023-08-04 | N | 7 | (uu),ee,ff,gg,hh,oo,pp,ccc,ddd,ffff,gggg | Y | Watts007M2QT 3/4" (H),Watts 709QT 3/4" (H), Ames 2000B 3/4" (H) | (M),B,C,D,E,F,G,H,I,J,K,L,N,O,P,Q,T | formerly DCDA
DCDA | Ames | 3000GDCDA | 4 | H | 1988-01-11 | 2024-01-11 | N | 7 | uu,ee,ff,gg,hh,mm,oo,pp,ccc,ddd,ffff,gggg | Y | Watts 007QT 3/4" (H) | (M),B,C,D,E,F,G,H,I,J,K,L,N,O,P,Q,T | formerly DCDA
DCDA | Ames | 3000GDCDA | 6 | H | 1988-01-11 | 2024-01-11 | N | 7 | uu,ee,ff,gg,hh,mm,oo,pp,ccc,ddd,ffff,gggg | Y | Watts 709QT 3/4" (H) | (M),B,C,D,E,F,G,H,I,J,K,L,N,O,P,Q,T | formerly DCDA-I
DCDA | Ames | 3000GDCDA | 8 | H | 1988-01-11 | 2024-01-11 | N | 7 | uu,ee,ff,gg,hh,mm,oo,pp,ccc,ddd,ffff,gggg | Y | Watts 007QT 3/4" (H) | (M),B,C,D,E,F,G,H,I,J,K,L,N,O,P,Q,T | formerly DCDA
DCDA | Ames | 3000GDCDC | 10 | H | 1987-08-04 | 2023-08-04 | N | 7 | uu,ee,ff,gg,hh,oo,pp,ccc,ddd,ffff,gggg | Y | Watts 709QT 3/4" (H) | (M),B,C,D,E,F,G,H,I,J,K,L,N,O,P,Q,T | formerly DCDC
DCDA | Ames | 3000SE | 2.5 | H | 1996-09-10 | 2023-09-10 | N | 8 | (mm),ee,ff,gg,hh,ll,oo,pp,tt,uu,ccc,ddd,ffff,gggg | Y | Watts007M2QT 3/4" (H), Ames 2000B 3/4" (H) | (M),N,O,P,Q
DCDA | Ames | 3000SE | 6 | H | 1995-05-24 | 2022-05-24 | N | 8 | uu,ee,ff,gg,hh,ll,mm,oo,pp,tt,ccc,ddd,ffff,gggg | Y | Watts007M2QT 3/4" (H), Ames 2000B 3/4" (H) | (M),A,B,C,D,E,F,G,H,I,J,K,L,N,O,P,Q,T
DCDA | Ames | 3000SE | 8 | H | 1992-09-09 | 2022-09-09 | N | 8 | uu,ee,ff,gg,hh,ll,mm,oo,pp,tt,ccc,ddd,ffff,gggg | Y | Watts 007M1QT 3/4" (H) | (M),A,B,C,D,E,F,G,H,I,J,K,L,N,O,P,Q,T
DCDA | Ames | 3000SEA | 8 | H | 1995-05-05 | 2022-05-05 | N | 8 | uu,ee,ff,gg,hh,ll,mm,oo,pp,tt,ccc,ddd,ffff,gggg | Y | Ames 2000SS 3/4" (H) | (M),A,B,C,D,E,F,G,H,I,J,K,L,N,O,P,Q,T
DCDA | Ames | 3000SEWM1 | 6 | H | 1993-11-22 | 2023-11-22 | N | 8 | (uu),ee,ff,gg,hh,ll,mm,oo,pp,tt,ccc,ddd,ffff,gggg | Y | Watts 007M1QT 3/4" (H) | (M),A,B,C,D,E,F,G,H,I,J,K,L,N,O,P,Q,T | formerly 3000SS prior to S/N 2EK0320
DCDA | Ames | 3000SS | 2.5 | H | 1995-05-24 | 2023-01-16 | N | 8 | (uu),ee,ff,gg,hh,ll,mm,oo,pp,tt,ccc,ddd,ffff,gggg | N | Watts007M2QT 3/4" (H), Ames 2000B 3/4" (H) | (M),A,B,C,D,E,F,G,H,I,J,K,L,N,O,P,Q,T
DCDA | Ames | 3000SS | 2.5 | [9 empty] | to S/N 2EK0320 model designation changed to 3000SSWM1
DCDA | Ames | 3000SS | 3 | H | 1995-05-24 | 2023-01-16 | N | 8 | (uu),ee,ff,gg,hh,ll,mm,oo,pp,tt,ccc,ddd,ffff,gggg | N | Watts007M2QT 3/4" (H), Ames 2000B 3/4" (H) | (M),A,B,C,D,E,F,G,H,I,J,K,L,N,O,P,Q,T
DCDA | Ames | 3000SS | 3 | [9 empty] | to S/N 2EK0320 model designation changed to 3000SSWM1
DCDA | Ames | 3000SS | 4 | H | 1995-05-24 | 2023-01-16 | N | 8 | (uu),ee,ff,gg,hh,ll,mm,oo,pp,tt,ccc,ddd,ffff,gggg | N | Watts007M2QT 3/4" (H), Ames 2000B 3/4" (H) | (M),A,B,C,D,E,F,G,H,I,J,K,L,N,O,P,Q,T
DCDA | Ames | 3000SS | 4 | [9 empty] | to S/N 2EK0320 model designation changed to 3000SSWM1
DCDA | Ames | 3000SS | 6 | H | 1992-09-09 | 2022-09-09 | N | 8 | (uu),ee,ff,gg,hh,ll,mm,oo,pp,tt,ccc,ddd,ffff,gggg | N | Watts 007M1QT 3/4" (H)), Watts 007M3QT 3/4" (H) | (M),A,B,C,D,E,F,G,H,I,J,K,L,N,O,P,Q,T
DCDA | Ames | 3000SS | 6 | [9 empty] | to S/N 2EK0320 model designation changed to 3000SEWM1
DCDA | Ames | 3000SS | 8 | H | 1996-09-16 | 2023-09-16 | N | 8 | (uu),ee,ff,gg,hh,ll,mm,tt,ccc,ddd,ffff,gggg | N | Watts007M2QT 3/4" (H), Ames 2000B 3/4" (H) | (M),A,B,C,D,E,F,G,H,I,J,K,L,N,O,P,Q,T
DCDA | Ames | 3000SS | 10 | H | 2001-02-16 | 2022-02-16 | N | 8 | (ll),mm,oo,pp,ffff,gggg | N | Ames 2000B 3/4" (H) | (J),C,E,F,G,H,I,K,L,M,N,O,P,Q,T
DCDA | Ames | 3000SS | 12 | H | 2009-12-04 | 2024-12-04 | N | 9 | (mm), ll | N | Ames 2000BM3 3/4" (H) | (N), H,I,J,K,L,M,O,P,Q
DCDA | Ames | 3000SS | 12 | VU | 2011-02-22 | 2023-02-22 | N | 9 | (mm), ll | N | Ames 2000BM3 3/4" (VU) | (N), H,I,J,K,L,M,O,P,Q
DCDA | Ames | 3000SSA | 6 | H | 1995-05-05 | 2022-05-05 | N | 8 | uu,ee,ff,gg,hh,ll,mm,oo,pp,tt,ccc,ddd,ffff,gggg | Y | Ames 2000SS 3/4" (H) | (M),A,B,C,D,E,F,G,H,I,J,K,L,N,O,P,Q,T
DCDA | Ames | 3000SSM | 4 | H | 1995-05-05 | 2022-05-05 | N | 8 | uu,ee,ff,gg,hh,ll,mm,oo,pp,tt,ccc,ddd,ffff,gggg | Y | Ames 2000SS 1" (H) | (R)
DCDA | Ames | 3000SSM | 6 | H | 1995-05-05 | 2022-05-05 | N | 8 | (uu),ee,ff,gg,hh,ll,mm,oo,pp,tt,ccc,ddd,ffff,gggg | N | Watts 007M2QT 1 1/2" (H) | (S)
DCDA | Ames | 3000SSWM1 | 2.5 | H | 1991-07-11 | 2024-07-11 | N | 8 | (uu),ee,ff,gg,hh,ll,mm,oo,pp,tt,ccc,ddd,ffff,gggg | N | Watts 007M1QT 3/4" (H) | (M),A,B,C,D,E,F,G,H,I,J,K,L,N,O,P,Q,T | formerly 3000SS prior to S/N 2EK0320
DCDA | Ames | 3000SSWM1 | 3 | H | 1991-07-11 | 2024-07-11 | N | 8 | (uu),ee,ff,gg,hh,ll,mm,oo,pp,tt,ccc,ddd,ffff,gggg | N | Watts 007M1QT 3/4" (H) | (M),A,B,C,D,E,F,G,H,I,J,K,L,N,O,P,Q,T | formerly 3000SS prior to S/N 2EK0320
DCDA | Ames | 3000SSWM1 | 4 | H | 1991-07-11 | 2024-07-11 | N | 8 | (uu),ee,ff,gg,hh,ll,mm,oo,pp,tt,ccc,ddd,ffff,gggg | N | Watts 007M1QT 3/4" (H) | (M),A,B,C,D,E,F,G,H,I,J,K,L,N,O,P,Q,T | formerly 3000SS prior to S/N 2EK0320
DCDA | Ames | Colt 300aBF | 2.5 | H | 2003-11-06 | 2024-11-06 | N | 9 | (yyy) | Y | Ames 2000BM3 3/4" (H) | (N),G,H,I,J,K,L,M,O,P,Q,T
DCDA | Ames | Colt 300aBF | 2.5 | VU | 2003-11-06 | 2024-11-06 | N | 9 | (yyy) | Y | Ames 2000BM3 3/4" (VU) | (N),G,H,I,J,K,L,M,O,P,Q,T
DCDA | Ames | Colt 300aBF | 3 | H | 2003-11-06 | 2024-11-06 | N | 9 | (yyy) | Y | Ames 2000BM3 3/4" (H) | (N),G,H,I,J,K,L,M,O,P,Q,T
DCDA | Ames | Colt 300aBF | 3 | VU | 2003-11-06 | 2024-11-06 | N | 9 | (yyy) | Y | Ames 2000BM3 3/4" (VU) | (N),G,H,I,J,K,L,M,O,P,Q,T
DCDA | Ames | Colt 300aBF | 4 | H | 2003-11-06 | 2024-11-06 | N | 9 | (yyy) | Y | Ames 2000BM3 3/4" (H) | (N),G,H,I,J,K,L,M,O,P,Q,T
DCDA | Ames | Colt 300aBF | 4 | VU | 2003-11-06 | 2024-11-06 | N | 9 | (yyy) | Y | Ames 2000BM3 3/4" (VU) | (N),G,H,I,J,K,L,M,O,P,Q,T
DCDA | Ames | Colt 300aBF | 6 | H | 2004-09-29 | 2022-09-29 | N | 9 | (yyy) | Y | Ames 2000BM3 3/4" (H) | (N),G,H,I,J,K,L,M,O,P,Q,T
DCDA | Ames | Colt 300aBF | 6 | VU | 2005-01-18 | 2023-01-18 | N | 9 | (yyy) | Y | Ames 2000BM3 3/4" (VU) | (N),G,H,I,J,K,L,M,O,P,Q,T
DCDA | Ames | Colt 300aGV | 2.5 | H | 2003-10-06 | 2024-10-06 | N | 9 | (zzz) | Y | Ames 2000BM3 3/4" (H) | (N),G,H,I,J,K,L,M,O,P,Q,T
DCDA | Ames | Colt 300aGV | 2.5 | VU | 2003-10-06 | 2024-10-06 | N | 9 | (zzz) | Y | Ames 2000BM3 3/4" (VU) | (N),G,H,I,J,K,L,M,O,P,Q,T
DCDA | Ames | Colt 300aGV | 3 | H | 2003-10-06 | 2024-10-06 | N | 9 | (zzz) | Y | Ames 2000BM3 3/4" (H) | (N),G,H,I,J,K,L,M,O,P,Q,T
DCDA | Ames | Colt 300aGV | 3 | VU | 2003-10-06 | 2024-10-06 | N | 9 | (zzz) | Y | Ames 2000BM3 3/4" (VU) | (N),G,H,I,J,K,L,M,O,P,Q,T
DCDA | Ames | Colt 300aGV | 4 | H | 2003-10-06 | 2024-10-06 | N | 9 | (zzz) | Y | Ames 2000BM3 3/4" (H) | (N),G,H,I,J,K,L,M,O,P,Q,T
DCDA | Ames | Colt 300aGV | 4 | VU | 2003-10-06 | 2024-10-06 | N | 9 | (zzz) | Y | Ames 2000BM3 3/4" (VU) | (N),G,H,I,J,K,L,M,O,P,Q,T
DCDA | Ames | Colt 300aGV | 6 | H | 2004-11-03 | 2022-11-03 | N | 9 | (zzz) | Y | Ames 2000BM3 3/4 (H) | (N),G,H,I,J,K,L,M,O,P,Q,T
DCDA | Ames | Colt 300aGV | 6 | VU | 2005-01-18 | 2023-01-18 | N | 9 | (zzz) | Y | Ames 2000BM3 3/4" (VU) | (N),G,H,I,J,K,L,M,O,P,Q,T
DCDA | Ames | Colt 300BF | 2.5 | H | 2005-10-04 | 2023-10-04 | N | 9 | (yyy) | N | Ames 2000BM3 3/4" (H) | (N),G,H,I,J,K,L,M,O,P,Q,T
DCDA | Ames | Colt 300BF | 2.5 | VU | 2005-10-04 | 2023-10-04 | N | 9 | (yyy) | N | Ames 2000BM3 3/4" (VU) | (N),G,H,I,J,K,L,M,O,P,Q,T
DCDA | Ames | Colt 300BF | 3 | H | 2005-10-04 | 2023-10-04 | N | 9 | (yyy) | N | Ames 2000BM3 3/4" (H) | (N),G,H,I,J,K,L,M,O,P,Q,T
DCDA | Ames | Colt 300BF | 3 | VU | 2005-10-04 | 2023-10-04 | N | 9 | (yyy) | N | Ames 2000BM3 3/4" (VU) | (N),G,H,I,J,K,L,M,O,P,Q,T
DCDA | Ames | Colt 300BF | 4 | H | 2005-10-04 | 2023-10-04 | N | 9 | (yyy) | N | Ames 2000BM3 3/4" (H) | (N),G,H,I,J,K,L,M,O,P,Q,T
DCDA | Ames | Colt 300BF | 4 | VU | 2005-10-04 | 2023-10-04 | N | 9 | (yyy) | N | Ames 2000BM3 3/4" (VU) | (N),G,H,I,J,K,L,M,O,P,Q,T
DCDA | Ames | Colt 300BF | 6 | H | 2007-03-02 | 2022-03-02 | N | 9 | (yyy) | N | Ames 2000BM3 3/4"(H) | (N),G,H,I,J,K,L,M,O,P,Q,T
DCDA | Ames | Colt 300BF | 6 | VU | 2007-03-02 | 2022-03-02 | N | 9 | (yyy) | N | Ames 2000BM3 3/4"(V) | (N),G,H,I,J,K,L,M,O,P,Q,T
DCDA | Ames | Colt 300BF | 8 | H | 2007-03-09 | 2022-03-09 | N | 9 | (yyy) | N | Ames 2000BM3 3/4" (H & VU) | (N),G,H,I,J,K,L,M,O,P,Q,T
DCDA | Ames | Colt 300BF | 8 | VU | 2007-03-09 | 2022-03-09 | N | 9 | (yyy) | N | Ames 2000BM3 3/4" (H & VU) | (N),G,H,I,J,K,L,M,O,P,Q,T
DCDA | Ames | Colt 300BF | 10 | H | 2009-09-17 | 2024-09-17 | N | 9 | (yyy) | N | Watts 007M3QT 3/4" (H), Ames 2000 BM3 (H) | (N),G,H,I,J,K,L,M,O,P,Q,T
DCDA | Ames | Colt 300BF | 10 | VU | 2009-09-17 | 2024-09-17 | N | 9 | (yyy) | N | Watts 007M3QT 3/4" (V), Ames 2000 BM3 (V) | (N),G,H,I,J,K,L,M,O,P,Q,T
DCDA | Ames | Colt 300GV | 2.5 | H | 2005-10-04 | 2023-10-04 | N | 9 | (zzz) | N | Ames 2000BM3 3/4" (H) | (N),G,H,I,J,K,L,M,O,P,Q,T
DCDA | Ames | Colt 300GV | 2.5 | VU | 2005-10-04 | 2023-10-04 | N | 9 | (zzz) | N | Ames 2000BM3 3/4" (VU) | (N),G,H,I,J,K,L,M,O,P,Q,T
DCDA | Ames | Colt 300GV | 3 | H | 2005-10-04 | 2023-10-04 | N | 9 | (zzz) | N | Ames 2000BM3 3/4" (H) | (N),G,H,I,J,K,L,M,O,P,Q,T
DCDA | Ames | Colt 300GV | 3 | VU | 2005-10-04 | 2023-10-04 | N | 9 | (zzz) | N | Ames 2000BM3 3/4" (VU) | (N),G,H,I,J,K,L,M,O,P,Q,T
DCDA | Ames | Colt 300GV | 4 | H | 2005-10-04 | 2023-10-04 | N | 9 | (zzz) | N | Ames 2000BM3 3/4" (H) | (N),G,H,I,J,K,L,M,O,P,Q,T
DCDA | Ames | Colt 300GV | 4 | VU | 2005-10-04 | 2023-10-04 | N | 9 | (zzz) | N | Ames 2000BM3 3/4" (VU) | (N),G,H,I,J,K,L,M,O,P,Q,T
DCDA | Ames | Colt 300GV | 6 | H | 2007-03-02 | 2022-03-02 | N | 9 | (zzz) | N | Ames 2000BM3 3/4"(H) | (N),G,H,I,J,K,L,M,O,P,Q,T
DCDA | Ames | Colt 300GV | 6 | VU | 2007-03-02 | 2022-03-02 | N | 9 | (zzz) | N | Ames 2000BM3 3/4"(V) | (N),G,H,I,J,K,L,M,O,P,Q,T
DCDA | Ames | Colt 300GV | 8 | H | 2007-03-09 | 2022-03-09 | N | 9 | (zzz) | N | Ames 2000BM3 3/4" (H & VU) | (N),G,H,I,J,K,L,M,O,P,Q,T
DCDA | Ames | Colt 300GV | 8 | VU | 2007-03-09 | 2022-03-09 | N | 9 | (zzz) | N | Ames 2000BM3 3/4" (H & VU) | (N),G,H,I,J,K,L,M,O,P,Q,T
DCDA | Ames | Colt 300GV | 10 | H | 2009-09-17 | 2024-09-17 | N | 9 | (zzz) | N | Watts 007M3QT 3/4" (H), Ames 2000 BM3 (H) | (N),G,H,I,J,K,L,M,O,P,Q,T
DCDA | Ames | Colt 300GV | 10 | VU | 2009-09-17 | 2024-09-17 | N | 9 | (zzz) | N | Watts 007M3QT 3/4" (V), Ames 2000 BM3 (V) | (N),G,H,I,J,K,L,M,O,P,Q,T
DCDA | Ames | Colt 300NBF | 2.5 | VUVD | 2009-04-07 | 2024-04-07 | N | 9 | (yyy) | N | Ames 2000BM3 3/4" (H) | (N),G,H,I,J,K,L,M,O,P,Q,T
DCDA | Ames | Colt 300NBF | 3 | VUVD | 2009-04-07 | 2024-04-07 | N | 9 | (yyy) | N | Ames 2000BM3 3/4" (H) | (N),G,H,I,J,K,L,M,O,P,Q,T
DCDA | Ames | Colt 300NBF | 4 | VUVD | 2009-04-07 | 2024-04-07 | N | 9 | (yyy) | N | Ames 2000BM3 3/4" (H) | (N),G,H,I,J,K,L,M,O,P,Q,T
DCDA | Ames | Colt 300NBF | 6 | VUVD | 2009-04-07 | 2024-04-07 | N | 9 | (yyy) | N | Ames 2000BM3 3/4" (H) | (N),G,H,I,J,K,L,M,O,P,Q,T
DCDA | Ames | Colt 300NBF | 8 | VUVD | 2013-01-03 | 2022-01-03 | N | 9 | (yyy) | N | Ames 2000BM3 3/4" (H) | (N),G,H,I,J,K,L,M,O,P,Q,T
DCDA | Ames | Colt 300NBF | 10 | VUVD | 2013-05-28 | 2022-05-28 | N | 9 | (yyy) | N | Ames 2000BM3 3/4" (H), Watts 007M3QT 3/4" (H) | (N), H,I,J,K,L,M,N,O,P,Q
DCDA | Ames | Colt 300NGV | 2.5 | VUVD | 2009-04-07 | 2024-04-07 | N | 9 | (zzz) | N | Ames 2000BM3 3/4" (H) | (N),G,H,I,J,K,L,M,O,P,Q,T
DCDA | Ames | Colt 300NGV | 3 | VUVD | 2009-04-07 | 2024-04-07 | N | 9 | (zzz) | N | Ames 2000BM3 3/4" (H) | (N),G,H,I,J,K,L,M,O,P,Q,T
DCDA | Ames | Colt 300NGV | 4 | VUVD | 2009-04-07 | 2024-04-07 | N | 9 | (zzz) | N | Ames 2000BM3 3/4" (H) | (N),G,H,I,J,K,L,M,O,P,Q,T
DCDA | Ames | Colt 300NGV | 6 | VUVD | 2009-04-07 | 2024-04-07 | N | 9 | (zzz) | N | Ames 2000BM3 3/4" (H) | (N),G,H,I,J,K,L,M,O,P,Q,T
DCDA | Ames | Colt 300NGV | 8 | VUVD | 2013-01-03 | 2022-01-03 | N | 9 | (zzz) | N | Ames 2000BM3 3/4" (H) | (N),G,H,I,J,K,L,M,O,P,Q,T
DCDA | Ames | Colt 300NGV | 10 | VUVD | 2013-05-28 | 2022-05-28 | N | 9 | (zzz) | N | Ames 2000BM3 3/4" (H), Watts 007M3QT 3/4" (H) | (N), H,I,J,K,L,M,N,O,P,Q
DCDA | Ames | DCDA | 4 | [9 empty] | model designation changed to 3000DCDA
DCDA | Ames | DCDA | 4 | [9 empty] | model designation changed to 3000GDCDA
DCDA | Ames | DCDA | 8 | [9 empty] | model designation changed to 3000DCDA
DCDA | Ames | DCDA | 8 | [9 empty] | model designation changed to 3000GDCDA
DCDA | Ames | DCDA | 10 | [9 empty] | model designation changed to 3000DCDC
DCDA | Ames | DCDA-I | 6 | [9 empty] | model designation changed to 3000DCDA
DCDA | Ames | DCDA-I | 6 | [9 empty] | model designation changed to 3000GDCDA
DCDA | Ames | DCDC | 4 | H | 1985-06-14 | 2024-06-14 | N | 6 | ee,ff,gg,hh,oo,pp,ccc,ddd,ffff,gggg | Y | Watts 709QT 3/4" (H) | (K),A,B,C,D,E,F,G,H,I,J,L,M,N,O,P,Q,T
DCDA | Ames | DCDC | 6 | H | 1985-06-14 | 2024-06-14 | N | 6 | ee,ff,gg,hh,oo,pp,ccc,ddd,ffff,gggg | Y | Watts 709QT 3/4" (H) | (K),A,B,C,D,E,F,G,H,I,J,L,M,N,O,P,Q,T
DCDA | Ames | DCDC | 8 | H | 1987-08-04 | 2023-08-04 | N | 7 | ee,ff,gg,hh,oo,pp,ccc,ddd,ffff,gggg | Y | Watts 709QT 3/4" (H) | (K),A,B,C,D,E,F,G,H,I,J,L,M,N,O,P,Q,T
DCDA | Ames | DCDC | 10 | [9 empty] | model designation changed to 3000GDCDC
DCDA | Ames | LFColt 300BF | 2.5 | H | 2014-01-08 | 2023-01-08 | Y | 9 | (yyy) | N | Watts LF007M3QT 3/4" (H), Ames LF2000BM3 3/4" (H) | (O) | Lead free compliant version identified with NSF61 mark on meter
DCDA | Ames | LFColt 300BF | 2.5 | VU | 2014-01-08 | 2023-01-08 | Y | 9 | (yyy) | N | Watts LF007M3QT 3/4" (VU), Ames LF2000BM3 3/4" (VU) | (O) | Lead free compliant version identified with NSF61 mark on meter
DCDA | Ames | LFColt 300BF | 3 | H | 2014-01-08 | 2023-01-08 | Y | 9 | (yyy) | N | Watts LF007M3QT 3/4" (H), Ames LF2000BM3 3/4" (H) | (O) | Lead free compliant version identified with NSF61 mark on meter
DCDA | Ames | LFColt 300BF | 3 | VU | 2014-01-08 | 2023-01-08 | Y | 9 | (yyy) | N | Watts LF007M3QT 3/4" (VU), Ames LF2000BM3 3/4" (VU) | (O) | Lead free compliant version identified with NSF61 mark on meter
DCDA | Ames | LFColt 300BF | 4 | H | 2014-01-08 | 2023-01-08 | Y | 9 | (yyy) | N | Watts LF007M3QT 3/4" (H), Ames LF2000BM3 3/4" (H) | (O) | Lead free compliant version identified with NSF61 mark on meter
DCDA | Ames | LFColt 300BF | 4 | VU | 2014-01-08 | 2023-01-08 | Y | 9 | (yyy) | N | Watts LF007M3QT 3/4" (VU), Ames LF2000BM3 3/4" (VU) | (O) | Lead free compliant version identified with NSF61 mark on meter
DCDA | Ames | LFColt 300BF | 6 | H | 2014-01-08 | 2023-01-08 | Y | 9 | (yyy) | N | Watts LF007M3QT 3/4" (H), Ames LF2000BM3 3/4" (H) | (O) | Lead free compliant version identified with NSF61 mark on meter
DCDA | Ames | LFColt 300BF | 6 | VU | 2014-01-08 | 2023-01-08 | Y | 9 | (yyy) | N | Watts LF007M3QT 3/4" (VU), Ames LF2000BM3 3/4" (VU) | (O) | Lead free compliant version identified with NSF61 mark on meter
DCDA | Ames | LFColt 300BF | 8 | H | 2014-01-08 | 2023-01-08 | Y | 9 | (yyy) | N | Watts LF007M3QT 3/4" (H), Ames LF2000BM3 3/4" (H) | (O) | Lead free compliant version identified with NSF61 mark on meter
DCDA | Ames | LFColt 300BF | 8 | VU | 2014-01-08 | 2023-01-08 | Y | 9 | (yyy) | N | Watts LF007M3QT 3/4" (VU), Ames LF2000BM3 3/4" (VU) | (O) | Lead free compliant version identified with NSF61 mark on meter
DCDA | Ames | LFColt 300BF | 10 | H | 2014-01-08 | 2023-01-08 | Y | 9 | (yyy) | N | Watts LF007M3QT 3/4" (H), Ames LF2000BM3 3/4" (H) | (O) | Lead free compliant version identified with NSF61 mark on meter
DCDA | Ames | LFColt 300BF | 10 | VU | 2014-01-08 | 2023-01-08 | Y | 9 | (yyy) | N | Watts LF007M3QT 3/4" (VU), Ames LF2000BM3 3/4" (VU) | (O) | Lead free compliant version identified with NSF61 mark on meter
DCDA | Ames | LFColt 300GV | 2.5 | H | 2014-01-08 | 2023-01-08 | Y | 9 | (zzz) | N | Watts LF007M3QT 3/4" (H), Ames LF2000BM3 3/4" (H) | (O) | Lead free compliant version identified with NSF61 mark on meter
DCDA | Ames | LFColt 300GV | 2.5 | VU | 2014-01-08 | 2023-01-08 | Y | 9 | (zzz) | N | Watts LF007M3QT 3/4" (VU), Ames LF2000BM3 3/4" (VU) | (O) | Lead free compliant version identified with NSF61 mark on meter
DCDA | Ames | LFColt 300GV | 3 | H | 2014-01-08 | 2023-01-08 | Y | 9 | (zzz) | N | Watts LF007M3QT 3/4" (H), Ames LF2000BM3 3/4" (H) | (O) | Lead free compliant version identified with NSF61 mark on meter
DCDA | Ames | LFColt 300GV | 3 | VU | 2014-01-08 | 2023-01-08 | Y | 9 | (zzz) | N | Watts LF007M3QT 3/4" (VU), Ames LF2000BM3 3/4" (VU) | (O) | Lead free compliant version identified with NSF61 mark on meter
DCDA | Ames | LFColt 300GV | 4 | H | 2014-01-08 | 2023-01-08 | Y | 9 | (zzz) | N | Watts LF007M3QT 3/4" (H), Ames LF2000BM3 3/4" (H) | (O) | Lead free compliant version identified with NSF61 mark on meter
DCDA | Ames | LFColt 300GV | 4 | VU | 2014-01-08 | 2023-01-08 | Y | 9 | (zzz) | N | Watts LF007M3QT 3/4" (VU), Ames LF2000BM3 3/4" (VU) | (O) | Lead free compliant version identified with NSF61 mark on meter
DCDA | Ames | LFColt 300GV | 6 | H | 2014-01-08 | 2023-01-08 | Y | 9 | (zzz) | N | Watts LF007M3QT 3/4" (H), Ames LF2000BM3 3/4" (H) | (O) | Lead free compliant version identified with NSF61 mark on meter
DCDA | Ames | LFColt 300GV | 6 | VU | 2014-01-08 | 2023-01-08 | Y | 9 | (zzz) | N | Watts LF007M3QT 3/4" (VU), Ames LF2000BM3 3/4" (VU) | (O) | Lead free compliant version identified with NSF61 mark on meter
DCDA | Ames | LFColt 300GV | 8 | H | 2014-01-08 | 2023-01-08 | Y | 9 | (zzz) | N | Watts LF007M3QT 3/4" (H), Ames LF2000BM3 3/4" (H) | (O) | Lead free compliant version identified with NSF61 mark on meter
DCDA | Ames | LFColt 300GV | 8 | VU | 2014-01-08 | 2023-01-08 | Y | 9 | (zzz) | N | Watts LF007M3QT 3/4" (VU), Ames LF2000BM3 3/4" (VU) | (O) | Lead free compliant version identified with NSF61 mark on meter
DCDA | Ames | LFColt 300GV | 10 | H | 2014-01-08 | 2023-01-08 | Y | 9 | (zzz) | N | Watts LF007M3QT 3/4" (H), Ames LF2000BM3 3/4" (H) | (O) | Lead free compliant version identified with NSF61 mark on meter
DCDA | Ames | LFColt 300GV | 10 | VU | 2014-01-08 | 2023-01-08 | Y | 9 | (zzz) | N | Watts LF007M3QT 3/4" (VU), Ames LF2000BM3 3/4" (VU) | (O) | Lead free compliant version identified with NSF61 mark on meter
DCDA | Ames | LFColt 300NBF | 2.5 | VUVD | 2014-01-08 | 2023-01-08 | Y | 9 | (yyy) | N | Watts LF007M3QT 3/4" (H), Ames LF2000BM3 3/4" (H) | (O) | Lead free compliant version identified with NSF61 mark on meter
DCDA | Ames | LFColt 300NBF | 3 | VUVD | 2014-01-08 | 2023-01-08 | Y | 9 | (yyy) | N | Watts LF007M3QT 3/4" (H), Ames LF2000BM3 3/4" (H) | (O) | Lead free compliant version identified with NSF61 mark on meter
DCDA | Ames | LFColt 300NBF | 4 | VUVD | 2014-01-08 | 2023-01-08 | Y | 9 | (yyy) | N | Watts LF007M3QT 3/4" (H), Ames LF2000BM3 3/4" (H) | (O) | Lead free compliant version identified with NSF61 mark on meter
DCDA | Ames | LFColt 300NBF | 6 | VUVD | 2014-01-08 | 2023-01-08 | Y | 9 | (yyy) | N | Watts LF007M3QT 3/4" (H), Ames LF2000BM3 3/4" (H) | (O) | Lead free compliant version identified with NSF61 mark on meter
DCDA | Ames | LFColt 300NBF | 8 | VUVD | 2014-01-08 | 2023-01-08 | Y | 9 | (yyy) | N | Watts LF007M3QT 3/4" (H), Ames LF2000BM3 3/4" (H) | (O) | Lead free compliant version identified with NSF61 mark on meter
DCDA | Ames | LFColt 300NBF | 10 | VUVD | 2014-01-08 | 2023-01-08 | Y | 9 | (yyy) | N | Watts LF007M3QT 3/4" (H), Ames LF2000BM3 3/4" (H) | (O) | Lead free compliant version identified with NSF61 mark on meter
DCDA | Ames | LFColt 300NGV | 2.5 | VUVD | 2014-01-08 | 2023-01-08 | Y | 9 | (zzz) | N | Watts LF007M3QT 3/4" (H), Ames LF2000BM3 3/4" (H) | (O) | Lead free compliant version identified with NSF61 mark on meter
DCDA | Ames | LFColt 300NGV | 3 | VUVD | 2014-01-08 | 2023-01-08 | Y | 9 | (zzz) | N | Watts LF007M3QT 3/4" (H), Ames LF2000BM3 3/4" (H) | (O) | Lead free compliant version identified with NSF61 mark on meter
DCDA | Ames | LFColt 300NGV | 4 | VUVD | 2014-01-08 | 2023-01-08 | Y | 9 | (zzz) | N | Watts LF007M3QT 3/4" (H), Ames LF2000BM3 3/4" (H) | (O) | Lead free compliant version identified with NSF61 mark on meter
DCDA | Ames | LFColt 300NGV | 6 | VUVD | 2014-01-08 | 2023-01-08 | Y | 9 | (zzz) | N | Watts LF007M3QT 3/4" (H), Ames LF2000BM3 3/4" (H) | (O) | Lead free compliant version identified with NSF61 mark on meter
DCDA | Ames | LFColt 300NGV | 8 | VUVD | 2014-01-08 | 2023-01-08 | Y | 9 | (zzz) | N | Watts LF007M3QT 3/4" (H), Ames LF2000BM3 3/4" (H) | (O) | Lead free compliant version identified with NSF61 mark on meter
DCDA | Ames | LFColt 300NGV | 10 | VUVD | 2014-01-08 | 2023-01-08 | Y | 9 | (zzz) | N | Watts LF007M3QT 3/4" (H), Ames LF2000BM3 3/4" (H) | (O) | Lead free compliant version identified with NSF61 mark on meter
DCDA | Ames | LFMaxim 300BF | 2.5 | H | 2014-01-08 | 2023-01-08 | Y | 9 | (yyy) | N | Watts LF007M3QT 3/4" (H), Ames LF2000BM3 3/4" (H) | (O) | Lead free compliant version identified with NSF61 mark on meter
DCDA | Ames | LFMaxim 300BF | 2.5 | VU | 2014-01-08 | 2023-01-08 | Y | 9 | (yyy) | N | Watts LF007M3QT 3/4" (VU), Ames LF2000BM3 3/4" (VU) | (O) | Lead free compliant version identified with NSF61 mark on meter
DCDA | Ames | LFMaxim 300BF | 3 | H | 2014-01-08 | 2023-01-08 | Y | 9 | (yyy) | N | Watts LF007M3QT 3/4" (H), Ames LF2000BM3 3/4" (H) | (O) | Lead free compliant version identified with NSF61 mark on meter
DCDA | Ames | LFMaxim 300BF | 3 | VU | 2014-01-08 | 2023-01-08 | Y | 9 | (yyy) | N | Watts LF007M3QT 3/4" (VU), Ames LF2000BM3 3/4" (VU) | (O) | Lead free compliant version identified with NSF61 mark on meter
DCDA | Ames | LFMaxim 300BF | 4 | H | 2014-01-08 | 2023-01-08 | Y | 9 | (yyy) | N | Watts LF007M3QT 3/4" (H), Ames LF2000BM3 3/4" (H) | (O) | Lead free compliant version identified with NSF61 mark on meter
DCDA | Ames | LFMaxim 300BF | 4 | VU | 2014-01-08 | 2023-01-08 | Y | 9 | (yyy) | N | Watts LF007M3QT 3/4" (VU), Ames LF2000BM3 3/4" (VU) | (O) | Lead free compliant version identified with NSF61 mark on meter
DCDA | Ames | LFMaxim 300BF | 6 | H | 2014-01-08 | 2023-01-08 | Y | 9 | (yyy) | N | Watts LF007M3QT 3/4" (H), Ames LF2000BM3 3/4" (H) | (O) | Lead free compliant version identified with NSF61 mark on meter
DCDA | Ames | LFMaxim 300BF | 6 | VU | 2014-01-08 | 2023-01-08 | Y | 9 | (yyy) | N | Watts LF007M3QT 3/4" (VU), Ames LF2000BM3 3/4" (VU) | (O) | Lead free compliant version identified with NSF61 mark on meter
DCDA | Ames | LFMaxim 300BF | 8 | H | 2014-01-08 | 2023-01-08 | Y | 9 | (yyy) | N | Watts LF007M3QT 3/4" (H), Ames LF2000BM3 3/4" (H) | (O) | Lead free compliant version identified with NSF61 mark on meter
DCDA | Ames | LFMaxim 300BF | 8 | VU | 2014-01-08 | 2023-01-08 | Y | 9 | (yyy) | N | Watts LF007M3QT 3/4" (VU), Ames LF2000BM3 3/4" (VU) | (O) | Lead free compliant version identified with NSF61 mark on meter
DCDA | Ames | LFMaxim 300BF | 10 | H | 2014-01-08 | 2023-01-08 | Y | 9 | (yyy) | N | Watts LF007M3QT 3/4" (H), Ames LF2000BM3 3/4" (H) | (O) | Lead free compliant version identified with NSF61 mark on meter
DCDA | Ames | LFMaxim 300BF | 10 | VU | 2014-01-08 | 2023-01-08 | Y | 9 | (yyy) | N | Watts LF007M3QT 3/4" (VU), Ames LF2000BM3 3/4" (VU) | (O) | Lead free compliant version identified with NSF61 mark on meter
DCDA | Ames | LFMaxim 300GV | 2.5 | H | 2014-01-08 | 2023-01-08 | Y | 9 | (zzz) | N | Watts LF007M3QT 3/4" (H), Ames LF2000BM3 3/4" (H) | (O) | Lead free compliant version identified with NSF61 mark on meter
DCDA | Ames | LFMaxim 300GV | 2.5 | VU | 2014-01-08 | 2023-01-08 | Y | 9 | (zzz) | N | Watts LF007M3QT 3/4" (VU), Ames LF2000BM3 3/4" (VU) | (O) | Lead free compliant version identified with NSF61 mark on meter
DCDA | Ames | LFMaxim 300GV | 3 | H | 2014-01-08 | 2023-01-08 | Y | 9 | (zzz) | N | Watts LF007M3QT 3/4" (H), Ames LF2000BM3 3/4" (H) | (O) | Lead free compliant version identified with NSF61 mark on meter
DCDA | Ames | LFMaxim 300GV | 3 | VU | 2014-01-08 | 2023-01-08 | Y | 9 | (zzz) | N | Watts LF007M3QT 3/4" (VU), Ames LF2000BM3 3/4" (VU) | (O) | Lead free compliant version identified with NSF61 mark on meter
DCDA | Ames | LFMaxim 300GV | 4 | H | 2014-01-08 | 2023-01-08 | Y | 9 | (zzz) | N | Watts LF007M3QT 3/4" (H), Ames LF2000BM3 3/4" (H) | (O) | Lead free compliant version identified with NSF61 mark on meter
DCDA | Ames | LFMaxim 300GV | 4 | VU | 2014-01-08 | 2023-01-08 | Y | 9 | (zzz) | N | Watts LF007M3QT 3/4" (VU), Ames LF2000BM3 3/4" (VU) | (O) | Lead free compliant version identified with NSF61 mark on meter
DCDA | Ames | LFMaxim 300GV | 6 | H | 2014-01-08 | 2023-01-08 | Y | 9 | (zzz) | N | Watts LF007M3QT 3/4" (H), Ames LF2000BM3 3/4" (H) | (O) | Lead free compliant version identified with NSF61 mark on meter
DCDA | Ames | LFMaxim 300GV | 6 | VU | 2014-01-08 | 2023-01-08 | Y | 9 | (zzz) | N | Watts LF007M3QT 3/4" (VU), Ames LF2000BM3 3/4" (VU) | (O) | Lead free compliant version identified with NSF61 mark on meter
DCDA | Ames | LFMaxim 300GV | 8 | H | 2014-01-08 | 2023-01-08 | Y | 9 | (zzz) | N | Watts LF007M3QT 3/4" (H), Ames LF2000BM3 3/4" (H) | (O) | Lead free compliant version identified with NSF61 mark on meter
DCDA | Ames | LFMaxim 300GV | 8 | VU | 2014-01-08 | 2023-01-08 | Y | 9 | (zzz) | N | Watts LF007M3QT 3/4" (VU), Ames LF2000BM3 3/4" (VU) | (O) | Lead free compliant version identified with NSF61 mark on meter
DCDA | Ames | LFMaxim 300GV | 10 | H | 2014-01-08 | 2023-01-08 | Y | 9 | (zzz) | N | Watts LF007M3QT 3/4" (H), Ames LF2000BM3 3/4" (H) | (O) | Lead free compliant version identified with NSF61 mark on meter
DCDA | Ames | LFMaxim 300GV | 10 | VU | 2014-01-08 | 2023-01-08 | Y | 9 | (zzz) | N | Watts LF007M3QT 3/4" (VU), Ames LF2000BM3 3/4" (VU) | (O) | Lead free compliant version identified with NSF61 mark on meter
DCDA | Ames | LFMaxim 300NBF | 2.5 | VUVD | 2014-01-08 | 2023-01-08 | Y | 9 | (yyy) | N | Watts LF007M3QT 3/4" (H), Ames LF2000BM3 3/4" (H) | (O) | Lead free compliant version identified with NSF61 mark on meter
DCDA | Ames | LFMaxim 300NBF | 3 | VUVD | 2014-01-08 | 2023-01-08 | Y | 9 | (yyy) | N | Watts LF007M3QT 3/4" (H), Ames LF2000BM3 3/4" (H) | (O) | Lead free compliant version identified with NSF61 mark on meter
DCDA | Ames | LFMaxim 300NBF | 4 | VUVD | 2014-01-08 | 2023-01-08 | Y | 9 | (yyy) | N | Watts LF007M3QT 3/4" (H), Ames LF2000BM3 3/4" (H) | (O) | Lead free compliant version identified with NSF61 mark on meter
DCDA | Ames | LFMaxim 300NBF | 6 | VUVD | 2014-01-08 | 2023-01-08 | Y | 9 | (yyy) | N | Watts LF007M3QT 3/4" (H), Ames LF2000BM3 3/4" (H) | (O) | Lead free compliant version identified with NSF61 mark on meter
DCDA | Ames | LFMaxim 300NBF | 8 | VUVD | 2014-01-08 | 2023-01-08 | Y | 9 | (yyy) | N | Watts LF007M3QT 3/4" (H), Ames LF2000BM3 3/4" (H) | (O) | Lead free compliant version identified with NSF61 mark on meter
DCDA | Ames | LFMaxim 300NBF | 10 | VUVD | 2014-01-08 | 2023-01-08 | Y | 9 | (yyy) | N | Watts LF007M3QT 3/4" (H), Ames LF2000BM3 3/4" (H) | (O) | Lead free compliant version identified with NSF61 mark on meter
DCDA | Ames | LFMaxim 300NGV | 2.5 | VUVD | 2014-01-08 | 2023-01-08 | Y | 9 | (zzz) | N | Watts LF007M3QT 3/4" (H), Ames LF2000BM3 3/4" (H) | (O) | Lead free compliant version identified with NSF61 mark on meter
DCDA | Ames | LFMaxim 300NGV | 3 | VUVD | 2014-01-08 | 2023-01-08 | Y | 9 | (zzz) | N | Watts LF007M3QT 3/4" (H), Ames LF2000BM3 3/4" (H) | (O) | Lead free compliant version identified with NSF61 mark on meter
DCDA | Ames | LFMaxim 300NGV | 4 | VUVD | 2014-01-08 | 2023-01-08 | Y | 9 | (zzz) | N | Watts LF007M3QT 3/4" (H), Ames LF2000BM3 3/4" (H) | (O) | Lead free compliant version identified with NSF61 mark on meter
DCDA | Ames | LFMaxim 300NGV | 6 | VUVD | 2014-01-08 | 2023-01-08 | Y | 9 | (zzz) | N | Watts LF007M3QT 3/4" (H), Ames LF2000BM3 3/4" (H) | (O) | Lead free compliant version identified with NSF61 mark on meter
DCDA | Ames | LFMaxim 300NGV | 8 | VUVD | 2014-01-08 | 2023-01-08 | Y | 9 | (zzz) | N | Watts LF007M3QT 3/4" (H), Ames LF2000BM3 3/4" (H) | (O) | Lead free compliant version identified with NSF61 mark on meter
DCDA | Ames | LFMaxim 300NGV | 10 | VUVD | 2014-01-08 | 2023-01-08 | Y | 9 | (zzz) | N | Watts LF007M3QT 3/4" (H), Ames LF2000BM3 3/4" (H) | (O) | Lead free compliant version identified with NSF61 mark on meter
DCDA | Ames | Maxim 300aBF | 2.5 | H | 2003-11-06 | 2024-11-06 | N | 9 | (yyy) | Y | Ames 2000BM3 3/4" (H) | (N),G,H,I,J,K,L,M,O,P,Q,T
DCDA | Ames | Maxim 300aBF | 2.5 | VU | 2003-11-06 | 2024-11-06 | N | 9 | (yyy) | Y | Ames 2000BM3 3/4" (VU) | (N),G,H,I,J,K,L,M,O,P,Q,T
DCDA | Ames | Maxim 300aBF | 3 | H | 2003-10-06 | 2024-10-06 | N | 9 | (yyy) | Y | Ames 2000BM3 3/4" (H) | (N),G,H,I,J,K,L,M,O,P,Q,T
DCDA | Ames | Maxim 300aBF | 3 | VU | 2003-10-06 | 2024-10-06 | N | 9 | (yyy) | Y | Ames 2000BM3 3/4" (VU) | (N),G,H,I,J,K,L,M,O,P,Q,T
DCDA | Ames | Maxim 300aBF | 4 | H | 2004-11-03 | 2022-11-03 | N | 9 | (yyy) | Y | Ames 2000BM3 3/4 (H) | (N),G,H,I,J,K,L,M,O,P,Q,T
DCDA | Ames | Maxim 300aBF | 4 | VU | 2005-01-18 | 2023-01-18 | N | 9 | (yyy) | Y | Ames 2000BM3 3/4" (VU) | (N),G,H,I,J,K,L,M,O,P,Q,T
DCDA | Ames | Maxim 300aGV | 2.5 | H | 2003-10-06 | 2024-10-06 | N | 9 | (zzz) | Y | Ames 2000BM3 3/4" (H) | (N),G,H,I,J,K,L,M,O,P,Q,T
DCDA | Ames | Maxim 300aGV | 2.5 | VU | 2003-10-06 | 2024-10-06 | N | 9 | (zzz) | Y | Ames 2000BM3 3/4" (VU) | (N),G,H,I,J,K,L,M,O,P,Q,T
DCDA | Ames | Maxim 300aGV | 3 | H | 2003-10-06 | 2024-10-06 | N | 9 | (zzz) | Y | Ames 2000BM3 3/4" (H) | (N),G,H,I,J,K,L,M,O,P,Q,T
DCDA | Ames | Maxim 300aGV | 3 | VU | 2003-10-06 | 2024-10-06 | N | 9 | (zzz) | Y | Ames 2000BM3 3/4" (VU) | (N),G,H,I,J,K,L,M,O,P,Q,T
DCDA | Ames | Maxim 300aGV | 4 | H | 2004-11-03 | 2022-11-03 | N | 9 | (zzz) | Y | Ames 2000BM3 3/4 (H) | (N),G,H,I,J,K,L,M,O,P,Q,T
DCDA | Ames | Maxim 300aGV | 4 | VU | 2005-01-18 | 2023-01-18 | N | 9 | (zzz) | Y | Ames 2000BM3 3/4" (VU) | (N),G,H,I,J,K,L,M,O,P,Q,T
DCDA | Ames | Maxim 300BF | 2.5 | H | 2005-10-04 | 2023-10-04 | N | 9 | (yyy) | N | Ames 2000BM3 3/4" (H) | (N),G,H,I,J,K,L,M,O,P,Q,T
DCDA | Ames | Maxim 300BF | 2.5 | VU | 2005-10-04 | 2023-10-04 | N | 9 | (yyy) | N | Ames 2000BM3 3/4" (VU) | (N),G,H,I,J,K,L,M,O,P,Q,T
DCDA | Ames | Maxim 300BF | 3 | H | 2005-10-04 | 2023-10-04 | N | 9 | (yyy) | N | Ames 2000BM3 3/4" (H) | (N),G,H,I,J,K,L,M,O,P,Q,T
DCDA | Ames | Maxim 300BF | 3 | VU | 2005-10-04 | 2023-10-04 | N | 9 | (yyy) | N | Ames 2000BM3 3/4" (VU) | (N),G,H,I,J,K,L,M,O,P,Q,T
DCDA | Ames | Maxim 300BF | 4 | H | 2007-03-02 | 2022-03-02 | N | 9 | (yyy) | N | Ames 2000BM3 3/4"(H) | (N),G,H,I,J,K,L,M,O,P,Q,T
DCDA | Ames | Maxim 300BF | 4 | Vu | 2007-03-02 | 2022-03-02 | N | 9 | (yyy) | N | Ames 2000BM3 3/4"(V) | (N),G,H,I,J,K,L,M,O,P,Q,T
DCDA | Ames | Maxim 300BF | 6 | H | 2007-03-09 | 2022-03-09 | N | 9 | (yyy) | N | Ames 2000BM3 3/4" (H & VU) | (N),G,H,I,J,K,L,M,O,P,Q,T
DCDA | Ames | Maxim 300BF | 6 | VU | 2007-03-09 | 2022-03-09 | N | 9 | (yyy) | N | Ames 2000BM3 3/4" (H & VU) | (N),G,H,I,J,K,L,M,O,P,Q,T
DCDA | Ames | Maxim 300BF | 8 | H | 2009-09-17 | 2024-09-17 | N | 9 | (yyy) | N | Watts 007M3QT 3/4" (H), Ames 2000 BM3 (H) | (N),G,H,I,J,K,L,M,O,P,Q,T
DCDA | Ames | Maxim 300BF | 8 | VU | 2009-09-17 | 2024-09-17 | N | 9 | (yyy) | N | Watts 007M3QT 3/4" (V), Ames 2000 BM3 (V) | (N),G,H,I,J,K,L,M,O,P,Q,T
DCDA | Ames | Maxim 300BF | 10 | H | 2009-09-17 | 2024-09-17 | N | 9 | (yyy) | N | Watts 007M3QT 3/4" (H), Ames 2000 BM3 (H) | (N),G,H,I,J,K,L,M,O,P,Q,T
DCDA | Ames | Maxim 300BF | 10 | VU | 2009-09-17 | 2024-09-17 | N | 9 | (yyy) | N | Watts 007M3QT 3/4" (V), Ames 2000 BM3 (V) | (N),G,H,I,J,K,L,M,O,P,Q,T
DCDA | Ames | Maxim 300GV | 2.5 | H | 2005-10-04 | 2023-10-04 | N | 9 | (zzz) | N | Ames 2000BM3 3/4" (H) | (N),G,H,I,J,K,L,M,O,P,Q,T
DCDA | Ames | Maxim 300GV | 2.5 | VU | 2005-10-04 | 2023-10-04 | N | 9 | (zzz) | N | Ames 2000BM3 3/4" (VU) | (N),G,H,I,J,K,L,M,O,P,Q,T
DCDA | Ames | Maxim 300GV | 3 | H | 2005-10-04 | 2023-10-04 | N | 9 | (zzz) | N | Ames 2000BM3 3/4" (H) | (N),G,H,I,J,K,L,M,O,P,Q,T
DCDA | Ames | Maxim 300GV | 3 | VU | 2005-10-04 | 2023-10-04 | N | 9 | (zzz) | N | Ames 2000BM3 3/4" (VU) | (N),G,H,I,J,K,L,M,O,P,Q,T
DCDA | Ames | Maxim 300GV | 4 | H | 2007-03-02 | 2022-03-02 | N | 9 | (zzz) | N | Ames 2000BM3 3/4"(H) | (N),G,H,I,J,K,L,M,O,P,Q,T
DCDA | Ames | Maxim 300GV | 4 | VU | 2007-03-02 | 2022-03-02 | N | 9 | (zzz) | N | Ames 2000BM3 3/4"(V) | (N),G,H,I,J,K,L,M,O,P,Q,T
DCDA | Ames | Maxim 300GV | 6 | H | 2007-03-09 | 2022-03-09 | N | 9 | (zzz) | N | Ames 2000BM3 3/4" (H & VU) | (N),G,H,I,J,K,L,M,O,P,Q,T
DCDA | Ames | Maxim 300GV | 6 | VU | 2007-03-09 | 2022-03-09 | N | 9 | (zzz) | N | Ames 2000BM3 3/4" (H & VU) | (N),G,H,I,J,K,L,M,O,P,Q,T
DCDA | Ames | Maxim 300GV | 8 | H | 2009-09-17 | 2024-09-17 | N | 9 | (zzz) | N | Watts 007M3QT 3/4" (H), Ames 2000 BM3 (H) | (N),G,H,I,J,K,L,M,O,P,Q,T
DCDA | Ames | Maxim 300GV | 8 | VU | 2009-09-17 | 2024-09-17 | N | 9 | (zzz) | N | Watts 007M3QT 3/4" (V), Ames 2000 BM3 (V) | (N),G,H,I,J,K,L,M,O,P,Q,T
DCDA | Ames | Maxim 300GV | 10 | H | 2009-09-17 | 2024-09-17 | N | 9 | (zzz) | N | Watts 007M3QT 3/4" (H), Ames 2000 BM3 (H) | (N),G,H,I,J,K,L,M,O,P,Q,T
DCDA | Ames | Maxim 300GV | 10 | VU | 2009-09-17 | 2024-09-17 | N | 9 | (zzz) | N | Watts 007M3QT 3/4" (V), Ames 2000 BM3 (V) | (N),G,H,I,J,K,L,M,O,P,Q,T
DCDA | Ames | Maxim 300NBF | 2.5 | VUVD | 2009-04-07 | 2024-04-07 | N | 9 | (yyy) | N | Ames 2000BM3 3/4" (H) | (N),G,H,I,J,K,L,M,O,P,Q,T
DCDA | Ames | Maxim 300NBF | 3 | VUVD | 2009-04-07 | 2024-04-07 | N | 9 | (yyy) | N | Ames 2000BM3 3/4" (H) | (N),G,H,I,J,K,L,M,O,P,Q,T
DCDA | Ames | Maxim 300NBF | 4 | VUVD | 2009-04-07 | 2024-04-07 | N | 9 | (yyy) | N | Ames 2000BM3 3/4" (H) | (N),G,H,I,J,K,L,M,O,P,Q,T
DCDA | Ames | Maxim 300NBF | 6 | VUVD | 2013-01-03 | 2022-01-03 | N | 9 | (yyy) | N | Ames 2000BM3 3/4" (H) | (N),G,H,I,J,K,L,M,O,P,Q,T
DCDA | Ames | Maxim 300NBF | 8 | VUVD | 2013-05-28 | 2022-05-28 | N | 9 | (yyy) | N | Ames 2000BM3 3/4" (H), Watts 007M3QT 3/4" (H) | (N), H,I,J,K,L,M,N,O,P,Q
DCDA | Ames | Maxim 300NBF | 10 | VUVD | 2013-05-28 | 2022-05-28 | N | 9 | (yyy) | N | Ames 2000BM3 3/4" (H), Watts 007M3QT 3/4" (H) | (N), H,I,J,K,L,M,N,O,P,Q
DCDA | Ames | Maxim 300NGV | 2.5 | VUVD | 2009-04-07 | 2024-04-07 | N | 9 | (zzz) | N | Ames 2000BM3 3/4" (H) | (N),G,H,I,J,K,L,M,N,O,P,Q,T
DCDA | Ames | Maxim 300NGV | 3 | VUVD | 2009-04-07 | 2024-04-07 | N | 9 | (zzz) | N | Ames 2000BM3 3/4" (H) | (N),G,H,I,J,K,L,M,N,O,P,Q,T
DCDA | Ames | Maxim 300NGV | 4 | VUVD | 2009-04-07 | 2024-04-07 | N | 9 | (zzz) | N | Ames 2000BM3 3/4" (H) | (N),G,H,I,J,K,L,M,N,O,P,Q,T
DCDA | Ames | Maxim 300NGV | 6 | VUVD | 2013-01-03 | 2022-01-03 | N | 9 | (zzz) | N | Ames 2000BM3 3/4" (H) | (N),G,H,I,J,K,L,M,N,O,P,Q,T
DCDA | Ames | Maxim 300NGV | 8 | VUVD | 2013-05-28 | 2022-05-28 | N | 9 | (zzz) | N | Ames 2000BM3 3/4" (H), Watts 007M3QT 3/4" (H) | (N), H,I,J,K,L,M,N,O,P,Q
DCDA | Ames | Maxim 300NGV | 10 | VUVD | 2013-05-28 | 2022-05-28 | N | 9 | (zzz) | N | Ames 2000BM3 3/4" (H), Watts 007M3QT 3/4" (H) | (N), H,I,J,K,L,M,N,O,P,Q
DCDA | Apollo/Conbraco | 4060003 | 3 | [9 empty] | model designation changed to 40600000
DCDA | Apollo/Conbraco | 4060003 | 3 | [9 empty] | model designation changed to 40600C3
DCDA | Apollo/Conbraco | 40600000 | 3 | H | 1996-08-20 | 2023-08-20 | N | 8 | uu,cc,mm | Y | Apollo/Conbraco 4010402 3/4" (H) | (M),A,B,C,D,E,F,G,H,I,J,K,L,N,O,P,Q,T | formerly 4060003
DCDA | Apollo/Conbraco | 10DCDA | 10 | [9 empty] | model designation changed to DCDA4S
DCDA | Apollo/Conbraco | 10DCDA | 10 | [9 empty] | model designation changed to DCDA4S
DCDA | Apollo/Conbraco | 2 1/2DCDA | 2.5 | H | 2000-10-16 | 2024-10-16 | N | 9 | (ll),mm | Y | Apollo/Conbraco 1/2DC 1/2" (H), Apollo/Conbraco W432100 1/2" (H) | (M),E,F,G,H,I,J,K,L,N,O,P,Q,T
DCDA | Apollo/Conbraco | 2 1/2DCDA | 2.5 | VU | 2000-10-16 | 2024-10-16 | N | 9 | (ll),mm | Y | Apollo/Conbraco 1/2DC 1/2" (VU), Apollo/Conbraco W432100 1/2" (VU) | (M),E,F,G,H,I,J,K,L,N,O,P,Q,T
DCDA | Apollo/Conbraco | 2 1/2DCDA6 | 2.5 | H | 2001-04-10 | 2022-04-10 | N | 9 | (mm)[#1SOV],(nnn)[#2SOV] | Y | Apollo/Conbraco 1/2DC 1/2" (H), Apollo/Conbraco W432100 1/2" (H) | (M),E,F,G,H,I,J,K,L,N,O,P,Q,T
DCDA | Apollo/Conbraco | 2 1/2DCDA6 | 2.5 | VU | 2001-04-10 | 2022-04-10 | N | 9 | (mm)[#1SOV],(nnn)[#2SOV] | Y | Apollo/Conbraco 1/2DC 1/2" (VU), Apollo/Conbraco W432100 1/2" (VU) | (M),E,F,G,H,I,J,K,L,N,O,P,Q,T
DCDA | Apollo/Conbraco | 2 1/2DCDA7 | 2.5 | H | 2004-09-29 | 2022-09-29 | N | 9 | (mm)[#1SOV], (qqq)[#2SOV] | Y | Apollo/Conbraco 1/2DC 1/2" (H), Apollo/Conbraco W432100 1/2" (H) | (M),E,F,G,H,I,J,K,L,N,O,P,Q,T
DCDA | Apollo/Conbraco | 2 1/2DCDA7 | 2.5 | VU | 2004-09-29 | 2022-09-29 | N | 9 | (mm)[#1SOV], (qqq)[#2SOV] | Y | Apollo/Conbraco 1/2DC 1/2" (VU), Apollo/Conbraco W432100 1/2" (VU) | (M),E,F,G,H,I,J,K,L,N,O,P,Q,T
DCDA | Apollo/Conbraco | 2 1/2DCDA8 | 2.5 | H | 2004-09-29 | 2022-09-29 | N | 9 | (ppp),qqq | Y | Apollo/Conbraco 1/2DC 1/2" (H), Apollo/Conbraco W432100 1/2" (H) | (M),E,F,G,H,I,J,K,L,N,O,P,Q,T
DCDA | Apollo/Conbraco | 2 1/2DCDA8 | 2.5 | VU | 2004-09-29 | 2022-09-29 | N | 9 | (ppp),qqq | Y | Apollo/Conbraco 1/2DC 1/2" (VU), Apollo/Conbraco W432100 1/2" (VU) | (M),E,F,G,H,I,J,K,L,N,O,P,Q,T
DCDA | Apollo/Conbraco | 2 1/2DCDAU | 2.5 | VUVD | 2001-04-10 | 2022-04-10 | N | 9 | (ll),mm | Y | Apollo/Conbraco 1/2DC 1/2" (H), Apollo/Conbraco W432100 1/2" (H) | (M),E,F,G,H,I,J,K,L,N,O,P,Q,T
DCDA | Apollo/Conbraco | 3DCDA | 3 | H | 2000-10-16 | 2024-10-16 | N | 9 | (ll),mm | Y | Apollo/Conbraco 1/2DC 1/2" (H), Apollo/Conbraco W432100 1/2" (H) | (M),E,F,G,H,I,J,K,L,N,O,P,Q,T
DCDA | Apollo/Conbraco | 3DCDA | 3 | VU | 2000-10-16 | 2024-10-16 | N | 9 | (ll),mm | Y | Apollo/Conbraco 1/2DC 1/2" (VU), Apollo/Conbraco W432100 1/2" (VU) | (M),E,F,G,H,I,J,K,L,N,O,P,Q,T
DCDA | Apollo/Conbraco | 3DCDA6 | 3 | H | 2001-04-10 | 2022-04-10 | N | 9 | (mm)[#1SOV],(nnn)[#2SOV] | Y | Apollo/Conbraco 1/2DC 1/2" (H), Apollo/Conbraco W432100 1/2" (H) | (M),E,F,G,H,I,J,K,L,N,O,P,Q,T
DCDA | Apollo/Conbraco | 3DCDA6 | 3 | VU | 2001-04-10 | 2022-04-10 | N | 9 | (mm)[#1SOV],(nnn)[#2SOV] | Y | Apollo/Conbraco 1/2DC 1/2" (VU), Apollo/Conbraco W432100 1/2" (VU) | (M),E,F,G,H,I,J,K,L,N,O,P,Q,T
DCDA | Apollo/Conbraco | 3DCDA7 | 3 | H | 2004-09-29 | 2022-09-29 | N | 9 | (mm)[#1SOV], (qqq)[#2SOV] | Y | Apollo/Conbraco 1/2DC 1/2" (H), Apollo/Conbraco W432100 1/2" (H) | (M),E,F,G,H,I,J,K,L,N,O,P,Q,T
DCDA | Apollo/Conbraco | 3DCDA7 | 3 | VU | 2004-09-29 | 2022-09-29 | N | 9 | (mm)[#1SOV], (qqq)[#2SOV] | Y | Apollo/Conbraco 1/2DC 1/2" (VU), Apollo/Conbraco W432100 1/2" (VU) | (M),E,F,G,H,I,J,K,L,N,O,P,Q,T
DCDA | Apollo/Conbraco | 3DCDA8 | 3 | H | 2004-09-29 | 2022-09-29 | N | 9 | (ppp),qqq | Y | Apollo/Conbraco 1/2DC 1/2" (H), Apollo/Conbraco W432100 1/2" (H) | (M),E,F,G,H,I,J,K,L,N,O,P,Q,T
DCDA | Apollo/Conbraco | 3DCDA8 | 3 | VU | 2004-09-29 | 2022-09-29 | N | 9 | (ppp),qqq | Y | Apollo/Conbraco 1/2DC 1/2" (VU), Apollo/Conbraco W432100 1/2" (VU) | (M),E,F,G,H,I,J,K,L,N,O,P,Q,T
DCDA | Apollo/Conbraco | 3DCDAU | 3 | VUVD | 2001-04-10 | 2022-04-10 | N | 9 | (ll),mm | Y | Apollo/Conbraco 1/2DC 1/2" (H), Apollo/Conbraco W432100 1/2" (H) | (M),E,F,G,H,I,J,K,L,N,O,P,Q,T
DCDA | Apollo/Conbraco | 40600C3 | 3 | H | 1996-08-20 | 2023-08-20 | N | 8 | uu,cc,mm | Y | Apollo/Conbraco 4010402 3/4" (H) | (M),A,B,C,D,E,F,G,H,I,J,K,L,N,O,P,Q,T | formerly 4060003
DCDA | Apollo/Conbraco | 4060A03 | 4 | [9 empty] | model designation changed to 4060AC3
DCDA | Apollo/Conbraco | 4060A03 | 4 | [9 empty] | model designation changed to 4060AE3
DCDA | Apollo/Conbraco | 4060AC3 | 4 | H | 1993-04-13 | 2023-04-13 | N | 8 | uu,cc,mm | Y | Apollo/Conbraco 4010402 3/4" (H) | (M),A,B,C,D,E,F,G,H,I,J,K,L,N,O,P,Q,T | formerly 4060A03
DCDA | Apollo/Conbraco | 4060AC6 | 4 | H | 2000-02-01 | 2024-02-01 | N | 8 | mm[#1SOV], nnn[#2SOV] | Y | Apollo/Conbraco 4010402 3/4" (H) | (M),A,B,C,D,E,F,G,H,I,J,K,L,N,O,P,Q,T
DCDA | Apollo/Conbraco | 4060AE3 | 4 | H | 1993-04-13 | 2023-04-13 | N | 8 | uu,cc,mm | Y | Apollo/Conbraco 4010402 3/4" (H) | (M),A,B,C,D,E,F,G,H,I,J,K,L,N,O,P,Q,T | formerly 4060A03
DCDA | Apollo/Conbraco | 4060AE6 | 4 | H | 2000-02-01 | 2024-02-01 | N | 8 | mm[#1SOV], nnn[#2SOV] | Y | Apollo/Conbraco 4010402 3/4" (H) | (M),A,B,C,D,E,F,G,H,I,J,K,L,N,O,P,Q,T
DCDA | Apollo/Conbraco | 4060C03 | 6 | [9 empty] | model designation changed to 4060CC3
DCDA | Apollo/Conbraco | 4060C03 | 6 | [9 empty] | model designation changed to 4060CE3
DCDA | Apollo/Conbraco | 4060CC3 | 6 | H | 1993-06-02 | 2023-06-02 | N | 8 | uu,cc,mm | Y | Apollo/Conbraco 4010402 3/4" (H) | (M),A,B,C,D,E,F,G,H,I,J,K,L,N,O,P,Q,T | formerly 4060C03
DCDA | Apollo/Conbraco | 4060CC6 | 6 | H | 2000-02-01 | 2024-02-01 | N | 8 | mm[#1SOV], nnn[#2SOV] | Y | Apollo/Conbraco 4010402 3/4" (H) | (M),A,B,C,D,E,F,G,H,I,J,K,L,N,O,P,Q,T
DCDA | Apollo/Conbraco | 4060CE3 | 6 | H | 1993-06-02 | 2023-06-02 | N | 8 | uu,cc,mm | Y | Apollo/Conbraco 4010402 3/4" (H) | (M),A,B,C,D,E,F,G,H,I,J,K,L,N,O,P,Q,T | formerly 4060C03
DCDA | Apollo/Conbraco | 4060CE6 | 6 | H | 2000-02-01 | 2024-02-01 | N | 8 | mm[#1SOV], nnn[#2SOV] | Y | Apollo/Conbraco 4010402 3/4" (H) | (M),A,B,C,D,E,F,G,H,I,J,K,L,N,O,P,Q,T
DCDA | Apollo/Conbraco | 4060E03 | 8 | [9 empty] | model designation changed to 4060EC3
DCDA | Apollo/Conbraco | 4060E03 | 8 | [9 empty] | model designation changed to 4060EE3
DCDA | Apollo/Conbraco | 4060EC3 | 8 | H | 1993-04-13 | 2023-04-13 | N | 8 | uu,cc,mm | Y | Apollo/Conbraco 4010402 3/4" (H) | (M),A,B,C,D,E,F,G,H,I,J,K,L,N,O,P,Q,T | formerly 4060E03
DCDA | Apollo/Conbraco | 4060EC6 | 8 | H | 2000-02-01 | 2024-02-01 | N | 8 | mm[#1SOV], nnn[#2SOV] | Y | Apollo/Conbraco 4010402 3/4" (H) | (M),A,B,C,D,E,F,G,H,I,J,K,L,N,O,P,Q,T
DCDA | Apollo/Conbraco | 4060EE3 | 8 | H | 1993-04-13 | 2023-04-13 | N | 8 | uu,cc,mm | Y | Apollo/Conbraco 4010402 3/4" (H) | (M),A,B,C,D,E,F,G,H,I,J,K,L,N,O,P,Q,T | formerly 4060E03
DCDA | Apollo/Conbraco | 4060EE6 | 8 | H | 2000-02-01 | 2024-02-01 | N | 8 | mm[#1SOV], nnn[#2SOV] | Y | Apollo/Conbraco 4010402 3/4" (H) | (M),A,B,C,D,E,F,G,H,I,J,K,L,N,O,P,Q,T
DCDA | Apollo/Conbraco | 4060G03 | 10 | [9 empty] | model designation changed to 4060GC3
DCDA | Apollo/Conbraco | 4060G03 | 10 | [9 empty] | model designation changed to 4060GE3
DCDA | Apollo/Conbraco | 4060GC3 | 10 | H | 1993-04-13 | 2023-04-13 | N | 8 | uu,cc,mm | Y | Apollo/Conbraco 4010402 3/4" (H) | (M),A,B,C,D,E,F,G,H,I,J,K,L,N,O,P,Q,T | formerly 4060G03
DCDA | Apollo/Conbraco | 4060GC6 | 10 | H | 2000-02-01 | 2024-02-01 | N | 8 | mm[#1SOV], nnn[#2SOV] | Y | Apollo/Conbraco 4010402 3/4" (H) | (M),A,B,C,D,E,F,G,H,I,J,K,L,N,O,P,Q,T
DCDA | Apollo/Conbraco | 4060GE3 | 10 | H | 1993-04-12 | 2023-04-12 | N | 8 | uu,cc,mm | Y | Apollo/Conbraco 4010402 3/4" (H) | (M),A,B,C,D,E,F,G,H,I,J,K,L,N,O,P,Q,T | formerly 4060G03
DCDA | Apollo/Conbraco | 4060GE6 | 10 | H | 2000-02-01 | 2024-02-01 | N | 8 | mm[#1SOV], nnn[#2SOV] | Y | Apollo/Conbraco 4010402 3/4" (H) | (M),A,B,C,D,E,F,G,H,I,J,K,L,N,O,P,Q,T
DCDA | Apollo/Conbraco | 4DCDA | 4 | H | 2000-10-16 | 2024-10-16 | N | 9 | (ll),mm | Y | Apollo/Conbraco 1/2DC 1/2" (H), Apollo/Conbraco W432100 1/2" (H) | (M),E,F,G,H,I,J,K,L,N,O,P,Q,T
DCDA | Apollo/Conbraco | 4DCDA | 4 | VU | 2000-10-16 | 2024-10-16 | N | 9 | (ll),mm | Y | Apollo/Conbraco 1/2DC 1/2" (VU), Apollo/Conbraco W432100 1/2" (VU) | (M),E,F,G,H,I,J,K,L,N,O,P,Q,T
DCDA | Apollo/Conbraco | 4DCDA6 | 4 | H | 2001-04-10 | 2022-04-10 | N | 9 | (mm)[#1SOV],(nnn)[#2SOV] | Y | Apollo/Conbraco 1/2DC 1/2" (H), Apollo/Conbraco W432100 1/2" (H) | (M),E,F,G,H,I,J,K,L,N,O,P,Q,T
DCDA | Apollo/Conbraco | 4DCDA6 | 4 | VU | 2001-04-10 | 2022-04-10 | N | 9 | (mm)[#1SOV],(nnn)[#2SOV] | Y | Apollo/Conbraco 1/2DC 1/2" (VU), Apollo/Conbraco W432100 1/2" (VU) | (M),E,F,G,H,I,J,K,L,N,O,P,Q,T
DCDA | Apollo/Conbraco | 4DCDA7 | 4 | H | 2004-09-29 | 2022-09-29 | N | 9 | (mm)[#1SOV], (qqq)[#2SOV] | Y | Apollo/Conbraco 1/2DC 1/2" (H), Apollo/Conbraco W432100 1/2" (H) | (M),E,F,G,H,I,J,K,L,N,O,P,Q,T
DCDA | Apollo/Conbraco | 4DCDA7 | 4 | VU | 2004-09-29 | 2022-09-29 | N | 9 | (mm)[#1SOV], (qqq)[#2SOV] | Y | Apollo/Conbraco 1/2DC 1/2" (VU), Apollo/Conbraco W432100 1/2" (VU) | (M),E,F,G,H,I,J,K,L,N,O,P,Q,T
DCDA | Apollo/Conbraco | 4DCDA8 | 4 | H | 2004-09-29 | 2022-09-29 | N | 9 | (ppp),qqq | Y | Apollo/Conbraco 1/2DC 1/2" (H), Apollo/Conbraco W432100 1/2" (H) | (M),E,F,G,H,I,J,K,L,N,O,P,Q,T
DCDA | Apollo/Conbraco | 4DCDA8 | 4 | VU | 2004-09-29 | 2022-09-29 | N | 9 | (ppp),qqq | Y | Apollo/Conbraco 1/2DC 1/2" (VU), Apollo/Conbraco W432100 1/2" (VU) | (M),E,F,G,H,I,J,K,L,N,O,P,Q,T
DCDA | Apollo/Conbraco | 4DCDAU | 4 | VUVD | 2001-04-10 | 2022-04-10 | N | 9 | (ll),mm | Y | Apollo/Conbraco 1/2DC 1/2" (H), Apollo/Conbraco W432100 1/2" (H) | (M),E,F,G,H,I,J,K,L,N,O,P,Q,T
DCDA | Apollo/Conbraco | 4SG 600U | 2.5 | [9 empty] | model designation changed to DCDA4SGN
DCDA | Apollo/Conbraco | 4SG 600U | 3 | [9 empty] | model designation changed to DCDA4SGN
DCDA | Apollo/Conbraco | 4SG 600U | 4 | [9 empty] | model designation changed to DCDA4SGN
DCDA | Apollo/Conbraco | 4SG 600U | 6 | [9 empty] | model designation changed to DCDA4SGN
DCDA | Apollo/Conbraco | 4SG 600U | 8 | [9 empty] | model designation changed to DCDA4SGN
DCDA | Apollo/Conbraco | 4SG-600 | 2.5 | [9 empty] | model designation changed to DCDA4SG
DCDA | Apollo/Conbraco | 4SG-600 | 2.5 | [9 empty] | model designation changed to DCDA4SG
DCDA | Apollo/Conbraco | 4SG-600 | 3 | [9 empty] | model designation changed to DCDA4SG
DCDA | Apollo/Conbraco | 4SG-600 | 3 | [9 empty] | model designation changed to DCDA4SG
DCDA | Apollo/Conbraco | 4SG-600 | 4 | [9 empty] | model designation changed to DCDA4SG
DCDA | Apollo/Conbraco | 4SG-600 | 4 | [9 empty] | model designation changed to DCDA4SG
DCDA | Apollo/Conbraco | 4SG-600 | 6 | [9 empty] | model designation changed to DCDA4SG
DCDA | Apollo/Conbraco | 4SG-600 | 6 | [9 empty] | model designation changed to DCDA4SG
DCDA | Apollo/Conbraco | 4SG-600 | 8 | [9 empty] | model designation changed to DCDA4SG
DCDA | Apollo/Conbraco | 4SG-600 | 8 | [9 empty] | model designation changed to DCDA4SG
DCDA | Apollo/Conbraco | 6DCDA | 6 | H | 2000-10-16 | 2024-10-16 | N | 9 | (ll),mm | Y | Apollo/Conbraco 1/2DC 1/2" (H), Apollo/Conbraco W432100 1/2" (H) | (M),E,F,G,H,I,J,K,L,N,O,P,Q,T
DCDA | Apollo/Conbraco | 6DCDA | 6 | VU | 2000-10-16 | 2024-10-16 | N | 9 | (ll),mm | Y | Apollo/Conbraco 1/2DC 1/2" (VU), Apollo/Conbraco W432100 1/2" (VU) | (M),E,F,G,H,I,J,K,L,N,O,P,Q,T
DCDA | Apollo/Conbraco | 6DCDA6 | 6 | H | 2001-04-10 | 2022-04-10 | N | 9 | (mm)[#1SOV],(nnn)[#2SOV] | Y | Apollo/Conbraco 1/2DC 1/2" (H), Apollo/Conbraco W432100 1/2" (H) | (M),E,F,G,H,I,J,K,L,N,O,P,Q,T
DCDA | Apollo/Conbraco | 6DCDA6 | 6 | VU | 2001-04-10 | 2022-04-10 | N | 9 | (mm)[#1SOV],(nnn)[#2SOV] | Y | Apollo/Conbraco 1/2DC 1/2" (VU), Apollo/Conbraco W432100 1/2" (VU) | (M),E,F,G,H,I,J,K,L,N,O,P,Q,T
DCDA | Apollo/Conbraco | 6DCDA7 | 6 | H | 2004-09-29 | 2022-09-29 | N | 9 | (mm)[#1SOV], (qqq)[#2SOV] | Y | Apollo/Conbraco 1/2DC 1/2" (H), Apollo/Conbraco W432100 1/2" (H) | (M),E,F,G,H,I,J,K,L,N,O,P,Q,T
DCDA | Apollo/Conbraco | 6DCDA7 | 6 | VU | 2004-09-29 | 2022-09-29 | N | 9 | (mm)[#1SOV], (qqq)[#2SOV] | Y | Apollo/Conbraco 1/2DC 1/2" (VU), Apollo/Conbraco W432100 1/2" (VU) | (M),E,F,G,H,I,J,K,L,N,O,P,Q,T
DCDA | Apollo/Conbraco | 6DCDA8 | 6 | H | 2004-09-29 | 2022-09-29 | N | 9 | (ppp),qqq | Y | Apollo/Conbraco 1/2DC 1/2" (H), Apollo/Conbraco W432100 1/2" (H) | (M),E,F,G,H,I,J,K,L,N,O,P,Q,T
DCDA | Apollo/Conbraco | 6DCDA8 | 6 | VU | 2004-09-29 | 2022-09-29 | N | 9 | (ppp),qqq | Y | Apollo/Conbraco 1/2DC 1/2" (VU), Apollo/Conbraco W432100 1/2" (VU) | (M),E,F,G,H,I,J,K,L,N,O,P,Q,T
DCDA | Apollo/Conbraco | 6DCDAU | 6 | VUVD | 2001-04-10 | 2022-04-10 | N | 9 | (ll),mm | Y | Apollo/Conbraco 1/2DC 1/2" (H), Apollo/Conbraco W432100 1/2" (H) | (M),E,F,G,H,I,J,K,L,N,O,P,Q,T
DCDA | Apollo/Conbraco | 8DCDA | 8 | H | 2003-01-16 | 2024-01-16 | N | 9 | (mm),ll | Y | Apollo/Conbraco 1/2DC 1/2" (H), Apollo/Conbraco W432100 1/2" (H) | (M),F,G,H,I,J,K,L,N,O,P,Q,T
DCDA | Apollo/Conbraco | 8DCDA | 8 | VU | 2003-01-16 | 2024-01-16 | N | 9 | (mm),ll | Y | Apollo/Conbraco 1/2DC 1/2" (VU), Apollo/Conbraco W432100 1/2" (VU) | (M),F,G,H,I,J,K,L,N,O,P,Q,T
DCDA | Apollo/Conbraco | 8DCDA7 | 8 | H | 2004-09-29 | 2022-09-29 | N | 9 | (mm)[#1SOV], (qqq)[#2SOV] | Y | Apollo/Conbraco 1/2DC 1/2" (H), Apollo/Conbraco W432100 1/2" (H) | (M),F,G,H,I,J,K,L,N,O,P,Q,T
DCDA | Apollo/Conbraco | 8DCDA7 | 8 | VU | 2004-09-29 | 2022-09-29 | N | 9 | (mm)[#1SOV], (qqq)[#2SOV] | Y | Apollo/Conbraco 1/2DC 1/2" (VU), Apollo/Conbraco W432100 1/2" (VU) | (M),F,G,H,I,J,K,L,N,O,P,Q,T
DCDA | Apollo/Conbraco | 8DCDA8 | 8 | H | 2004-09-29 | 2022-09-29 | N | 9 | (ppp),qqq | Y | Apollo/Conbraco 1/2DC 1/2" (H), Apollo/Conbraco W432100 1/2" (H) | (M),E,F,G,H,I,J,K,L,N,O,P,Q,T
DCDA | Apollo/Conbraco | 8DCDA8 | 8 | VU | 2004-09-29 | 2022-09-29 | N | 9 | (ppp),qqq | Y | Apollo/Conbraco 1/2DC 1/2" (VU), Apollo/Conbraco W432100 1/2" (VU) | (M),E,F,G,H,I,J,K,L,N,O,P,Q,T
DCDA | Apollo/Conbraco | DCDA4S | 10 | H | 2003-01-16 | 2024-01-16 | N | 9 | (mm),ll, xxxxx, zzzzz, bbbbbb, cccccc | N | Apollo/Conbraco 1/2DC 1/2" (H), Apollo/Conbraco W432100 1/2" (H) | (M),F,G,H,I,J,K,L,N,O,P,Q,T | formerly 10DCDA
DCDA | Apollo/Conbraco | DCDA4S | 10 | VU | 2003-01-16 | 2024-01-16 | N | 9 | (mm),ll, xxxxx, zzzzz, bbbbbb, cccccc | N | Apollo/Conbraco 1/2DC 1/2" (VU), Apollo/Conbraco W432100 1/2" (VU) | (M),F,G,H,I,J,K,L,N,O,P,Q,T | formerly 10DCDA
DCDA | Apollo/Conbraco | DCDA4SG | 2.5 | H | 2007-10-18 | 2022-10-18 | N | 9 | (yyy)ppp,qqq,ttt,xxxxx,yyyyy,zzzzz,aaaaaa, xxxxxx | N | Apollo/Conbraco 4S103 1/2" (H), Apollo/Conbraco W432100 1/2" (H) | (M),E,F,G,H,I,J,K,L,N,O,P,Q,T | formerly 4SG-600
DCDA | Apollo/Conbraco | DCDA4SG | 2.5 | VU | 2007-10-18 | 2022-10-18 | N | 9 | (yyy)ppp,qqq,ttt,xxxxx,yyyyy,zzzzz,aaaaaa, xxxxxx | N | Apollo/Conbraco 4S103 1/2" (VU), Apollo/Conbraco W432100 1/2" (V) | (M),E,F,G,H,I,J,K,L,N,O,P,Q,T | formerly 4SG-600
DCDA | Apollo/Conbraco | DCDA4SG | 3 | H | 2007-10-18 | 2022-10-18 | N | 9 | (yyy)ppp,qqq,ttt,xxxxx,yyyyy,zzzzz,aaaaaa, xxxxxx | N | Apollo/Conbraco 4S103 1/2" (H), Apollo/Conbraco W432100 1/2" (H) | (M),E,F,G,H,I,J,K,L,N,O,P,Q,T | formerly 4SG-600
DCDA | Apollo/Conbraco | DCDA4SG | 3 | VU | 2007-10-18 | 2022-10-18 | N | 9 | (yyy)ppp,qqq,ttt,xxxxx,yyyyy,zzzzz,aaaaaa, xxxxxx | N | Apollo/Conbraco 4S103 1/2" (VU), Apollo/Conbraco W432100 1/2" (V) | (M),E,F,G,H,I,J,K,L,N,O,P,Q,T | formerly 4SG-600
DCDA | Apollo/Conbraco | DCDA4SG | 4 | H | 2007-10-18 | 2022-10-18 | N | 9 | (yyy)ppp,qqq,ttt,xxxxx,yyyyy,zzzzz,aaaaaa, xxxxxx | N | Apollo/Conbraco 4S103 1/2" (H), Apollo/Conbraco W432100 1/2" (H) | (M),E,F,G,H,I,J,K,L,N,O,P,Q,T | formerly 4SG-600
DCDA | Apollo/Conbraco | DCDA4SG | 4 | VU | 2007-10-18 | 2022-10-18 | N | 9 | (yyy)ppp,qqq,ttt,xxxxx,yyyyy,zzzzz,aaaaaa, xxxxxx | N | Apollo/Conbraco 4S103 1/2" (VU), Apollo/Conbraco W432100 1/2" (V) | (M),E,F,G,H,I,J,K,L,N,O,P,Q,T | formerly 4SG-600
DCDA | Apollo/Conbraco | DCDA4SG | 6 | H | 2007-10-18 | 2022-10-18 | N | 9 | (yyy)ppp,qqq,ttt,xxxxx,yyyyy,zzzzz,aaaaaa, xxxxxx | N | Apollo/Conbraco 4S103 1/2" (H), Apollo/Conbraco W432100 1/2" (H) | (M),E,F,G,H,I,J,K,L,N,O,P,Q,T | formerly 4SG-600
DCDA | Apollo/Conbraco | DCDA4SG | 6 | VU | 2007-10-18 | 2022-10-18 | N | 9 | (yyy)ppp,qqq,ttt,xxxxx,yyyyy,zzzzz,aaaaaa, xxxxxx | N | Apollo/Conbraco 4S103 1/2" (VU), Apollo/Conbraco W432100 1/2" (V) | (M),E,F,G,H,I,J,K,L,N,O,P,Q,T | formerly 4SG-600
DCDA | Apollo/Conbraco | DCDA4SG | 8 | H | 2007-10-18 | 2022-10-18 | N | 9 | (yyy)ppp,qqq,ttt,xxxxx,yyyyy,zzzzz,aaaaaa, xxxxxx | N | Apollo/Conbraco 4S103 1/2" (H), Apollo/Conbraco W432100 1/2" (H) | (M),E,F,G,H,I,J,K,L,N,O,P,Q,T | formerly 4SG-600
DCDA | Apollo/Conbraco | DCDA4SG | 8 | VU | 2007-10-18 | 2022-10-18 | N | 9 | (yyy)ppp,qqq,ttt,xxxxx,yyyyy,zzzzz,aaaaaa, xxxxxx | N | Apollo/Conbraco 4S103 1/2" (VU), Apollo/Conbraco W432100 1/2" (V) | (M),E,F,G,H,I,J,K,L,N,O,P,Q,T | formerly 4SG-600
DCDA | Apollo/Conbraco | DCDA4SGN | 2.5 | VUVD | 2007-10-18 | 2022-10-18 | N | 9 | (yyy)ppp,qqq,ttt | Y | Apollo/Conbraco 4S103 1/2" (H), Apollo/Conbraco W432100 1/2" (H) | (M),E,F,G,H,I,J,K,L,N,O,P,Q,T | formerly 4SG 600U
DCDA | Apollo/Conbraco | DCDA4SGN | 3 | VUVD | 2007-10-18 | 2022-10-18 | N | 9 | (yyy)ppp,qqq,ttt | Y | Apollo/Conbraco 4S103 1/2" (H), Apollo/Conbraco W432100 1/2" (H) | (M),E,F,G,H,I,J,K,L,N,O,P,Q,T | formerly 4SG 600U
DCDA | Apollo/Conbraco | DCDA4SGN | 4 | VUVD | 2007-10-18 | 2022-10-18 | N | 9 | (yyy)ppp,qqq,ttt | Y | Apollo/Conbraco 4S103 1/2" (H), Apollo/Conbraco W432100 1/2" (H) | (M),E,F,G,H,I,J,K,L,N,O,P,Q,T | formerly 4SG 600U
DCDA | Apollo/Conbraco | DCDA4SGN | 6 | VUVD | 2007-10-18 | 2022-10-18 | N | 9 | (yyy)ppp,qqq,ttt | Y | Apollo/Conbraco 4S103 1/2" (H), Apollo/Conbraco W432100 1/2" (H) | (M),E,F,G,H,I,J,K,L,N,O,P,Q,T | formerly 4SG 600U
DCDA | Apollo/Conbraco | DCDA4SGN | 8 | VUVD | 2007-10-18 | 2022-10-18 | N | 9 | (yyy)ppp,qqq,ttt | Y | Apollo/Conbraco 4S103 1/2" (H), Apollo/Conbraco W432100 1/2" (H) | (M),E,F,G,H,I,J,K,L,N,O,P,Q,T | formerly 4SG 600U
DCDA | Apollo/Conbraco | DCDALF4A | 2.5 | H | 2013-10-30 | 2022-10-30 | Y | 10 | (yyy), cccc, dddd, mmmm, nnnn, xxxxx, yyyyy, zzzzz, aaaaaa, xxxxxx | N | Apollo DCLF4A 1/2" (H) | (P),G,H,I,J,K,L,M,N,O,Q,T
DCDA | Apollo/Conbraco | DCDALF4A | 2.5 | VU | 2013-10-30 | 2022-10-30 | Y | 10 | (yyy), cccc, dddd, mmmm, nnnn, xxxxx, yyyyy, zzzzz, aaaaaa, xxxxxx | N | Apollo DCLF4A 1/2" (VU) | (P),G,H,I,J,K,L,M,N,O,Q,T
DCDA | Apollo/Conbraco | DCDALF4A | 3 | H | 2013-10-30 | 2022-10-30 | Y | 10 | (yyy), cccc, dddd, mmmm, nnnn, xxxxx, yyyyy, zzzzz, aaaaaa, xxxxxx | N | Apollo DCLF4A 1/2" (H) | (P),G,H,I,J,K,L,M,N,O,Q,T
DCDA | Apollo/Conbraco | DCDALF4A | 3 | VU | 2013-10-30 | 2022-10-30 | Y | 10 | (yyy), cccc, dddd, mmmm, nnnn, xxxxx, yyyyy, zzzzz, aaaaaa, xxxxxx | N | Apollo DCLF4A 1/2" (VU) | (P),G,H,I,J,K,L,M,N,O,Q,T
DCDA | Apollo/Conbraco | DCDALF4A | 4 | H | 2013-06-24 | 2022-06-24 | Y | 10 | (yyy), cccc, dddd, mmmm, nnnn, xxxxx, yyyyy, zzzzz, aaaaaa, xxxxxx | N | Apollo DCLF4A 1/2" (H) | (P),G,H,I,J,K,L,M,N,O,Q,T
DCDA | Apollo/Conbraco | DCDALF4A | 4 | VU | 2013-06-24 | 2022-06-24 | Y | 10 | (yyy), cccc, dddd, mmmm, nnnn, xxxxx, yyyyy, zzzzz, aaaaaa, xxxxxx | N | Apollo DCLF4A 1/2" (VU) | (P),G,H,I,J,K,L,M,N,O,Q,T
DCDA | Apollo/Conbraco | DCDALF4A | 6 | H | 2013-06-24 | 2022-06-24 | Y | 10 | (yyy), cccc, dddd, mmmm, nnnn, xxxxx, yyyyy, zzzzz, aaaaaa, xxxxxx | N | Apollo DCLF4A 1/2" (H) | (P),G,H,I,J,K,L,M,N,O,Q,T
DCDA | Apollo/Conbraco | DCDALF4A | 6 | VU | 2013-06-24 | 2022-06-24 | Y | 10 | (yyy), cccc, dddd, mmmm, nnnn, xxxxx, yyyyy, zzzzz, aaaaaa, xxxxxx | N | Apollo DCLF4A 1/2" (VU) | (P),G,H,I,J,K,L,M,N,O,Q,T
DCDA | Apollo/Conbraco | DCDALF4A | 8 | H | 2014-05-15 | 2023-05-15 | Y | 10 | (yyy), cccc, dddd, mmmm, nnnn, xxxxx, yyyyy, zzzzz, aaaaaa, xxxxxx | N | Apollo DCLF4A 1/2" (H) | (P),G,H,I,J,K,L,M,N,O,Q,T
DCDA | Apollo/Conbraco | DCDALF4A | 8 | VU | 2014-05-15 | 2023-05-15 | Y | 10 | (yyy), cccc, dddd, mmmm, nnnn, xxxxx, yyyyy, zzzzz, aaaaaa, xxxxxx | N | Apollo DCLF4A 1/2" (VU) | (P),G,H,I,J,K,L,M,N,O,Q,T
DCDA | Apollo/Conbraco | DCDALF4AN | 2.5 | VUVD | 2014-06-10 | 2023-06-10 | Y | 10 | (yyy), cccc, dddd, mmmm, nnnn, xxxxx, yyyyy, zzzzz, aaaaaa, xxxxxx | N | Apollo DCLF4A 1/2" (H) | (P),G,H,I,J,K,L,M,N,O,Q,T
DCDA | Apollo/Conbraco | DCDALF4AN | 3 | VUVD | 2014-04-08 | 2023-04-08 | Y | 10 | (yyy), cccc, dddd, mmmm, nnnn, xxxxx, yyyyy, zzzzz, aaaaaa, xxxxxx | N | Apollo DCLF4A 1/2" (H) | (P),G,H,I,J,K,L,M,N,O,Q,T
DCDA | Apollo/Conbraco | DCDALF4AN | 4 | VUVD | 2014-01-23 | 2023-01-23 | Y | 10 | (yyy), cccc, dddd, mmmm, nnnn, xxxxx, yyyyy, zzzzz, aaaaaa, xxxxxx | N | Apollo DCLF4A 1/2" (H) | (P),G,H,I,J,K,L,M,N,O,Q,T
DCDA | Apollo/Conbraco | DCDALF4AN | 6 | VUVD | 2014-06-10 | 2023-06-10 | Y | 10 | (yyy), cccc, dddd, mmmm, nnnn, xxxxx, yyyyy, zzzzz, aaaaaa, xxxxxx | N | Apollo DCLF4A 1/2" (H) | (P),G,H,I,J,K,L,M,N,O,Q,T
DCDA | Apollo/Conbraco | DCDALF4AN | 8 | VUVD | 2014-03-14 | 2023-03-14 | Y | 10 | (yyy), cccc, dddd, mmmm, nnnn, xxxxx, yyyyy, zzzzz, aaaaaa, xxxxxx | N | Apollo DCLF4A 1/2" (H) | (P),G,H,I,J,K,L,M,N,O,Q,T
DCDA | Apollo/Conbraco | DCDALF4AP | 8 | H | 2019-10-30 | 2022-10-30 | Y | 10 | (yyy), cccc, dddd, mmmm, nnnn, xxxxx, yyyyy, zzzzz, aaaaaa, xxxxxx | N | Apollo DCLF4A 1/2" (H) | (P),G,H,I,J,K,L,M,N,O,Q,T
DCDA | Apollo/Conbraco | DCDALF4AP | 8 | VU | 2019-10-30 | 2022-10-30 | Y | 10 | (yyy), cccc, dddd, mmmm, nnnn, xxxxx, yyyyy, zzzzz, aaaaaa, xxxxxx | N | Apollo DCLF4A 1/2" (VU) | (P),G,H,I,J,K,L,M,N,O,Q,T
DCDA | Apollo/Conbraco | DCDALF4AR | 2.5 | H | 2015-11-09 | 2024-11-09 | Y | 10 | (cccc), dddd, mmmm, nnnn, xxxxx, yyyyy, zzzzz, aaaaaa | Y | Apollo/Conbraco DCLF4A 1/2" (H) | (M),G,H,I,J,K,L,N,O,Q,T | Integral Stainless Steel grooved spool between the #2 ck and #2 SOV - assembly length: min. 34" and max. 47 1/8"
DCDA | Apollo/Conbraco | DCDALF4AR | 2.5 | VU | 2015-11-09 | 2024-11-09 | Y | 10 | (cccc), dddd, mmmm, nnnn, xxxxx, yyyyy, zzzzz, aaaaaa | Y | Apollo/Conbraco DCLF4A 1/2" (VU) | (M),G,H,I,J,K,L,N,O,Q,T | Integral Stainless Steel grooved spool between the #2 ck and #2 SOV - assembly length: min. 34" and max. 47 1/8"
DCDA | Apollo/Conbraco | DCDALF4AR | 3 | H | 2015-11-09 | 2024-11-09 | Y | 10 | (cccc), dddd, mmmm, nnnn, xxxxx, yyyyy, zzzzz, aaaaaa | Y | Apollo/Conbraco DCLF4A 1/2" (H) | (M),G,H,I,J,K,L,N,O,Q,T | Integral Stainless Steel grooved spool between the #2 ck and #2 SOV - assembly length: min. 35" and max. 48 1/8"
DCDA | Apollo/Conbraco | DCDALF4AR | 3 | VU | 2015-11-09 | 2024-11-09 | Y | 10 | (cccc), dddd, mmmm, nnnn, xxxxx, yyyyy, zzzzz, aaaaaa | Y | Apollo/Conbraco DCLF4A 1/2" (VU) | (M),G,H,I,J,K,L,N,O,Q,T | Integral Stainless Steel grooved spool between the #2 ck and #2 SOV - assembly length: min. 35" and max. 48 1/8"
DCDA | Apollo/Conbraco | DCDALF4AR | 4 | H | 2015-09-21 | 2024-09-21 | Y | 10 | (cccc), dddd, mmmm, nnnn, xxxxx, yyyyy, zzzzz, aaaaaa | Y | Apollo/Conbraco DCLF4A 1/2" (H) | (M),G,H,I,J,K,L,N,O,Q,T | Integral Stainless Steel grooved spool between the #2 ck and #2 SOV - assembly length: min. 37 3/8" and max. 62 1/4"
DCDA | Apollo/Conbraco | DCDALF4AR | 4 | VU | 2015-09-21 | 2024-09-21 | Y | 10 | (cccc), dddd, mmmm, nnnn, xxxxx, yyyyy, zzzzz, aaaaaa | Y | Apollo/Conbraco DCLF4A 1/2" (VU) | (M),G,H,I,J,K,L,N,O,Q,T | Integral Stainless Steel grooved spool between the #2 ck and #2 SOV - assembly length: min. 37 3/8" and max. 62 1/4"
DCDA | Apollo/Conbraco | DCDALF4AR | 6 | H | 2015-09-21 | 2024-09-21 | Y | 10 | (cccc), dddd, mmmm, nnnn, xxxxx, yyyyy, zzzzz, aaaaaa | Y | Apollo/Conbraco DCLF4A 1/2" (H) | (M),G,H,I,J,K,L,N,O,Q,T | Integral Stainless Steel grooved spool between the #2 ck and #2 SOV - assembly length: min. 46" and max. 71 1/4"
DCDA | Apollo/Conbraco | DCDALF4AR | 6 | VU | 2015-09-21 | 2024-09-21 | Y | 10 | (cccc), dddd, mmmm, nnnn, xxxxx, yyyyy, zzzzz, aaaaaa | Y | Apollo/Conbraco DCLF4A 1/2" (VU) | (M),G,H,I,J,K,L,N,O,Q,T | Integral Stainless Steel grooved spool between the #2 ck and #2 SOV - assembly length: min. 46" and max. 71 1/4"
DCDA | Apollo/Conbraco | DCDALF4AR | 8 | H | 2015-12-21 | 2024-12-21 | Y | 10 | (cccc), dddd, mmmm, nnnn, xxxxx, yyyyy, zzzzz, aaaaaa | Y | Apollo/Conbraco DCLF4A 1/2" (H) | (M),G,H,I,J,K,L,N,O,Q,T | Integral Stainless Steel grooved spool between the #2 ck and #2 SOV - assembly length: min. 55 3/4" and max. 86"
DCDA | Apollo/Conbraco | DCDALF4AR | 8 | VU | 2015-12-21 | 2024-12-21 | Y | 10 | (cccc), dddd, mmmm, nnnn, xxxxx, yyyyy, zzzzz, aaaaaa | Y | Apollo/Conbraco DCLF4A 1/2" (VU) | (M),G,H,I,J,K,L,N,O,Q,T | Integral Stainless Steel grooved spool between the #2 ck and #2 SOV - assembly length: min. 55 3/4" and max. 86"
DCDA | Conbraco | [5 empty] | N | [5 empty] | See Apollo/Conbraco
DCDA | Febco | 856 | 2.5 | H | 1997-03-19 | 2024-03-19 | N | 8 | (ff),mm,oo,pp,uu,zzz,cccc,ffff,gggg | Y | Febco 805YB 3/4" (H) | (M),B,C,D,E,F,G,H,I,J,K,L,N,O,P,Q,T
DCDA | Febco | 856 | 2.5 | VU | 2000-01-05 | 2023-01-05 | N | 8 | (ff),mm,oo,pp,uu,zzz,cccc,ffff,gggg | Y | Febco 805YB 3/4" (VU) | (M),B,C,D,E,F,G,H,I,J,K,L,N,O,P,Q,T
DCDA | Febco | 856 | 3 | H | 1997-03-19 | 2024-03-19 | N | 8 | (ff),mm,oo,pp,uu,zzz,cccc,ffff,gggg | Y | Febco 805YB 3/4" (H) | (M),B,C,D,E,F,G,H,I,J,K,L,N,O,P,Q,T
DCDA | Febco | 856 | 3 | VU | 2000-01-05 | 2023-01-05 | N | 8 | (ff),mm,oo,pp,uu,zzz,cccc,ffff,gggg | Y | Febco 805YB 3/4" (VU) | (M),B,C,D,E,F,G,H,I,J,K,L,N,O,P,Q,T
DCDA | Febco | 856 | 4 | H | 1994-05-04 | 2024-05-04 | N | 8 | (ff),mm,oo,pp,uu,nnn,zzz,cccc,ffff,gggg | Y | Febco 805YB 3/4" (H) | (M),B,C,D,E,F,G,H,I,J,K,L,N,O,P,Q,T
DCDA | Febco | 856 | 4 | VU | 1996-04-16 | 2023-04-16 | N | 8 | (ff),mm,oo,pp,uu,nnn,zzz,cccc,ffff,gggg | Y | Febco 805YB 3/4" (VU) | (M),B,C,D,E,F,G,H,I,J,K,L,N,O,P,Q,T
DCDA | Febco | 856 | 6 | H | 1994-05-04 | 2024-05-04 | N | 8 | (ff),mm,oo,pp,uu,nnn,zzz,cccc,ffff,gggg | Y | Febco 805YB 3/4" (H) | (M),B,C,D,E,F,G,H,I,J,K,L,N,O,P,Q,T
DCDA | Febco | 856 | 6 | VU | 1996-04-16 | 2023-04-16 | N | 8 | (ff),mm,oo,pp,uu,nnn,zzz,cccc,ffff,gggg | Y | Febco 805YB 3/4" (VU) | (M),B,C,D,E,F,G,H,I,J,K,L,N,O,P,Q,T
DCDA | Febco | 856 | 8 | H | 1995-10-04 | 2022-10-04 | N | 8 | (ff),mm,oo,pp,uu,nnn,zzz,cccc,ffff,gggg | Y | Febco 805YB 3/4" (H) | (M),B,C,D,E,F,G,H,I,J,K,L,N,O,P,Q,T
DCDA | Febco | 856 | 8 | VU | 2000-01-05 | 2023-01-05 | N | 8 | (ff),mm,oo,pp,uu,nnn,zzz,cccc,ffff,gggg | Y | Febco 805YB 3/4" (VU) | (M),B,C,D,E,F,G,H,I,J,K,L,N,O,P,Q,T
DCDA | Febco | 858 | 2 | H | 2006-08-01 | 2024-08-01 | N | 9 | bbb,jjjj | Y | Watts 007QT 1/2" (H) | (H),A,B,C,D,E,F,G,I,J,K,L,M,N,O,P,Q,T
DCDA | Febco | 858 | 2 | VU | 2006-08-01 | 2024-08-01 | N | 9 | bbb,jjjj | Y | Watts 007QT 1/2" (VU) | (H),A,B,C,D,E,F,G,I,J,K,L,M,N,O,P,Q,T
DCDA | Febco | 858 | 2.5 | H | 2006-08-01 | 2024-08-01 | N | 8 | (pp), gg, hh,ll, mm, oo, tt, uu, zz, fff | Y | Watts 007M2QT 3/4" (H), Watts 007M1QT 3/4" (H) | (H),D,E,F,G,I,J,K,L,M,N,O,P,Q,T
DCDA | Febco | 858 | 2.5 | VU | 2006-08-01 | 2024-08-01 | N | 8 | (pp), gg, hh,ll, mm, oo, tt, uu, zz, fff | Y | Watts 007M2QT 3/4" (VU) | (H),D,E,F,G,I,J,K,L,M,N,O,P,Q,T
DCDA | Febco | 858 | 3 | H | 2006-08-01 | 2024-08-01 | N | 8 | (pp), gg, hh,ll, mm, oo, tt, uu, zz, fff | Y | Watts 007M2QT 3/4" (H), Watts 007M1QT 3/4" (H) | (H),D,E,F,G,I,J,K,L,M,N,O,P,Q,T
DCDA | Febco | 876 | 2.5 | VUVD | 1995-03-10 | 2022-03-10 | N | 8 | ff,mm,oo,pp,uu,cccc,zzz,ffff,gggg | Y | Febco 805YB 3/4" (H) | (M),B,C,D,E,F,G,H,I,J,K,L,N,O,P,Q,T
DCDA | Febco | 876 | 3 | VUVD | 1995-03-10 | 2022-03-10 | N | 8 | ff,mm,oo,pp,uu,cccc,zzz,ffff,gggg | Y | Febco 805YB 3/4" (H) | (M),B,C,D,E,F,G,H,I,J,K,L,N,O,P,Q,T
DCDA | Febco | 876 | 4 | VUVD | 1994-05-04 | 2024-05-04 | N | 8 | ff,mm,oo,pp,uu,cccc,zzz,ffff,gggg | Y | Febco 805YB 3/4" (H) | (M),B,C,D,E,F,G,H,I,J,K,L,N,O,P,Q,T
DCDA | Febco | 876 | 6 | VUVD | 1994-05-04 | 2024-05-04 | N | 8 | ff,mm,oo,pp,uu,cccc,zzz,ffff,gggg | Y | Febco 805YB 3/4" (H) | (M),B,C,D,E,F,G,H,I,J,K,L,N,O,P,Q,T
DCDA | Febco | 876 | 8 | VUVD | 1995-05-24 | 2022-05-24 | N | 8 | ff,mm,oo,pp,uu,cccc,zzz,ffff,gggg | Y | Febco 805YB 3/4" (H) | (M),B,C,D,E,F,G,H,I,J,K,L,N,O,P,Q,T
DCDA | Febco | 876 | 10 | VUVD | 1996-10-04 | 2023-10-04 | N | 8 | ff,mm,oo,pp,uu,cccc,zzz,ffff,gggg | Y | Febco 805YB 3/4" (H) | (M),B,C,D,E,F,G,H,I,J,K,L,N,O,P,Q,T
DCDA | Febco | 806 Type YD | 3 | [9 empty] | model designation changed to 806YD
DCDA | Febco | 806 Type YD | 4 | [9 empty] | model designation changed to 806YD
DCDA | Febco | 806 Type YD | 6 | [9 empty] | model designation changed to 806YD
DCDA | Febco | 806 Type YD | 8 | [9 empty] | model designation changed to 806YD
DCDA | Febco | 806 Type YD | 10 | [9 empty] | model designation changed to 806YD
DCDA | Febco | 806YD | 3 | H | 1988-09-26 | 2024-09-26 | N | 8 | (ff),mm,oo,pp,uu,zzz,ffff,gggg | Y | Febco 805Y 3/4" (H), Febco 805YB 3/4"(H) | (M),B,C,D,E,F,G,H,I,J,K,L,N,O,P,Q,T | formerly 806 Type YD
DCDA | Febco | 806YD | 4 | H | 1987-07-10 | 2023-07-10 | N | 7 | (ff),mm,oo,pp,uu,zzz,ffff,gggg | Y | Febco 805Y 3/4" (H), Febco 805YB 3/4"(H) | (F),A,B,C,D,E,G,H,I,J,K,L,M,N,O,P,Q,T | formerly 806 Type YD
DCDA | Febco | 806YD | 6 | H | 1987-07-10 | 2023-07-10 | N | 7 | (ff),mm,oo,pp,uu,zzz,ffff,gggg | Y | Febco 805Y 3/4" (H), Febco 805YB 3/4"(H) | (F),A,B,C,D,E,G,H,I,J,K,L,M,N,O,P,Q,T | formerly 806 Type YD
DCDA | Febco | 806YD | 8 | H | 1987-07-10 | 2023-07-10 | N | 7 | (ff),mm,oo,pp,uu,zzz,ffff,gggg | Y | Febco 805Y 3/4" (H), Febco 805YB 3/4"(H) | (F),A,B,C,D,E,G,H,I,J,K,L,M,N,O,P,Q,T | formerly 806 Type YD
DCDA | Febco | 806YD | 10 | H | 1987-07-10 | 2023-07-10 | N | 7 | (ff),mm,oo,pp,uu,zzz,ffff,gggg | Y | Febco 805Y 3/4" (H), Febco 805YB 3/4"(H) | (F),A,B,C,D,E,G,H,I,J,K,L,M,N,O,P,Q,T | formerly 806 Type YD
DCDA | Febco | 856ST | 2.5 | H | 2012-05-22 | 2024-05-22 | N | 9 | (ll),mm,oo,pp,zzz,cccc,dddd,eeee,ffff,gggg,nnnnn | Y | Watts 719QT 3/4" (H) | (O),G,H,I,J,K,L,M,N,P,Q,T
DCDA | Febco | 856ST | 2.5 | VU | 2012-05-22 | 2024-05-22 | N | 9 | (ll),mm,oo,pp,zzz,cccc,dddd,eeee,ffff,gggg,nnnnn | Y | Watts 719QT 3/4" (VU) | (O),G,H,I,J,K,L,M,N,P,Q,T
DCDA | Febco | 856ST | 3 | H | 2012-05-22 | 2024-05-22 | N | 9 | (ll),mm,oo,pp,zzz,cccc,dddd,eeee,ffff,gggg,nnnnn | Y | Watts 719QT 3/4" (H) | (O),H,I,J,K,L,M,N,P,Q
DCDA | Febco | 856ST | 3 | VU | 2012-05-22 | 2024-05-22 | N | 9 | (ll),mm,oo,pp,zzz,cccc,dddd,eeee,ffff,gggg,nnnnn | Y | Watts 719QT 3/4" (VU) | (O),H,I,J,K,L,M,N,P,Q
DCDA | Febco | 856ST | 4 | H | 2012-05-22 | 2024-05-22 | N | 9 | (ll),mm,oo,pp,zzz,cccc,dddd,eeee,ffff,gggg,nnnnn | Y | Watts 719QT 3/4" (H) | (O),H,I,J,K,L,M,N,P,Q
DCDA | Febco | 856ST | 4 | VU | 2012-05-22 | 2024-05-22 | N | 9 | (ll),mm,oo,pp,zzz,cccc,dddd,eeee,ffff,gggg,nnnnn | Y | Watts 719QT 3/4" (VU) | (O),H,I,J,K,L,M,N,P,Q
DCDA | Febco | 856ST | 6 | H | 2012-05-22 | 2024-05-22 | N | 9 | (ll),mm,oo,pp,zzz,cccc,dddd,eeee,ffff,gggg,nnnnn | Y | Watts 719QT 3/4" (H) | (O),H,I,J,K,L,M,N,P,Q
DCDA | Febco | 856ST | 6 | VU | 2012-08-09 | 2024-08-09 | N | 9 | (ll),mm,oo,pp,zzz,cccc,dddd,eeee,ffff,gggg,nnnnn | Y | Watts 719QT 3/4" (H) | (O),H,I,J,K,L,M,N,P,Q
DCDA | Febco | 856ST | 8 | H | 2012-05-22 | 2024-05-22 | N | 9 | (ll),mm,oo,pp,zzz,cccc,dddd,eeee,ffff,gggg,nnnnn | Y | Watts 719QT 3/4" (H) | (O),H,I,J,K,L,M,N,P,Q
DCDA | Febco | 856ST | 8 | VU | 2012-08-09 | 2024-08-09 | N | 9 | (ll),mm,oo,pp,zzz,cccc,dddd,eeee,ffff,gggg,nnnnn | Y | Watts 719QT 3/4" (H) | (O),H,I,J,K,L,M,N,P,Q
DCDA | Febco | 856ST | 10 | H | 2013-09-03 | 2022-09-03 | N | 9 | (ll),mm,oo,pp,zzz,cccc,dddd,eeee,ffff,gggg,nnnnn | N | Watts 719QT 3/4" (H) | (O),H,I,J,K,L,M,N,P,Q
DCDA | Febco | 856ST | 10 | VU | 2013-09-03 | 2022-09-03 | N | 9 | (ll),mm,oo,pp,zzz,cccc,dddd,eeee,ffff,gggg,nnnnn | N | Watts 719QT 3/4" (H) | (O),H,I,J,K,L,M,N,P,Q
DCDA | Febco | 876V | 2.5 | VUVD | 1996-03-08 | 2023-03-08 | N | 8 | (ff),ee,ll,mm,oo,pp,tt,uu,zzz,ffff,gggg | Y | Febco 805YB 3/4" (H) | (M),B,C,D,E,F,G,H,I,J,K,L,N,O,P,Q,T
DCDA | Febco | 876V | 2.5 | VUVU | 1996-03-08 | 2023-03-08 | N | 8 | (ff),ee,ll,mm,oo,pp,tt,uu,zzz,ffff,gggg | Y | Febco 805YB 3/4" (H) | (M),B,C,D,E,F,G,H,I,J,K,L,N,O,P,Q,T
DCDA | Febco | 876V | 3 | VUVD | 1996-03-08 | 2023-03-08 | N | 8 | (ff),ee,ll,mm,oo,pp,tt,uu,zzz,ffff,gggg | Y | Febco 805YB 3/4" (H) | (M),B,C,D,E,F,G,H,I,J,K,L,N,O,P,Q,T
DCDA | Febco | 876V | 3 | VUVU | 1996-03-08 | 2023-03-08 | N | 8 | (ff),ee,ll,mm,oo,pp,tt,uu,zzz,ffff,gggg | Y | Febco 805YB 3/4" (H) | (M),B,C,D,E,F,G,H,I,J,K,L,N,O,P,Q,T
DCDA | Febco | 876V | 4 | VUVD | 1996-03-08 | 2023-03-08 | N | 8 | (ff),ee,ll,mm,oo,pp,tt,uu,zzz,ffff,gggg | Y | Febco 805YB 3/4" (H) | (M),B,C,D,E,F,G,H,I,J,K,L,N,O,P,Q,T
DCDA | Febco | 876V | 4 | VUVU | 1996-03-08 | 2023-03-08 | N | 8 | (ff),ee,ll,mm,oo,pp,tt,uu,zzz,ffff,gggg | Y | Febco 805YB 3/4" (H) | (M),B,C,D,E,F,G,H,I,J,K,L,N,O,P,Q,T
DCDA | Febco | 876V | 6 | VUVD | 1996-03-08 | 2023-03-08 | N | 8 | (ff),ee,ll,mm,oo,pp,tt,uu,zzz,ffff,gggg | Y | Febco 805YB 3/4" (H) | (M),B,C,D,E,F,G,H,I,J,K,L,N,O,P,Q,T
DCDA | Febco | 876V | 6 | VUVU | 1996-03-08 | 2023-03-08 | N | 8 | (ff),ee,ll,mm,oo,pp,tt,uu,zzz,ffff,gggg | Y | Febco 805YB 3/4" (H) | (M),B,C,D,E,F,G,H,I,J,K,L,N,O,P,Q,T
DCDA | Febco | 876V | 8 | VUVD | 1997-01-06 | 2023-01-06 | N | 8 | (ff),mm,oo,pp,uu,zzz,ffff,gggg | Y | Febco 805YB 3/4" (H) | (M),B,C,D,E,F,G,H,I,J,K,L,N,O,P,Q,T
DCDA | Febco | 876V | 8 | VUVU | 1997-01-06 | 2023-01-06 | N | 8 | (ff),mm,oo,pp,uu,zzz,ffff,gggg | Y | Febco 805YB 3/4" (H) | (M),B,C,D,E,F,G,H,I,J,K,L,N,O,P,Q,T
DCDA | Febco | 876V | 10 | VUVD | 1997-07-11 | 2024-07-11 | N | 8 | (ee),ff,ll,mm,oo,pp,tt,uu,zzz,ffff,gggg | Y | Febco 805YB 3/4" (H) | (M),B,C,D,E,F,G,H,I,J,K,L,N,O,P,Q,T
DCDA | Febco | 876V | 10 | VUVU | 1997-07-11 | 2024-07-11 | N | 8 | (ee),ff,ll,mm,oo,pp,tt,uu,zzz,ffff,gggg | Y | Febco 805YB 3/4" (H) | (M),B,C,D,E,F,G,H,I,J,K,L,N,O,P,Q,T
DCDA | Febco | 876VST | 2.5 | VUVD | 2012-05-22 | 2024-05-22 | N | 9 | (ll),mm,oo,pp,zzz,cccc,dddd,eeee,ffff,gggg,nnnnn | Y | Watts 719QT 3/4" (H) | (O),G,H,I,J,K,L,M,N,P,Q,T
DCDA | Febco | 876VST | 2.5 | VUVU | 2012-05-22 | 2024-05-22 | N | 9 | (ll),mm,oo,pp,zzz,cccc,dddd,eeee,ffff,gggg,nnnnn | Y | Watts 719QT 3/4" (H) | (O),G,H,I,J,K,L,M,N,P,Q,T
DCDA | Febco | 876VST | 3 | VUVD | 2012-05-22 | 2024-05-22 | N | 9 | (ll),mm,oo,pp,zzz,cccc,dddd,eeee,ffff,gggg,nnnnn | Y | Watts 719QT 3/4" (H) | (O),H,I,J,K,L,M,N,P,Q
DCDA | Febco | 876VST | 3 | VUVU | 2012-05-22 | 2024-05-22 | N | 9 | (ll),mm,oo,pp,zzz,cccc,dddd,eeee,ffff,gggg,nnnnn | Y | Watts 719QT 3/4" (H) | (O),H,I,J,K,L,M,N,P,Q
DCDA | Febco | 876VST | 4 | VUVD | 2012-05-22 | 2024-05-22 | N | 9 | (ll),mm,oo,pp,zzz,cccc,dddd,eeee,ffff,gggg,nnnnn | Y | Watts 719QT 3/4" (H) | (O),H,I,J,K,L,M,N,P,Q
DCDA | Febco | 876VST | 4 | VUVU | 2012-05-22 | 2024-05-22 | N | 9 | (ll),mm,oo,pp,zzz,cccc,dddd,eeee,ffff,gggg,nnnnn | Y | Watts 719QT 3/4" (H) | (O),H,I,J,K,L,M,N,P,Q
DCDA | Febco | 876VST | 6 | VUVD | 2012-05-22 | 2024-05-22 | N | 9 | (ll),mm,oo,pp,zzz,cccc,dddd,eeee,ffff,gggg,nnnnn | Y | Watts 719QT 3/4" (H) | (O),H,I,J,K,L,M,N,P,Q
DCDA | Febco | 876VST | 6 | VUVU | 2012-05-22 | 2024-05-22 | N | 9 | (ll),mm,oo,pp,zzz,cccc,dddd,eeee,ffff,gggg,nnnnn | Y | Watts 719QT 3/4" (H) | (O),H,I,J,K,L,M,N,P,Q
DCDA | Febco | 876VST | 8 | VUVD | 2012-05-22 | 2024-05-22 | N | 9 | (ll),mm,oo,pp,zzz,cccc,dddd,eeee,ffff,gggg,nnnnn | Y | Watts 719QT 3/4" (H) | (O),H,I,J,K,L,M,N,P,Q
DCDA | Febco | 876VST | 8 | VUVU | 2012-05-22 | 2024-05-22 | N | 9 | (ll),mm,oo,pp,zzz,cccc,dddd,eeee,ffff,gggg,nnnnn | Y | Watts 719QT 3/4" (H) | (O),H,I,J,K,L,M,N,P,Q
DCDA | Watts | 007DCDA | 2 | H | 1997-06-16 | 2024-06-16 | N | 9 | (bbb),jjjj,rrrrr | Y | Watts 007QT 1/2" (H) | (H),A,B,C,D,E,F,G,I,J,K,L,M,N,O,P,Q,T,U | Previously Approved 8th Ed. (19 Apr 1996)
DCDA | Watts | 007DCDA | 2 | VU | 1997-06-16 | 2024-06-16 | N | 9 | (bbb),jjjj,rrrrr | Y | Watts 007QT 1/2" (VU) | (H),A,B,C,D,E,F,G,I,J,K,L,M,N,O,P,Q,T,U | Previously Approved 8th Ed. (10 Sept 1996)
DCDA | Watts | 007DCDA | 2.5 | H | 1993-10-11 | 2023-10-11 | N | 8 | (pp),gg,hh,ll,mm,oo,tt,uu,zz,ffff,gggg | N | Watts 007M2QT 3/4" (H), Watts 007M1QT 3/4" (H) | (H),D,E,F,G,I,J,K,L,M,N,O,P,Q,T,U
DCDA | Watts | 007DCDA | 2.5 | VU | 1996-08-27 | 2023-08-27 | N | 8 | (pp),gg,hh,ll,mm,oo,tt,uu,zz,ffff,gggg | N | Watts 007M2QT 3/4" (VU) | (H),D,E,F,G,I,J,K,L,M,N,O,P,Q,T,U
DCDA | Watts | 007DCDA | 3 | H | 1992-09-19 | 2022-09-19 | N | 8 | (pp),hh,mm,uu,zz,ffff,gggg | N | Watts 007M2QT 3/4" (H), Watts 007M1QT 3/4" (H) | (H),D,E,F,G,I,J,K,L,M,N,O,P,Q,T,U
DCDA | Watts | 007DCDA-FP | 2 | H | 2009-09-01 | 2024-09-01 | N | 9 | (eeeee) | N | Ames 2000B 1/2" (H), Watts 007QT 1/2" (H) | (H),A,B,C,D,E,F,G,I,J,K,L,M,N,O,P,Q,T,U
DCDA | Watts | 007M1DCDA | 2 | H | 2015-06-19 | 2024-06-19 | N | 9 | (eeeee), bbb, jjjj,rrrrr | N | Watts 007QT 1/2" (H) | (H),A,B,C,D,E,F,G,I,J,K,L,M,N,O,P,Q,T,U
DCDA | Watts | 007M1DCDA | 2 | VU | 2015-06-19 | 2024-06-19 | N | 9 | (eeeee), bbb, jjjj,rrrrr | N | Watts 007QT 1/2" (VU) | (H),A,B,C,D,E,F,G,I,J,K,L,M,N,O,P,Q,T,U
DCDA | Watts | 709DCDA | 3 | H | 1987-04-19 | 2023-04-19 | N | 6 | (pp),hh,uu,zz,eee,ffff,gggg,aaaaaaa | N | Watts 007QT 1/2" (H), Watts 007M1QT 3/4" (H), Watts 709QT 3/4" (H) | (N),B,C,D,E,F,G,H,I,J,K,L,M,O,P,Q,T,U | formerly 709DDC
DCDA | Watts | 709DCDA | 4 | H | 1987-07-27 | 2023-07-27 | N | 6 | (pp),hh,uu,zz,eee,ffff,gggg,aaaaaaa | N | Watts 007QT 1/2" (H), Watts 007M1QT 3/4" (H), Watts 709QT 3/4" (H) | (N),A,B,C,D,E,F,G,H,I,J,K,L,M,O,P,Q,T,U | formerly 709DDC
DCDA | Watts | 709DCDA | 4 | VU | 1996-08-27 | 2023-08-27 | N | 8 | (pp),hh,uu,zz,eee,ffff,gggg,aaaaaaa | N | Watts 007QT 1/2" (VU), Watts 007M2QT 3/4" (VU) | (N),A,B,C,D,E,F,G,H,I,J,K,L,M,O,P,Q,T,U | formerly 709DDC
DCDA | Watts | 709DCDA | 6 | H | 1987-07-27 | 2023-07-27 | N | 6 | (pp),hh,uu,zz,eee,ffff,gggg,aaaaaaa | N | Watts 007QT 1/2" (H), Watts 007M1QT 3/4" (H), Watts 709QT 3/4" (H) | (N),A,B,C,D,E,F,G,H,I,J,K,L,M,O,P,Q,T,U | formerly 709DDC
DCDA | Watts | 709DCDA | 6 | VU | 1996-12-05 | 2023-12-05 | N | 8 | (pp),hh,mm,uu,zz,eee,ffff,gggg,aaaaaaa | N | Watts 007QT 1/2" (VU) | (H),A,B,C,D,E,F,G,I,J,K,L,M,N,O,P,Q,T,U
DCDA | Watts | 709DCDA | 8 | H | 1987-04-19 | 2023-04-19 | N | 6 | (pp),hh,mm,uu,zz,eee,ffff,gggg,aaaaaaa | N | Watts 007QT 1/2" (H), Watts 007M1QT 3/4" (H), Watts 709QT 3/4" (H) | (N),A,B,C,D,E,F,G,H,I,J,K,L,M,O,P,Q,T,U | formerly 709DDC
DCDA | Watts | 709DCDA | 8 | VU | 1996-12-05 | 2023-12-05 | N | 8 | (pp),hh,mm,uu,zz,eee,ffff,gggg,aaaaaaa | N | Watts 007QT 1/2" (VU) | (H),A,B,C,D,E,F,G,I,J,K,L,M,N,O,P,Q,T,U
DCDA | Watts | 709DCDA | 10 | H | 1987-07-27 | 2023-07-27 | N | 6 | (pp),hh,mm,uu,zz,eee,ffff,gggg | N | Watts 007QT 1/2" (H), Watts 007M1QT 3/4" (H), Watts 709QT 3/4" (H) | (N),E,F,G,H,I,J,K,L,M,O,P,Q,T,U | formerly 709DDC
DCDA | Watts | 709DCDA | 10 | VU | 1996-12-05 | 2023-12-05 | N | 8 | (pp),hh,mm,uu,zz,eee,ffff,gggg | N | Watts 007QT 1/2" (VU) | (H),A,B,C,D,E,F,G,I,J,K,L,M,N,O,P,Q,T,U
DCDA | Watts | 709DDC | 3 | [9 empty] | model designation changed to 709DCDA
DCDA | Watts | 709DDC | 4 | [9 empty] | model designation changed to 709DCDA
DCDA | Watts | 709DDC | 4 | [9 empty] | model designation changed to 709DCDA
DCDA | Watts | 709DDC | 6 | [9 empty] | model designation changed to 709DCDA
DCDA | Watts | 709DDC | 8 | [9 empty] | model designation changed to 709DCDA
DCDA | Watts | 709DDC | 10 | [9 empty] | model designation changed to 709DCDA
DCDA | Watts | 757aDCDABF | 2.5 | H | 2003-11-06 | 2024-11-06 | N | 9 | (yyy) | Y | Watts 007M3QT 3/4" (H) | (N),G,H,I,J,K,L,M,O,P,Q,T
DCDA | Watts | 757aDCDABF | 2.5 | VU | 2003-11-06 | 2024-11-06 | N | 9 | (yyy) | Y | Watts 007M3QT 3/4" (VU) | (N),G,H,I,J,K,L,M,O,P,Q,T
DCDA | Watts | 757aDCDABF | 3 | H | 2003-11-06 | 2024-11-06 | N | 9 | (yyy) | Y | Watts 007M3QT 3/4" (H) | (N),G,H,I,J,K,L,M,O,P,Q,T
DCDA | Watts | 757aDCDABF | 3 | VU | 2003-11-06 | 2024-11-06 | N | 9 | (yyy) | Y | Watts 007M3QT 3/4" (VU) | (N),G,H,I,J,K,L,M,O,P,Q,T
DCDA | Watts | 757aDCDABF | 4 | H | 2003-11-06 | 2024-11-06 | N | 9 | (yyy) | Y | Watts 007M3QT 3/4" (H) | (N),G,H,I,J,K,L,M,O,P,Q,T
DCDA | Watts | 757aDCDABF | 4 | VU | 2003-11-06 | 2024-11-06 | N | 9 | (yyy) | Y | Watts 007M3QT 3/4" (VU) | (N),G,H,I,J,K,L,M,O,P,Q,T
DCDA | Watts | 757aDCDABF | 6 | H | 2004-11-03 | 2022-11-03 | N | 9 | (yyy) | Y | Watts 007M3QT 3/4 (H) | (N),G,H,I,J,K,L,M,O,P,Q,T
DCDA | Watts | 757aDCDABF | 6 | VU | 2005-01-18 | 2023-01-18 | N | 9 | (yyy) | Y | Watts 007M3QT 3/4" (VU) | (N),G,H,I,J,K,L,M,O,P,Q,T
DCDA | Watts | 757aDCDAGV | 2.5 | H | 2003-11-06 | 2024-11-06 | N | 9 | (zzz) | Y | Watts 007M3QT 3/4" (H) | (N),G,H,I,J,K,L,M,O,P,Q,T
DCDA | Watts | 757aDCDAGV | 2.5 | VU | 2003-11-06 | 2024-11-06 | N | 9 | (zzz) | Y | Watts 007M3QT 3/4" (VU) | (N),G,H,I,J,K,L,M,O,P,Q,T
DCDA | Watts | 757aDCDAGV | 3 | H | 2003-11-06 | 2024-11-06 | N | 9 | (zzz) | Y | Watts 007M3QT 3/4" (H) | (N),G,H,I,J,K,L,M,O,P,Q,T
DCDA | Watts | 757aDCDAGV | 3 | VU | 2003-11-06 | 2024-11-06 | N | 9 | (zzz) | Y | Watts 007M3QT 3/4" (VU) | (N),G,H,I,J,K,L,M,O,P,Q,T
DCDA | Watts | 757aDCDAGV | 4 | H | 2003-11-06 | 2024-11-06 | N | 9 | (zzz) | Y | Watts 007M3QT 3/4" (H) | (N),G,H,I,J,K,L,M,O,P,Q,T
DCDA | Watts | 757aDCDAGV | 4 | VU | 2003-11-06 | 2024-11-06 | N | 9 | (zzz) | Y | Watts 007M3QT 3/4" (VU) | (N),G,H,I,J,K,L,M,O,P,Q,T
DCDA | Watts | 757aDCDAGV | 6 | H | 2005-01-18 | 2023-01-18 | N | 9 | (zzz) | Y | Watts 007M3QT 3/4" (VU) | (N),G,H,I,J,K,L,M,O,P,Q,T
DCDA | Watts | 757aDCDAGV | 6 | VU | 2005-01-18 | 2023-01-18 | N | 9 | (zzz) | Y | Watts 007M3QT 3/4" (VU) | (N),G,H,I,J,K,L,M,O,P,Q,T
DCDA | Watts | 757DCDABF | 2.5 | H | 2005-10-04 | 2023-10-04 | N | 9 | (yyy) | N | Watts 007M3QT 3/4" (H) | (N),G,H,I,J,K,L,M,O,P,Q,T
DCDA | Watts | 757DCDABF | 2.5 | VU | 2005-10-04 | 2023-10-04 | N | 9 | (yyy) | N | Watts 007M3QT 3/4" (V) | (N),G,H,I,J,K,L,M,O,P,Q,T
DCDA | Watts | 757DCDABF | 3 | H | 2005-10-04 | 2023-10-04 | N | 9 | (yyy) | N | Watts 007M3QT 3/4" (H) | (N),G,H,I,J,K,L,M,O,P,Q,T
DCDA | Watts | 757DCDABF | 3 | VU | 2005-10-04 | 2023-10-04 | N | 9 | (yyy) | N | Watts 007M3QT 3/4" (V) | (N),G,H,I,J,K,L,M,O,P,Q,T
DCDA | Watts | 757DCDABF | 4 | H | 2005-10-04 | 2023-10-04 | N | 9 | (yyy) | N | Watts 007M3QT 3/4" (H) | (N),G,H,I,J,K,L,M,O,P,Q,T
DCDA | Watts | 757DCDABF | 4 | VU | 2005-10-04 | 2023-10-04 | N | 9 | (yyy) | N | Watts 007M3QT 3/4" (V) | (N),G,H,I,J,K,L,M,O,P,Q,T
DCDA | Watts | 757DCDABF | 6 | H | 2007-03-19 | 2022-03-23 | N | 9 | (yyy) | N | Watts 007M3QT 3/4" (H ) | (N),G,H,I,J,K,L,M,O,P,Q,T
DCDA | Watts | 757DCDABF | 6 | VU | 2007-03-19 | 2022-03-23 | N | 9 | (yyy) | N | Watts 007M3QT 3/4" (VU) | (N),G,H,I,J,K,L,M,O,P,Q,T
DCDA | Watts | 757DCDABF | 8 | H | 2007-03-09 | 2022-03-09 | N | 9 | (yyy) | N | Watts 007M3QT 3/4" (H & VU) | (N),G,H,I,J,K,L,M,O,P,Q,T
DCDA | Watts | 757DCDABF | 8 | VU | 2007-03-09 | 2022-03-09 | N | 9 | (yyy) | N | Watts 007M3QT 3/4" (H & VU) | (N),G,H,I,J,K,L,M,O,P,Q,T
DCDA | Watts | 757DCDABF | 10 | H | 2009-09-17 | 2024-09-17 | N | 9 | (yyy) | N | Watts 007M3QT 3/4" (H), Ames 2000 BM3 (H) | (N),G,H,I,J,K,L,M,O,P,Q,T
DCDA | Watts | 757DCDABF | 10 | VU | 2009-09-17 | 2024-09-17 | N | 9 | (yyy) | N | Watts 007M3QT 3/4" (V), Ames 2000 BM3 (V) | (N),G,H,I,J,K,L,M,O,P,Q,T
DCDA | Watts | 757DCDAGV | 2.5 | H | 2005-10-04 | 2023-10-04 | N | 9 | (zzz) | N | Watts 007M3QT 3/4" (H) | (N),G,H,I,J,K,L,M,O,P,Q,T
DCDA | Watts | 757DCDAGV | 2.5 | VU | 2005-10-04 | 2023-10-04 | N | 9 | (zzz) | N | Watts 007M3QT 3/4" (V) | (N),G,H,I,J,K,L,M,O,P,Q,T
DCDA | Watts | 757DCDAGV | 3 | H | 2005-10-04 | 2023-10-04 | N | 9 | (zzz) | N | Watts 007M3QT 3/4" (H) | (N),G,H,I,J,K,L,M,O,P,Q,T
DCDA | Watts | 757DCDAGV | 3 | VU | 2005-10-04 | 2023-10-04 | N | 9 | (zzz) | N | Watts 007M3QT 3/4" (V) | (N),G,H,I,J,K,L,M,O,P,Q,T
DCDA | Watts | 757DCDAGV | 4 | H | 2005-10-04 | 2023-10-04 | N | 9 | (zzz) | N | Watts 007M3QT 3/4" (H) | (N),G,H,I,J,K,L,M,O,P,Q,T
DCDA | Watts | 757DCDAGV | 4 | VU | 2005-10-04 | 2023-10-04 | N | 9 | (zzz) | N | Watts 007M3QT 3/4" (V) | (N),G,H,I,J,K,L,M,O,P,Q,T
DCDA | Watts | 757DCDAGV | 6 | H | 2007-03-19 | 2022-03-23 | N | 9 | (zzz) | N | Watts 007M3QT 3/4" (H ) | (N),G,H,I,J,K,L,M,O,P,Q,T
DCDA | Watts | 757DCDAGV | 6 | VU | 2007-03-19 | 2022-03-23 | N | 9 | (zzz) | N | Watts 007M3QT 3/4" (VU) | (N),G,H,I,J,K,L,M,O,P,Q,T
DCDA | Watts | 757DCDAGV | 8 | H | 2007-03-09 | 2022-03-09 | N | 9 | (zzz) | N | Watts 007M3QT 3/4" (H & VU) | (N),G,H,I,J,K,L,M,O,P,Q,T
DCDA | Watts | 757DCDAGV | 8 | VU | 2007-03-09 | 2022-03-09 | N | 9 | (zzz) | N | Watts 007M3QT 3/4" (H & VU) | (N),G,H,I,J,K,L,M,O,P,Q,T
DCDA | Watts | 757DCDAGV | 10 | H | 2009-09-17 | 2024-09-17 | N | 9 | (zzz) | N | Watts 007M3QT 3/4" (H), Ames 2000 BM3 (H) | (N),G,H,I,J,K,L,M,O,P,Q,T
DCDA | Watts | 757DCDAGV | 10 | VU | 2009-09-17 | 2024-09-17 | N | 9 | (zzz) | N | Watts 007M3QT 3/4" (V), Ames 2000 BM3 (V) | (N),G,H,I,J,K,L,M,O,P,Q,T
DCDA | Watts | 757NDCDABF | 2.5 | VUVD | 2009-04-07 | 2024-04-07 | N | 9 | (yyy) | N | Watts 007M3QT 3/4" (H) | (N),G,H,I,J,K,L,M,O,P,Q,T
DCDA | Watts | 757NDCDABF | 3 | VUVD | 2009-04-07 | 2024-04-07 | N | 9 | (yyy) | N | Watts 007M3QT 3/4" (H) | (N),G,H,I,J,K,L,M,O,P,Q,T
DCDA | Watts | 757NDCDABF | 4 | VUVD | 2009-04-07 | 2024-04-07 | N | 9 | (yyy) | N | Watts 007M3QT 3/4" (H) | (N),G,H,I,J,K,L,M,O,P,Q,T
DCDA | Watts | 757NDCDABF | 6 | VUVD | 2009-04-07 | 2024-04-07 | N | 9 | (yyy) | N | Watts 007M3QT 3/4" (H) | (N),G,H,I,J,K,L,M,O,P,Q,T
DCDA | Watts | 757NDCDABF | 8 | VUVD | 2013-01-03 | 2022-01-03 | N | 9 | (yyy) | N | Watts 007M3QT 3/4" (H) | (N),G,H,I,J,K,L,M,O,P,Q,T
DCDA | Watts | 757NDCDABF | 10 | VUVD | 2013-05-28 | 2022-05-28 | N | 9 | (yyy) | N | Watts 007M3QT 3/4" (H), Ames 2000BM3 3/4" (H) | (N), H,I,J,K,L,M,N,O,P,Q
DCDA | Watts | 757NDCDAGV | 2.5 | VUVD | 2009-04-07 | 2024-04-07 | N | 9 | (zzz) | N | Watts 007M3QT 3/4" (H) | (N),G,H,I,J,K,L,M,O,P,Q,T
DCDA | Watts | 757NDCDAGV | 3 | VUVD | 2009-04-07 | 2024-04-07 | N | 9 | (zzz) | N | Watts 007M3QT 3/4" (H) | (N),G,H,I,J,K,L,M,O,P,Q,T
DCDA | Watts | 757NDCDAGV | 4 | VUVD | 2009-04-07 | 2024-04-07 | N | 9 | (zzz) | N | Watts 007M3QT 3/4" (H) | (N),G,H,I,J,K,L,M,O,P,Q,T
DCDA | Watts | 757NDCDAGV | 6 | VUVD | 2009-04-07 | 2024-04-07 | N | 9 | (zzz) | N | Watts 007M3QT 3/4" (H) | (N),G,H,I,J,K,L,M,O,P,Q,T
DCDA | Watts | 757NDCDAGV | 8 | VUVD | 2013-01-03 | 2022-01-03 | N | 9 | (zzz) | N | Watts 007M3QT 3/4" (H) | (N),G,H,I,J,K,L,M,O,P,Q,T
DCDA | Watts | 757NDCDAGV | 10 | VUVD | 2013-05-28 | 2022-05-28 | N | 9 | (zzz) | N | Watts 007M3QT 3/4" (H), Ames 2000BM3 3/4" (H) | (N), H,I,J,K,L,M,N,O,P,Q
DCDA | Watts | 767aDCDABF | 2.5 | H | 2003-11-06 | 2024-11-06 | N | 9 | (yyy) | Y | Watts 007M3QT 3/4" (H) | (N),G,H,I,J,K,L,M,O,P,Q,T
DCDA | Watts | 767aDCDABF | 2.5 | VU | 2003-11-06 | 2024-11-06 | N | 9 | (yyy) | Y | Watts 007M3QT 3/4" (VU) | (N),G,H,I,J,K,L,M,O,P,Q,T
DCDA | Watts | 767aDCDABF | 3 | H | 2003-11-06 | 2024-11-06 | N | 9 | (yyy) | Y | Watts 007M3QT 3/4" (H) | (N),G,H,I,J,K,L,M,O,P,Q,T
DCDA | Watts | 767aDCDABF | 3 | VU | 2003-11-06 | 2024-11-06 | N | 9 | (yyy) | Y | Watts 007M3QT 3/4" (VU) | (N),G,H,I,J,K,L,M,O,P,Q,T
DCDA | Watts | 767aDCDABF | 4 | H | 2006-08-30 | 2024-08-30 | N | 9 | (yyy) | Y | Watts 007M3QT 3/4" (VU) | (N),G,H,I,J,K,L,M,O,P,Q,T
DCDA | Watts | 767aDCDABF | 4 | VU | 2005-01-18 | 2023-01-18 | N | 9 | (yyy) | Y | Watts 007M3QT 3/4" (VU) | (N),G,H,I,J,K,L,M,O,P,Q,T
DCDA | Watts | 767aDCDAGV | 2.5 | H | 2003-11-06 | 2024-11-06 | N | 9 | (zzz) | Y | Watts 007M3QT 3/4" (H) | (N),G,H,I,J,K,L,M,O,P,Q,T
DCDA | Watts | 767aDCDAGV | 2.5 | VU | 2003-11-06 | 2024-11-06 | N | 9 | (zzz) | Y | Watts 007M3QT 3/4" (VU) | (N),G,H,I,J,K,L,M,O,P,Q,T
DCDA | Watts | 767aDCDAGV | 3 | H | 2003-11-06 | 2024-11-06 | N | 9 | (zzz) | Y | Watts 007M3QT 3/4" (H) | (N),G,H,I,J,K,L,M,O,P,Q,T
DCDA | Watts | 767aDCDAGV | 3 | VU | 2003-11-06 | 2024-11-06 | N | 9 | (zzz) | Y | Watts 007M3QT 3/4" (VU) | (N),G,H,I,J,K,L,M,O,P,Q,T
DCDA | Watts | 767aDCDAGV | 4 | H | 2003-11-06 | 2024-11-06 | N | 9 | (zzz) | Y | Watts 007M3QT 3/4" (H) | (N),G,H,I,J,K,L,M,O,P,Q,T
DCDA | Watts | 767aDCDAGV | 4 | VU | 2005-01-18 | 2023-01-18 | N | 9 | (zzz) | Y | Watts 007M3QT 3/4" (VU) | (N),G,H,I,J,K,L,M,O,P,Q,T
DCDA | Watts | 767DCDABF | 2.5 | H | 2005-10-04 | 2023-10-04 | N | 9 | (yyy) | N | Watts 007M3QT 3/4" (H) | (N),G,H,I,J,K,L,M,O,P,Q,T
DCDA | Watts | 767DCDABF | 2.5 | VU | 2005-10-04 | 2023-10-04 | N | 9 | (yyy) | N | Watts 007M3QT 3/4" (V) | (N),G,H,I,J,K,L,M,O,P,Q,T
DCDA | Watts | 767DCDABF | 3 | H | 2005-10-04 | 2023-10-04 | N | 9 | (yyy) | N | Watts 007M3QT 3/4" (H) | (N),G,H,I,J,K,L,M,O,P,Q,T
DCDA | Watts | 767DCDABF | 3 | VU | 2005-10-04 | 2023-10-04 | N | 9 | (yyy) | N | Watts 007M3QT 3/4" (V) | (N),G,H,I,J,K,L,M,O,P,Q,T
DCDA | Watts | 767DCDABF | 4 | H | 2007-03-19 | 2022-03-23 | N | 9 | (yyy) | N | Watts 007M3QT 3/4" (H ) | (N),G,H,I,J,K,L,M,O,P,Q,T
DCDA | Watts | 767DCDABF | 4 | VU | 2007-03-19 | 2022-03-23 | N | 9 | (yyy) | N | Watts 007M3QT 3/4" (VU) | (N),G,H,I,J,K,L,M,O,P,Q,T
DCDA | Watts | 767DCDABF | 6 | H | 2007-03-09 | 2022-03-09 | N | 9 | (yyy) | N | Watts 007M3QT 3/4" (H & VU) | (N),G,H,I,J,K,L,M,O,P,Q,T
DCDA | Watts | 767DCDABF | 6 | VU | 2007-03-09 | 2022-03-09 | N | 9 | (yyy) | N | Watts 007M3QT 3/4" (H & VU) | (N),G,H,I,J,K,L,M,O,P,Q,T
DCDA | Watts | 767DCDABF | 8 | H | 2009-09-17 | 2024-09-17 | N | 9 | (yyy) | N | Watts 007M3QT 3/4" (H), Ames 2000 BM3 (H) | (N),G,H,I,J,K,L,M,O,P,Q,T
DCDA | Watts | 767DCDABF | 8 | VU | 2009-09-17 | 2024-09-17 | N | 9 | (yyy) | N | Watts 007M3QT 3/4" (V), Ames 2000 BM3 (V) | (N),G,H,I,J,K,L,M,O,P,Q,T
DCDA | Watts | 767DCDABF | 10 | H | 2009-09-17 | 2024-09-17 | N | 9 | (yyy) | N | Watts 007M3QT 3/4" (H), Ames 2000 BM3 (H) | (N),G,H,I,J,K,L,M,O,P,Q,T
DCDA | Watts | 767DCDABF | 10 | VU | 2009-09-17 | 2024-09-17 | N | 9 | (yyy) | N | Watts 007M3QT 3/4" (V), Ames 2000 BM3 (V) | (N),G,H,I,J,K,L,M,O,P,Q,T
DCDA | Watts | 767DCDAGV | 2.5 | H | 2005-10-04 | 2023-10-04 | N | 9 | (zzz) | N | Watts 007M3QT 3/4" (H) | (N),G,H,I,J,K,L,M,O,P,Q,T
DCDA | Watts | 767DCDAGV | 2.5 | VU | 2005-10-04 | 2023-10-04 | N | 9 | (zzz) | N | Watts 007M3QT 3/4" (V) | (N),G,H,I,J,K,L,M,O,P,Q,T
DCDA | Watts | 767DCDAGV | 3 | H | 2005-10-04 | 2023-10-04 | N | 9 | (zzz) | N | Watts 007M3QT 3/4" (H) | (N),G,H,I,J,K,L,M,O,P,Q,T
DCDA | Watts | 767DCDAGV | 3 | VU | 2005-10-04 | 2023-10-04 | N | 9 | (zzz) | N | Watts 007M3QT 3/4" (V) | (N),G,H,I,J,K,L,M,O,P,Q,T
DCDA | Watts | 767DCDAGV | 4 | H | 2007-03-19 | 2022-03-23 | N | 9 | (zzz) | N | Watts 007M3QT 3/4" (H ) | (N),G,H,I,J,K,L,M,O,P,Q,T
DCDA | Watts | 767DCDAGV | 4 | VU | 2007-03-19 | 2022-03-23 | N | 9 | (zzz) | N | Watts 007M3QT 3/4" (VU) | (N),G,H,I,J,K,L,M,O,P,Q,T
DCDA | Watts | 767DCDAGV | 6 | H | 2007-03-09 | 2022-03-09 | N | 9 | (zzz) | N | Watts 007M3QT 3/4" (H & VU) | (N),G,H,I,J,K,L,M,O,P,Q,T
DCDA | Watts | 767DCDAGV | 6 | VU | 2007-03-09 | 2022-03-09 | N | 9 | (zzz) | N | Watts 007M3QT 3/4" (H & VU) | (N),G,H,I,J,K,L,M,O,P,Q,T
DCDA | Watts | 767DCDAGV | 8 | H | 2009-09-17 | 2024-09-17 | N | 9 | (zzz) | N | Watts 007M3QT 3/4" (H), Ames 2000 BM3 (H) | (N),G,H,I,J,K,L,M,O,P,Q,T
DCDA | Watts | 767DCDAGV | 8 | VU | 2009-09-17 | 2024-09-17 | N | 9 | (zzz) | N | Watts 007M3QT 3/4" (V), Ames 2000 BM3 (V) | (N),G,H,I,J,K,L,M,O,P,Q,T
DCDA | Watts | 767DCDAGV | 10 | H | 2009-09-17 | 2024-09-17 | N | 9 | (zzz) | N | Watts 007M3QT 3/4" (H), Ames 2000 BM3 (H) | (N),G,H,I,J,K,L,M,O,P,Q,T
DCDA | Watts | 767DCDAGV | 10 | VU | 2009-09-17 | 2024-09-17 | N | 9 | (zzz) | N | Watts 007M3QT 3/4" (V), Ames 2000 BM3 (V) | (N),G,H,I,J,K,L,M,O,P,Q,T
DCDA | Watts | 767NDCDABF | 2.5 | VUVD | 2009-04-07 | 2024-04-07 | N | 9 | (yyy) | N | Watts 007M3QT 3/4" (H) | (N),G,H,I,J,K,L,M,O,P,Q,T
DCDA | Watts | 767NDCDABF | 3 | VUVD | 2009-04-07 | 2024-04-07 | N | 9 | (yyy) | N | Watts 007M3QT 3/4" (H) | (N),G,H,I,J,K,L,M,O,P,Q,T
DCDA | Watts | 767NDCDABF | 4 | VUVD | 2009-04-07 | 2024-04-07 | N | 9 | (yyy) | N | Watts 007M3QT 3/4" (H) | (N),G,H,I,J,K,L,M,O,P,Q,T
DCDA | Watts | 767NDCDABF | 6 | VUVD | 2013-01-03 | 2022-01-03 | N | 9 | (yyy) | N | Watts 007M3QT 3/4" (H) | (N),G,H,I,J,K,L,M,O,P,Q,T
DCDA | Watts | 767NDCDABF | 8 | VUVD | 2013-05-28 | 2022-05-28 | N | 9 | (yyy) | N | Watts 007M3QT 3/4" (H), Ames 2000BM3 3/4" (H) | (N), H,I,J,K,L,M,N,O,P,Q
DCDA | Watts | 767NDCDABF | 10 | VUVD | 2013-05-28 | 2022-05-28 | N | 9 | (yyy) | N | Watts 007M3QT 3/4" (H), Ames 2000BM3 3/4" (H) | (N), H,I,J,K,L,M,N,O,P,Q
DCDA | Watts | 767NDCDAGV | 2.5 | VUVD | 2009-04-07 | 2024-04-07 | N | 9 | (zzz) | N | Watts 007M3QT 3/4" (H) | (N),G,H,I,J,K,L,M,O,P,Q,T
DCDA | Watts | 767NDCDAGV | 3 | VUVD | 2009-04-07 | 2024-04-07 | N | 9 | (zzz) | N | Watts 007M3QT 3/4" (H) | (N),G,H,I,J,K,L,M,O,P,Q,T
DCDA | Watts | 767NDCDAGV | 4 | VUVD | 2009-04-07 | 2024-04-07 | N | 9 | (zzz) | N | Watts 007M3QT 3/4" (H) | (N),G,H,I,J,K,L,M,O,P,Q,T
DCDA | Watts | 767NDCDAGV | 6 | VUVD | 2013-01-03 | 2022-01-03 | N | 9 | (zzz) | N | Watts 007M3QT 3/4" (H) | (N),G,H,I,J,K,L,M,O,P,Q,T
DCDA | Watts | 767NDCDAGV | 8 | VUVD | 2013-05-28 | 2022-05-28 | N | 9 | (zzz) | N | Watts 007M3QT 3/4" (H), Ames 2000BM3 3/4" (H) | (N), H,I,J,K,L,M,N,O,P,Q
DCDA | Watts | 767NDCDAGV | 10 | VUVD | 2013-05-28 | 2022-05-28 | N | 9 | (zzz) | N | Watts 007M3QT 3/4" (H), Ames 2000BM3 3/4" (H) | (N), H,I,J,K,L,M,N,O,P,Q
DCDA | Watts | 770DCDA | 4 | H | 1992-05-20 | 2022-05-20 | N | 8 | pp,hh,mm,uu,zz | Y | Watts 007M1QT 3/4" (H) | (H),A,B,C,D,E,F,G,I,J,K,L,M,N,O,P,Q,T
DCDA | Watts | 770DCDA | 8 | H | 1993-01-13 | 2023-01-13 | N | 8 | oo,gg,hh,ll,mm,pp,tt,uu | Y | Watts 007M1QT 3/4" (H) | (N),D,E,F,G,H,I,J,K,L,M,O,P,Q,T
DCDA | Watts | 772DCDA | 4 | H | 1992-08-01 | 2022-08-01 | N | 8 | oo | Y | Watts 007M1QT 3/4" (H) | (H),A,B,C,D,E,F,G,I,J,K,L,M,N,O,P,Q,T
DCDA | Watts | 772DCDA | 10 | H | 1993-01-13 | 2023-01-13 | N | 8 | oo | Y | Watts 007M1QT 3/4" (H) | (H),A,B,C,D,E,F,G,I,J,K,L,M,N,O,P,Q,T
DCDA | Watts | 774DCDA | 2.5 | H | 1995-05-24 | 2023-01-16 | N | 8 | (uu),ee,ff,gg,hh,ll,mm,oo,pp,tt,ccc,ddd,ffff,gggg | N | Watts 007M2QT 3/4: (H), Ames 2000B 3/4" (H) | (M),A,B,C,D,E,F,G,H,I,J,K,L,N,O,P,Q,T
DCDA | Watts | 774DCDA | 3 | H | 1995-05-24 | 2023-01-16 | N | 8 | (uu),ee,ff,gg,hh,ll,mm,oo,pp,tt,ccc,ddd,ffff,gggg | N | Watts 007M2QT 3/4: (H), Ames 2000B 3/4" (H) | (M),A,B,C,D,E,F,G,H,I,J,K,L,N,O,P,Q,T
DCDA | Watts | 774DCDA | 4 | H | 1995-05-24 | 2023-01-16 | N | 8 | (uu),ee,ff,gg,hh,ll,mm,oo,pp,tt,ccc,ddd,ffff,gggg | N | Watts 007M2QT 3/4: (H), Ames 2000B 3/4" (H) | (M),A,B,C,D,E,F,G,H,I,J,K,L,N,O,P,Q,T
DCDA | Watts | 774DCDA | 6 | H | 1992-09-09 | 2022-09-09 | N | 8 | (uu),ee,ff,gg,hh,ll,mm,oo,pp,tt,ccc,ddd,ffff,gggg | N | Watts 007M1QT 3/4" (H)), Watts 007M3QT 3/4" (H) | (M),A,B,C,D,E,F,G,H,I,J,K,L,N,O,P,Q,T
DCDA | Watts | 774DCDA | 8 | H | 1996-09-16 | 2023-09-16 | N | 8 | (mm),ee,ff,gg,hh,ll,oo,pp,tt,uu,ccc,ddd,ffff,gggg | N | Watts 007M2QT 3/4: (H), Ames 2000B 3/4" (H) | (M),A,B,C,D,E,F,G,H,I,J,K,L,N,O,P,Q,T
DCDA | Watts | 774DCDA | 10 | H | 2001-02-16 | 2022-02-16 | N | 8 | (ll),mm,ffff,gggg | N | Watts 007M2QT 3/4: (H), Ames 2000B 3/4" (H) | (J),C,E,F,G,H,I,K,L,M,N,O,P,Q,T
DCDA | Watts | 774DCDA | 12 | H | 2010-02-18 | 2022-02-18 | N | 9 | (mm), ll | N | Ames 2000BM3 3/4" (H); Watts 007M3QT 3/4" (H) | (N),H,I,J,K,L,M,O,P,Q
DCDA | Watts | 774DCDA | 12 | VU | 2011-03-21 | 2023-03-21 | N | 9 | (mm), ll | N | Ames 2000BM3 3/4" (H); Watts 007M3QT 3/4" (H) | (N),H,I,J,K,L,M,O,P,Q
DCDA | Watts | 774DCDA-1 | 12 | H | 2010-02-18 | 2022-02-18 | N | 9 | (mm), ll | N | Ames 200B 3/4" (H); Watts 719QT 3/4" (H) | (N),H,I,J,K,L,M,O,P,Q
DCDA | Watts | 774DCDA-1 | 12 | VU | 2011-03-21 | 2023-03-21 | N | 9 | (mm), ll | N | Ames 200B 3/4" (VU); Watts 719QT 3/4" (VU) | (N), H,I,J,K,L,M,O,P,Q
DCDA | Watts | 774XDCDA | 2.5 | H | 1996-09-10 | 2023-09-10 | N | 8 | (mm),ee,ff,gg,hh,ll,oo,pp,tt,uu,ccc,ddd,ffff,gggg | Y | Watts 007M2QT 3/4: (H), Ames 2000B 3/4" (H) | (M),N,O,P,Q
DCDA | Watts | 774XDCDA | 6 | H | 1995-05-24 | 2022-05-24 | N | 8 | (uu),ee,ff,gg,hh,ll,mm,oo,pp,tt,uu,ccc,ddd,ffff,gggg | Y | Watts 007M2QT 3/4: (H), Ames 2000B 3/4" (H) | (M),A,B,C,D,E,F,G,H,I,J,K,L,N,O,P,Q,T
DCDA | Watts | 774XDCDA | 8 | H | 1992-09-09 | 2022-09-09 | N | 8 | (uu),ee,ff,gg,hh,ll,mm,oo,pp,tt,ccc,ddd,ffff,gggg | Y | Watts 007M1QT 3/4" (H) | (M),A,B,C,D,E,F,G,H,I,J,K,L,N,O,P,Q,T
DCDA | Watts | LF757DCDABF | 2.5 | H | 2014-01-08 | 2023-01-08 | Y | 9 | (yyy) | N | Watts LF007M3QT 3/4" (H) | (O) | Lead free compliant version identified with NSF61 mark on meter
DCDA | Watts | LF757DCDABF | 2.5 | VU | 2014-01-08 | 2023-01-08 | Y | 9 | (yyy) | N | Watts LF007M3QT 3/4" (VU) | (O) | Lead free compliant version identified with NSF61 mark on meter
DCDA | Watts | LF757DCDABF | 3 | H | 2014-01-08 | 2023-01-08 | Y | 9 | (yyy) | N | Watts LF007M3QT 3/4" (H) | (O) | Lead free compliant version identified with NSF61 mark on meter
DCDA | Watts | LF757DCDABF | 3 | VU | 2014-01-08 | 2023-01-08 | Y | 9 | (yyy) | N | Watts LF007M3QT 3/4" (VU) | (O) | Lead free compliant version identified with NSF61 mark on meter
DCDA | Watts | LF757DCDABF | 4 | H | 2014-01-08 | 2023-01-08 | Y | 9 | (yyy) | N | Watts LF007M3QT 3/4" (H) | (O) | Lead free compliant version identified with NSF61 mark on meter
DCDA | Watts | LF757DCDABF | 4 | VU | 2014-01-08 | 2023-01-08 | Y | 9 | (yyy) | N | Watts LF007M3QT 3/4" (VU) | (O) | Lead free compliant version identified with NSF61 mark on meter
DCDA | Watts | LF757DCDABF | 6 | H | 2014-01-08 | 2023-01-08 | Y | 9 | (yyy) | N | Watts LF007M3QT 3/4" (H) | (O) | Lead free compliant version identified with NSF61 mark on meter
DCDA | Watts | LF757DCDABF | 6 | VU | 2014-01-08 | 2023-01-08 | Y | 9 | (yyy) | N | Watts LF007M3QT 3/4" (VU) | (O) | Lead free compliant version identified with NSF61 mark on meter
DCDA | Watts | LF757DCDABF | 8 | H | 2014-01-08 | 2023-01-08 | Y | 9 | (yyy) | N | Watts LF007M3QT 3/4" (H) | (O) | Lead free compliant version identified with NSF61 mark on meter
DCDA | Watts | LF757DCDABF | 8 | VU | 2014-01-08 | 2023-01-08 | Y | 9 | (yyy) | N | Watts LF007M3QT 3/4" (VU) | (O) | Lead free compliant version identified with NSF61 mark on meter
DCDA | Watts | LF757DCDABF | 10 | H | 2014-01-08 | 2023-01-08 | Y | 9 | (yyy) | N | Watts LF007M3QT 3/4" (H) | (O) | Lead free compliant version identified with NSF61 mark on meter
DCDA | Watts | LF757DCDABF | 10 | VU | 2014-01-08 | 2023-01-08 | Y | 9 | (yyy) | N | Watts LF007M3QT 3/4" (VU) | (O) | Lead free compliant version identified with NSF61 mark on meter
DCDA | Watts | LF757DCDAGV | 2.5 | H | 2014-01-08 | 2023-01-08 | Y | 9 | (zzz) | N | Watts LF007M3QT 3/4" (H) | (O) | Lead free compliant version identified with NSF61 mark on meter
DCDA | Watts | LF757DCDAGV | 2.5 | VU | 2014-01-08 | 2023-01-08 | Y | 9 | (zzz) | N | Watts LF007M3QT 3/4" (VU) | (O) | Lead free compliant version identified with NSF61 mark on meter
DCDA | Watts | LF757DCDAGV | 3 | H | 2014-01-08 | 2023-01-08 | Y | 9 | (zzz) | N | Watts LF007M3QT 3/4" (H) | (O) | Lead free compliant version identified with NSF61 mark on meter
DCDA | Watts | LF757DCDAGV | 3 | VU | 2014-01-08 | 2023-01-08 | Y | 9 | (zzz) | N | Watts LF007M3QT 3/4" (VU) | (O) | Lead free compliant version identified with NSF61 mark on meter
DCDA | Watts | LF757DCDAGV | 4 | H | 2014-01-08 | 2023-01-08 | Y | 9 | (zzz) | N | Watts LF007M3QT 3/4" (H) | (O) | Lead free compliant version identified with NSF61 mark on meter
DCDA | Watts | LF757DCDAGV | 4 | VU | 2014-01-08 | 2023-01-08 | Y | 9 | (zzz) | N | Watts LF007M3QT 3/4" (VU) | (O) | Lead free compliant version identified with NSF61 mark on meter
DCDA | Watts | LF757DCDAGV | 6 | H | 2014-01-08 | 2023-01-08 | Y | 9 | (zzz) | N | Watts LF007M3QT 3/4" (H) | (O) | Lead free compliant version identified with NSF61 mark on meter
DCDA | Watts | LF757DCDAGV | 6 | VU | 2014-01-08 | 2023-01-08 | Y | 9 | (zzz) | N | Watts LF007M3QT 3/4" (VU) | (O) | Lead free compliant version identified with NSF61 mark on meter
DCDA | Watts | LF757DCDAGV | 8 | H | 2014-01-08 | 2023-01-08 | Y | 9 | (zzz) | N | Watts LF007M3QT 3/4" (H) | (O) | Lead free compliant version identified with NSF61 mark on meter
DCDA | Watts | LF757DCDAGV | 8 | VU | 2014-01-08 | 2023-01-08 | Y | 9 | (zzz) | N | Watts LF007M3QT 3/4" (VU) | (O) | Lead free compliant version identified with NSF61 mark on meter
DCDA | Watts | LF757DCDAGV | 10 | H | 2014-01-08 | 2023-01-08 | Y | 9 | (zzz) | N | Watts LF007M3QT 3/4" (H) | (O) | Lead free compliant version identified with NSF61 mark on meter
DCDA | Watts | LF757DCDAGV | 10 | VU | 2014-01-08 | 2023-01-08 | Y | 9 | (zzz) | N | Watts LF007M3QT 3/4" (VU) | (O) | Lead free compliant version identified with NSF61 mark on meter
DCDA | Watts | LF757NDCDABF | 2.5 | VUVD | 2014-01-08 | 2023-01-08 | Y | 9 | (yyy) | N | Watts LF007M3QT 3/4" (H) | (O) | Lead free compliant version identified with NSF61 mark on meter
DCDA | Watts | LF757NDCDABF | 3 | VUVD | 2014-01-08 | 2023-01-08 | Y | 9 | (yyy) | N | Watts LF007M3QT 3/4" (H) | (O) | Lead free compliant version identified with NSF61 mark on meter
DCDA | Watts | LF757NDCDABF | 4 | VUVD | 2014-01-08 | 2023-01-08 | Y | 9 | (yyy) | N | Watts LF007M3QT 3/4" (H) | (O) | Lead free compliant version identified with NSF61 mark on meter
DCDA | Watts | LF757NDCDABF | 6 | VUVD | 2014-01-08 | 2023-01-08 | Y | 9 | (yyy) | N | Watts LF007M3QT 3/4" (H) | (O) | Lead free compliant version identified with NSF61 mark on meter
DCDA | Watts | LF757NDCDABF | 8 | VUVD | 2014-01-08 | 2023-01-08 | Y | 9 | (yyy) | N | Watts LF007M3QT 3/4" (H) | (O) | Lead free compliant version identified with NSF61 mark on meter
DCDA | Watts | LF757NDCDABF | 10 | VUVD | 2014-01-08 | 2023-01-08 | Y | 9 | (yyy) | N | Watts LF007M3QT 3/4" (H) | (O) | Lead free compliant version identified with NSF61 mark on meter
DCDA | Watts | LF757NDCDAGV | 2.5 | VUVD | 2014-01-08 | 2023-01-08 | Y | 9 | (zzz) | N | Watts LF007M3QT 3/4" (H) | (O) | Lead free compliant version identified with NSF61 mark on meter
DCDA | Watts | LF757NDCDAGV | 3 | VUVD | 2014-01-08 | 2023-01-08 | Y | 9 | (zzz) | N | Watts LF007M3QT 3/4" (H) | (O) | Lead free compliant version identified with NSF61 mark on meter
DCDA | Watts | LF757NDCDAGV | 4 | VUVD | 2014-01-08 | 2023-01-08 | Y | 9 | (zzz) | N | Watts LF007M3QT 3/4" (H) | (O) | Lead free compliant version identified with NSF61 mark on meter
DCDA | Watts | LF757NDCDAGV | 6 | VUVD | 2014-01-08 | 2023-01-08 | Y | 9 | (zzz) | N | Watts LF007M3QT 3/4" (H) | (O) | Lead free compliant version identified with NSF61 mark on meter
DCDA | Watts | LF757NDCDAGV | 8 | VUVD | 2014-01-08 | 2023-01-08 | Y | 9 | (zzz) | N | Watts LF007M3QT 3/4" (H) | (O) | Lead free compliant version identified with NSF61 mark on meter
DCDA | Watts | LF757NDCDAGV | 10 | VUVD | 2014-01-08 | 2023-01-08 | Y | 9 | (zzz) | N | Watts LF007M3QT 3/4" (H) | (O) | Lead free compliant version identified with NSF61 mark on meter
DCDA | Wilkins | 350ADA | 2.5 | H | 2005-06-22 | 2023-06-22 | N | 9 | (qqq),ttt,yyy,zzz,uuuu,vvvv,xxxx,yyyy,kkkkk,lllll,iiiiii,jjjjjj,llllll,mmmmmm | N | Wilkins 950XLD 3/4" (H) | (M),A,B,C,D,E,F,G,H,I,J,K,L,N,O,P,Q,T
DCDA | Wilkins | 350ADA | 2.5 | H | 2014-02-18 | 2023-02-18 | Y | 9 | (qqq),ttt,www,yyy,xxxx,yyyy,kkkkk,lllll,llllll,mmmmmm | N | Wilkins 950XLD 3/4" (H) | (O), M | Lead free compliant version: Starting Serial # V39030; By-pass Assembly Starting Serial # 3863325 and identified with NSF61 mark on meter
DCDA | Wilkins | 350ADA | 2.5 | VU | 2005-06-22 | 2023-06-22 | N | 9 | (qqq),ttt,yyy,zzz,uuuu,vvvv,xxxx,yyyy,kkkkk,lllll,iiiiii,jjjjjj,llllll,mmmmmm | N | Wilkins 950XLD 3/4" (VU) | (M),A,B,C,D,E,F,G,H,I,J,K,L,N,O,P,Q,T
DCDA | Wilkins | 350ADA | 2.5 | VU | 2014-02-18 | 2023-02-18 | Y | 9 | (qqq),ttt,www,yyy,xxxx,yyyy,kkkkk,lllll,llllll,mmmmmm | N | Wilkins 950XLD 3/4" (VU) | (O), M | Lead free compliant version: Starting Serial # V39030; By-pass Assembly Starting Serial # 3863325 and identified with NSF61 mark on meter
DCDA | Wilkins | 350ADA | 3 | H | 2005-06-22 | 2023-06-22 | N | 9 | (qqq),ttt,yyy,zzz,uuuu,vvvv,xxxx,yyyy,kkkkk,lllll,iiiiii,jjjjjj,llllll,mmmmmm | N | Wilkins 950XLD 3/4" (H) | (M),A,B,C,D,E,F,G,H,I,J,K,L,N,O,P,Q,T
DCDA | Wilkins | 350ADA | 3 | H | 2014-02-18 | 2023-02-18 | Y | 9 | (qqq),ttt,www,yyy,xxxx,yyyy,kkkkk,lllll,llllll,mmmmmm | N | Wilkins 950XLD 3/4" (H) | (O), M | Lead free compliant version: Starting Serial # V39030; By-pass Assembly Starting Serial # 3863325 and identified with NSF61 mark on meter
DCDA | Wilkins | 350ADA | 3 | VU | 2005-06-22 | 2023-06-22 | N | 9 | (qqq),ttt,yyy,zzz,uuuu,vvvv,xxxx,yyyy,kkkkk,lllll,iiiiii,jjjjjj,llllll,mmmmmm | N | Wilkins 950XLD 3/4" (VU) | (M),A,B,C,D,E,F,G,H,I,J,K,L,N,O,P,Q,T
DCDA | Wilkins | 350ADA | 3 | VU | 2014-02-18 | 2023-02-18 | Y | 9 | (qqq),ttt,www,yyy,xxxx,yyyy,kkkkk,lllll,llllll,mmmmmm | N | Wilkins 950XLD 3/4" (VU) | (O), M | Lead free compliant version: Starting Serial # V39030; By-pass Assembly Starting Serial # 3863325 and identified with NSF61 mark on meter
DCDA | Wilkins | 350ADA | 4 | H | 2004-03-16 | 2022-03-16 | N | 9 | (qqq),ttt,www,yyy,zzz,eeee,uuuu,vvvv,xxxx,yyyy,kkkkk,lllll,iiiiii,jjjjjj,llllll,mmmmmm | N | Wilkins 950XLD 3/4" (H) | (M),A,B,C,D,E,F,G,H,I,J,K,L,N,O,P,Q,T
DCDA | Wilkins | 350ADA | 4 | H | 2014-02-18 | 2023-02-18 | Y | 9 | (qqq),ttt,www,yyy,xxxx,yyyy,kkkkk,lllll,llllll,mmmmmm | N | Wilkins 950XLD 3/4" (H) | (O), M | Lead free compliant version: Starting Serial # V39030; By-pass Assembly Starting Serial # 3863325 and identified with NSF61 mark on meter
DCDA | Wilkins | 350ADA | 4 | VU | 2004-03-16 | 2022-03-16 | N | 9 | (qqq),ttt,www,yyy,zzz,eeee,uuuu,vvvv,xxxx,yyyy,kkkkk,lllll,iiiiii,jjjjjj,llllll,mmmmmm | N | Wilkins 950XLD 3/4" (VU) | (M),A,B,C,D,E,F,G,H,I,J,K,L,N,O,P,Q,T
DCDA | Wilkins | 350ADA | 4 | VU | 2014-02-18 | 2023-02-18 | Y | 9 | (qqq),ttt,www,yyy,xxxx,yyyy,kkkkk,lllll,llllll,mmmmmm | N | Wilkins 950XLD 3/4" (VU) | (O), M | Lead free compliant version: Starting Serial # V39030; By-pass Assembly Starting Serial # 3863325 and identified with NSF61 mark on meter
DCDA | Wilkins | 350ADA | 6 | H | 2003-11-25 | 2024-11-25 | N | 9 | (qqq),ttt,www,yyy,zzz,eeee,uuuu,vvvv,xxxx,yyyy,kkkkk,lllll,iiiiii,jjjjjj,llllll,mmmmmm | N | Wilkins 950XLD 3/4" (H) | (M),A,B,C,D,E,F,G,H,I,J,K,L,N,O,P,Q,T
DCDA | Wilkins | 350ADA | 6 | H | 2014-02-18 | 2023-02-18 | Y | 9 | (qqq),ttt,www,yyy,xxxx,yyyy,kkkkk,lllll,llllll,mmmmmm | N | Wilkins 950XLD 3/4" (H) | (O), M | Lead free compliant version: Starting Serial # V39030; By-pass Assembly Starting Serial # 3863325 and identified with NSF61 mark on meter
DCDA | Wilkins | 350ADA | 6 | VU | 2003-11-25 | 2024-11-25 | N | 9 | (qqq),ttt,www,yyy,zzz,eeee,uuuu,vvvv,xxxx,yyyy,kkkkk,lllll,iiiiii,jjjjjj,llllll,mmmmmm | N | Wilkins 950XLD 3/4" (VU) | (M),A,B,C,D,E,F,G,H,I,J,K,L,N,O,P,Q,T
DCDA | Wilkins | 350ADA | 6 | VU | 2014-02-18 | 2023-02-18 | Y | 9 | (qqq),ttt,www,yyy,xxxx,yyyy,kkkkk,lllll,llllll,mmmmmm | N | Wilkins 950XLD 3/4" (VU) | (O), M | Lead free compliant version: Starting Serial # V39030; By-pass Assembly Starting Serial # 3863325 and identified with NSF61 mark on meter
DCDA | Wilkins | 350ADA | 8 | H | 2004-02-12 | 2022-02-12 | N | 9 | (qqq),ttt,www,yyy,zzz,eeee,uuuu,vvvv,xxxx,yyyy,kkkkk,lllll,iiiiii,jjjjjj,llllll,mmmmmm | N | Wilkins 950XLD 3/4" (H) | (N),F,G,H,I,J,K,L,M,O,P,Q,T
DCDA | Wilkins | 350ADA | 8 | H | 2014-02-18 | 2023-02-18 | Y | 9 | (qqq),ttt,www,yyy,xxxx,yyyy,kkkkk,lllll,llllll,mmmmmm | N | Wilkins 950XLD 3/4" (H) | (O), M | Lead free compliant version: Starting Serial # V39030; By-pass Assembly Starting Serial # 3863325 and identified with NSF61 mark on meter
DCDA | Wilkins | 350ADA | 8 | VU | 2004-02-12 | 2022-02-12 | N | 9 | (qqq),ttt,www,yyy,zzz,eeee,uuuu,vvvv,xxxx,yyyy,kkkkk,lllll,iiiiii,jjjjjj,llllll,mmmmmm | N | Wilkins 950XLD 3/4" (VU) | (N),F,G,H,I,J,K,L,M,O,P,Q,T
DCDA | Wilkins | 350ADA | 8 | VU | 2014-02-18 | 2023-02-18 | Y | 9 | (qqq),ttt,www,yyy,xxxx,yyyy,kkkkk,lllll,llllll,mmmmmm | N | Wilkins 950XLD 3/4" (VU) | (O), M | Lead free compliant version: Starting Serial # V39030; By-pass Assembly Starting Serial # 3863325 and identified with NSF61 mark on meter
DCDA | Wilkins | 350ADA | 10 | H | 2006-04-06 | 2024-04-06 | N | 9 | (qqq),ttt,yyy,uuuu,vvvv,xxxx,yyyy,kkkkk,lllll,iiiiii,jjjjjj,llllll,mmmmmm | N | Wilkins 950XLD 3/4" (H) | (N),F,G,H,I,J,K,L,M,O,P,Q,T
DCDA | Wilkins | 350ADA | 10 | H | 2014-02-18 | 2023-02-18 | Y | 9 | (qqq),ttt,www,yyy,xxxx,yyyy,kkkkk,lllll,llllll,mmmmmm | N | Wilkins 950XLD 3/4" (H) | (O), M | Lead free compliant version: Starting Serial # V39030; By-pass Assembly Starting Serial # 3863325 and identified with NSF61 mark on meter
DCDA | Wilkins | 350ADA | 10 | VU | 2006-04-06 | 2024-04-06 | N | 9 | (qqq),ttt,yyy,uuuu,vvvv,xxxx,yyyy,kkkkk,lllll,iiiiii,jjjjjj,llllll,mmmmmm | N | Wilkins 950XLD 3/4" (VU) | (N),F,G,H,I,J,K,L,M,O,P,Q,T
DCDA | Wilkins | 350ADA | 10 | VU | 2014-02-18 | 2023-02-18 | Y | 9 | (qqq),ttt,www,yyy,xxxx,yyyy,kkkkk,lllll,llllll,mmmmmm | N | Wilkins 950XLD 3/4" (VU) | (O), M | Lead free compliant version: Starting Serial # V39030; By-pass Assembly Starting Serial # 3863325 and identified with NSF61 mark on meter
DCDA | Wilkins | 350ADAR | 2.5 | H | 2010-06-16 | 2022-06-16 | N | 9 | (qqq),ttt,yyy,zzz,uuuu,vvvv,xxxx,yyyy,kkkkk,lllll,iiiiii,jjjjjj,llllll,mmmmmm | N | Wilkins 950XLD 3/4" (H) | (M),A,B,C,D,E,F,G,H,I,J,K,L,N,O,P,Q,T | Integral grooved spool between the #2 ck and #2 SOV - assembly length: min. 34 1/4" and max. 47 1/8"
DCDA | Wilkins | 350ADAR | 2.5 | H | 2014-02-18 | 2023-02-18 | Y | 9 | (qqq),ttt,www,yyy,xxxx,yyyy,kkkkk,lllll,llllll,mmmmmm | N | Wilkins 950XLD 3/4" (H) | (O), M | Integral grooved spool between the #2 ck and #2 SOV - assembly length: min. 34 1/4" and max. 47 1/8" and Lead free compliant version: Starting Serial # E00687; By-pass Assembly Starting Serial # 3863325 and identified with NSF61 mark on meter
DCDA | Wilkins | 350ADAR | 2.5 | VU | 2010-06-16 | 2022-06-16 | N | 9 | (qqq),ttt,yyy,zzz,uuuu,vvvv,xxxx,yyyy,kkkkk,lllll,iiiiii,jjjjjj,llllll,mmmmmm | N | Wilkins 950XLD 3/4" (VU) | (M),A,B,C,D,E,F,G,H,I,J,K,L,N,O,P,Q,T | Integral grooved spool between the #2 ck and #2 SOV - assembly length: min. 34 1/4" and max. 47 1/8"
DCDA | Wilkins | 350ADAR | 2.5 | VU | 2014-02-18 | 2023-02-18 | Y | 9 | (qqq),ttt,www,yyy,xxxx,yyyy,kkkkk,lllll,llllll,mmmmmm | N | Wilkins 950XLD 3/4" (VU) | (O), M | Integral grooved spool between the #2 ck and #2 SOV - assembly length: min. 34 1/4" and max. 47 1/8" and Lead free compliant version: Starting Serial # E00687; By-pass Assembly Starting Serial # 3863325 and identified with NSF61 mark on meter
DCDA | Wilkins | 350ADAR | 3 | H | 2010-06-16 | 2022-06-16 | N | 9 | (qqq),ttt,yyy,zzz,uuuu,vvvv,xxxx,yyyy,kkkkk,lllll,iiiiii,jjjjjj,llllll,mmmmmm | N | Wilkins 950XLD 3/4" (H) | (M),A,B,C,D,E,F,G,H,I,J,K,L,N,O,P,Q,T | Integral grooved spool between the #2 ck and #2 SOV - assembly length: min. 34 3/4" and max. 48 1/8"
DCDA | Wilkins | 350ADAR | 3 | H | 2014-02-18 | 2023-02-18 | Y | 9 | (qqq),ttt,www,yyy,xxxx,yyyy,kkkkk,lllll,llllll,mmmmmm | N | Wilkins 950XLD 3/4" (H) | (O), M | Integral grooved spool between the #2 ck and #2 SOV - assembly length: min. 34 3/4" and max. 48 1/8" and Lead free compliant version: Starting Serial # E00687; By-pass Assembly Starting Serial # 3863325 and identified with NSF61 mark on meter
DCDA | Wilkins | 350ADAR | 3 | VU | 2010-06-16 | 2022-06-16 | N | 9 | (qqq),ttt,yyy,zzz,uuuu,vvvv,xxxx,yyyy,kkkkk,lllll,iiiiii,jjjjjj,llllll,mmmmmm | N | Wilkins 950XLD 3/4" (VU) | (M),A,B,C,D,E,F,G,H,I,J,K,L,N,O,P,Q,T | Integral grooved spool between the #2 ck and #2 SOV - assembly length: min. 34 3/4" and max. 48 1/8"
DCDA | Wilkins | 350ADAR | 3 | VU | 2014-02-18 | 2023-02-18 | Y | 9 | (qqq),ttt,www,yyy,xxxx,yyyy,kkkkk,lllll,llllll,mmmmmm | N | Wilkins 950XLD 3/4" (VU) | (O), M | Integral grooved spool between the #2 ck and #2 SOV - assembly length: min. 34 3/4" and max. 48 1/8" and Lead free compliant version: Starting Serial # E00687; By-pass Assembly Starting Serial # 3863325 and identified with NSF61 mark on meter
DCDA | Wilkins | 350ADAR | 4 | H | 2010-03-25 | 2022-03-25 | N | 9 | (qqq),ttt,www,yyy,zzz,eeee,uuuu,vvvv,xxxx,yyyy,kkkkk,lllll,iiiiii,jjjjjj,llllll,mmmmmm | N | Wilkins 950XLD 3/4" (VU) | (M),A,B,C,D,E,F,G,H,I,J,K,L,N,O,P,Q,T | Integral grooved spool between the #2 ck and #2 SOV - assembly length: min. 35 3/4" and max. 62 1/4"
DCDA | Wilkins | 350ADAR | 4 | H | 2014-02-18 | 2023-02-18 | Y | 9 | (qqq),ttt,www,yyy,xxxx,yyyy,kkkkk,lllll,llllll,mmmmmm | N | Wilkins 950XLD 3/4" (VU) | (O), M | Integral grooved spool between the #2 ck and #2 SOV - assembly length: min. 35 3/4" and max. 62 1/4" and Lead free compliant version: Starting Serial # E00687; By-pass Assembly Starting Serial # 3863325 and identified with NSF61 mark on meter
DCDA | Wilkins | 350ADAR | 4 | VU | 2010-03-25 | 2022-03-25 | N | 9 | (qqq),ttt,www,yyy,zzz,eeee,uuuu,vvvv,xxxx,yyyy,kkkkk,lllll,iiiiii,jjjjjj,llllll,mmmmmm | N | Wilkins 950XLD 3/4" (H) | (M),A,B,C,D,E,F,G,H,I,J,K,L,N,O,P,Q,T | Integral grooved spool between the #2 ck and #2 SOV - assembly length: min. 35 3/4" and max. 62 1/4"
DCDA | Wilkins | 350ADAR | 4 | VU | 2014-02-18 | 2023-02-18 | Y | 9 | (qqq),ttt,www,yyy,xxxx,yyyy,kkkkk,lllll,llllll,mmmmmm | N | Wilkins 950XLD 3/4" (H) | (O), M | Integral grooved spool between the #2 ck and #2 SOV - assembly length: min. 35 3/4" and max. 62 1/4" and Lead free compliant version: Starting Serial # E00687; By-pass Assembly Starting Serial # 3863325 and identified with NSF61 mark on meter
DCDA | Wilkins | 350ADAR | 6 | H | 2010-03-25 | 2022-03-25 | N | 9 | (qqq),ttt,www,yyy,zzz,eeee,uuuu,vvvv,xxxx,yyyy,kkkkk,lllll,iiiiii,jjjjjj,llllll,mmmmmm | N | Wilkins 950XLD 3/4" (VU) | (M),A,B,C,D,E,F,G,H,I,J,K,L,N,O,P,Q,T | Integral grooved spool between the #2 ck and #2 SOV - assembly length: min. 42 1/2" and max. 71 1/4"
DCDA | Wilkins | 350ADAR | 6 | H | 2014-02-18 | 2023-02-18 | Y | 9 | (qqq),ttt,www,yyy,xxxx,yyyy,kkkkk,lllll,llllll,mmmmmm | N | Wilkins 950XLD 3/4" (VU) | (O), M | Integral grooved spool between the #2 ck and #2 SOV - assembly length: min. 42 1/2" and max. 71 1/4" and Lead free compliant version: Starting Serial # E00687; By-pass Assembly Starting Serial # 3863325 and identified with NSF61 mark on meter
DCDA | Wilkins | 350ADAR | 6 | VU | 2010-03-25 | 2022-03-25 | N | 9 | (qqq),ttt,www,yyy,zzz,eeee,uuuu,vvvv,xxxx,yyyy,kkkkk,lllll,iiiiii,jjjjjj,llllll,mmmmmm | N | Wilkins 950XLD 3/4" (H) | (M),A,B,C,D,E,F,G,H,I,J,K,L,N,O,P,Q,T | Integral grooved spool between the #2 ck and #2 SOV - assembly length: min. 42 1/2" and max. 71 1/4"
DCDA | Wilkins | 350ADAR | 6 | VU | 2014-02-18 | 2023-02-18 | Y | 9 | (qqq),ttt,www,yyy,xxxx,yyyy,kkkkk,lllll,llllll,mmmmmm | N | Wilkins 950XLD 3/4" (H) | (O), M | Integral grooved spool between the #2 ck and #2 SOV - assembly length: min. 42 1/2" and max. 71 1/4" and Lead free compliant version: Starting Serial # E00687; By-pass Assembly Starting Serial # 3863325 and identified with NSF61 mark on meter
DCDA | Wilkins | 350ADAR | 8 | H | 2010-03-25 | 2022-03-25 | N | 9 | (qqq),ttt,www,yyy,zzz,eeee,uuuu,vvvv,xxxx,yyyy,kkkkk,lllll,iiiiii,jjjjjj,llllll,mmmmmm | N | Wilkins 950XLD 3/4" (VU) | (M),A,B,C,D,E,F,G,H,I,J,K,L,N,O,P,Q,T | Integral grooved spool between the #2 ck and #2 SOV - assembly length: min. 57 7/8" and max. 86"
DCDA | Wilkins | 350ADAR | 8 | H | 2014-02-18 | 2023-02-18 | Y | 9 | (qqq),ttt,www,yyy,xxxx,yyyy,kkkkk,lllll,llllll,mmmmmm | N | Wilkins 950XLD 3/4" (VU) | (O), M | Integral grooved spool between the #2 ck and #2 SOV - assembly length: min. 57 7/8" and max. 86" and Lead free compliant version: Starting Serial # E00687; By-pass Assembly Starting Serial # 3863325 and identified with NSF61 mark on meter
DCDA | Wilkins | 350ADAR | 8 | VU | 2010-03-25 | 2022-03-25 | N | 9 | (qqq),ttt,www,yyy,zzz,eeee,uuuu,vvvv,xxxx,yyyy,kkkkk,lllll,iiiiii,jjjjjj,llllll,mmmmmm | N | Wilkins 950XLD 3/4" (H) | (M),A,B,C,D,E,F,G,H,I,J,K,L,N,O,P,Q,T | Integral grooved spool between the #2 ck and #2 SOV - assembly length: min. 57 7/8" and max. 86"
DCDA | Wilkins | 350ADAR | 8 | VU | 2014-02-18 | 2023-02-18 | Y | 9 | (qqq),ttt,www,yyy,xxxx,yyyy,kkkkk,lllll,llllll,mmmmmm | N | Wilkins 950XLD 3/4" (H) | (O), M | Integral grooved spool between the #2 ck and #2 SOV - assembly length: min. 57 7/8" and max. 86" and Lead free compliant version: Starting Serial # E00687; By-pass Assembly Starting Serial # 3863325 and identified with NSF61 mark on meter
DCDA | Wilkins | 350ADAR | 10 | H | 2010-03-25 | 2022-03-25 | N | 9 | (qqq),ttt,www,yyy,zzz,eeee,uuuu,vvvv,xxxx,yyyy,kkkkk,lllll,iiiiii,jjjjjj,llllll,mmmmmm | N | Wilkins 950XLD 3/4" (VU) | (M),A,B,C,D,E,F,G,H,I,J,K,L,N,O,P,Q,T | Integral grooved spool between the #2 ck and #2 SOV - assembly length: min. 61 3/8" and max. 100 5/8"
DCDA | Wilkins | 350ADAR | 10 | H | 2014-02-18 | 2023-02-18 | Y | 9 | (qqq),ttt,www,yyy,xxxx,yyyy,kkkkk,lllll,llllll,mmmmmm | N | Wilkins 950XLD 3/4" (VU) | (O), M | Integral grooved spool between the #2 ck and #2 SOV - assembly length: min. 61 3/8" and max. 100 5/8" and Lead free compliant version: Starting Serial # E00687; By-pass Assembly Starting Serial # 3863325 and identified with NSF61 mark on meter
DCDA | Wilkins | 350ADAR | 10 | VU | 2010-03-25 | 2022-03-25 | N | 9 | (qqq),ttt,www,yyy,zzz,eeee,uuuu,vvvv,xxxx,yyyy,kkkkk,lllll,iiiiii,jjjjjj,llllll,mmmmmm | N | Wilkins 950XLD 3/4" (H) | (M),A,B,C,D,E,F,G,H,I,J,K,L,N,O,P,Q,T | Integral grooved spool between the #2 ck and #2 SOV - assembly length: min. 61 3/8" and max. 100 5/8"
DCDA | Wilkins | 350ADAR | 10 | VU | 2014-02-18 | 2023-02-18 | Y | 9 | (qqq),ttt,www,yyy,xxxx,yyyy,kkkkk,lllll,llllll,mmmmmm | N | Wilkins 950XLD 3/4" (H) | (O), M | Integral grooved spool between the #2 ck and #2 SOV - assembly length: min. 61 3/8" and max. 100 5/8" and Lead free compliant version: Starting Serial # E00687; By-pass Assembly Starting Serial # 3863325 and identified with NSF61 mark on meter
DCDA | Wilkins | 350ASTDA | 2.5 | H | 2013-04-18 | 2022-04-18 | N | 10 | (qqq),ttt,www,yyy,uuuu,vvvv,xxxx,yyyy,kkkkk,lllll,iiiiii,jjjjjj,llllll,mmmmmm | N | Wilkins 950XLD 3/4" (H) | (N),G,H,I,J,K,L,M,O,P,Q,T
DCDA | Wilkins | 350ASTDA | 2.5 | H | 2014-02-18 | 2023-02-18 | Y | 10 | (qqq),ttt,www,yyy,uuuu,vvvv,xxxx,yyyy,kkkkk,lllll,iiiiii,jjjjjj,llllll,mmmmmm | N | Wilkins 950XLD 3/4" (H) | (O), M | Lead free compliant version: Starting Serial # 1458B; By-pass Assembly Starting Serial # 3863325 and identified with NSF61 mark on meter
DCDA | Wilkins | 350ASTDA | 2.5 | VU | 2013-04-18 | 2022-04-18 | N | 10 | (qqq),ttt,www,yyy,uuuu,vvvv,xxxx,yyyy,kkkkk,lllll,iiiiii,jjjjjj,llllll,mmmmmm | N | Wilkins 950XLD 3/4" (VU) | (N),G,H,I,J,K,L,M,O,P,Q,T
DCDA | Wilkins | 350ASTDA | 2.5 | VU | 2014-02-18 | 2023-02-18 | Y | 10 | (qqq),ttt,www,yyy,uuuu,vvvv,xxxx,yyyy,kkkkk,lllll,iiiiii,jjjjjj,llllll,mmmmmm | N | Wilkins 950XLD 3/4" (VU) | (O), M | Lead free compliant version: Starting Serial # 1458B; By-pass Assembly Starting Serial # 3863325 and identified with NSF61 mark on meter
DCDA | Wilkins | 350ASTDA | 3 | H | 2013-04-18 | 2022-04-18 | N | 10 | (qqq),ttt,www,yyy,uuuu,vvvv,xxxx,yyyy,kkkkk,lllll,iiiiii,jjjjjj,llllll,mmmmmm | N | Wilkins 950XLD 3/4" (H) | (N),G,H,I,J,K,L,M,O,P,Q,T
DCDA | Wilkins | 350ASTDA | 3 | H | 2014-02-18 | 2023-02-18 | Y | 10 | (qqq),ttt,www,yyy,uuuu,vvvv,xxxx,yyyy,kkkkk,lllll,iiiiii,jjjjjj,llllll,mmmmmm | N | Wilkins 950XLD 3/4" (H) | (O), M | Lead free compliant version: Starting Serial # 1458B; By-pass Assembly Starting Serial # 3863325 and identified with NSF61 mark on meter
DCDA | Wilkins | 350ASTDA | 3 | VU | 2013-04-18 | 2022-04-18 | N | 10 | (qqq),ttt,www,yyy,uuuu,vvvv,xxxx,yyyy,kkkkk,lllll,iiiiii,jjjjjj,llllll,mmmmmm | N | Wilkins 950XLD 3/4" (VU) | (N),G,H,I,J,K,L,M,O,P,Q,T
DCDA | Wilkins | 350ASTDA | 3 | VU | 2014-02-18 | 2023-02-18 | Y | 10 | (qqq),ttt,www,yyy,uuuu,vvvv,xxxx,yyyy,kkkkk,lllll,iiiiii,jjjjjj,llllll,mmmmmm | N | Wilkins 950XLD 3/4" (VU) | (O), M | Lead free compliant version: Starting Serial # 1458B; By-pass Assembly Starting Serial # 3863325 and identified with NSF61 mark on meter
DCDA | Wilkins | 350ASTDA | 4 | H | 2013-04-18 | 2022-04-18 | N | 10 | (qqq),ttt,www,yyy,uuuu,vvvv,xxxx,yyyy,kkkkk,lllll,iiiiii,jjjjjj,llllll,mmmmmm | N | Wilkins 950XLD 3/4" (H) | (N),F,G,H,I,J,K,L,M,O,P,Q,T
DCDA | Wilkins | 350ASTDA | 4 | H | 2014-02-18 | 2023-02-18 | Y | 10 | (qqq),ttt,www,yyy,uuuu,vvvv,xxxx,yyyy,kkkkk,lllll,iiiiii,jjjjjj,llllll,mmmmmm | N | Wilkins 950XLD 3/4" (H) | (O), M | Lead free compliant version: Starting Serial # 1458B; By-pass Assembly Starting Serial # 3863325 and identified with NSF61 mark on meter
DCDA | Wilkins | 350ASTDA | 4 | VU | 2013-04-18 | 2022-04-18 | N | 10 | (qqq),ttt,www,yyy,uuuu,vvvv,xxxx,yyyy,kkkkk,lllll,iiiiii,jjjjjj,llllll,mmmmmm | N | Wilkins 950XLD 3/4" (VU) | (N),F,G,H,I,J,K,L,M,O,P,Q,T
DCDA | Wilkins | 350ASTDA | 4 | VU | 2014-02-18 | 2023-02-18 | Y | 10 | (qqq),ttt,www,yyy,uuuu,vvvv,xxxx,yyyy,kkkkk,lllll,iiiiii,jjjjjj,llllll,mmmmmm | N | Wilkins 950XLD 3/4" (VU) | (O), M | Lead free compliant version: Starting Serial # 1458B; By-pass Assembly Starting Serial # 3863325 and identified with NSF61 mark on meter
DCDA | Wilkins | 350ASTDA | 6 | H | 2013-07-03 | 2022-07-03 | N | 10 | (qqq),ttt,www,yyy,uuuu,vvvv,xxxx,yyyy,kkkkk,lllll,iiiiii,jjjjjj,llllll,mmmmmm | N | Wilkins 950XLD 3/4" (H) | (N),G,H,I,J,K,L,M,O,P,Q,T
DCDA | Wilkins | 350ASTDA | 6 | H | 2014-02-18 | 2023-02-18 | Y | 10 | (qqq),ttt,www,yyy,uuuu,vvvv,xxxx,yyyy,kkkkk,lllll,iiiiii,jjjjjj,llllll,mmmmmm | N | Wilkins 950XLD 3/4" (H) | (O), M | Lead free compliant version: Starting Serial # 1458B; By-pass Assembly Starting Serial # 3863325 and identified with NSF61 mark on meter
DCDA | Wilkins | 350ASTDA | 6 | VU | 2013-07-03 | 2022-07-03 | N | 10 | (qqq),ttt,www,yyy,uuuu,vvvv,xxxx,yyyy,kkkkk,lllll,iiiiii,jjjjjj,llllll,mmmmmm | N | Wilkins 950XLD 3/4" (VU) | (N),G,H,I,J,K,L,M,O,P,Q,T
DCDA | Wilkins | 350ASTDA | 6 | VU | 2014-02-18 | 2023-02-18 | Y | 10 | (qqq),ttt,www,yyy,uuuu,vvvv,xxxx,yyyy,kkkkk,lllll,iiiiii,jjjjjj,llllll,mmmmmm | N | Wilkins 950XLD 3/4" (VU) | (O), M | Lead free compliant version: Starting Serial # 1458B; By-pass Assembly Starting Serial # 3863325 and identified with NSF61 mark on meter
DCDA | Wilkins | 350ASTDA | 8 | H | 2014-02-20 | 2023-02-20 | Y | 10 | (qqq),ttt,www,yyy,uuuu,vvvv,xxxx,yyyy,kkkkk,lllll,iiiiii,jjjjjj,llllll,mmmmmm | N | Wilkins 950XLD 3/4" (H) | (O), M | Lead free compliant version: By-pass Assembly Starting Serial # 3863325 and identified with NSF61 mark on meter
DCDA | Wilkins | 350ASTDA | 8 | VU | 2014-02-20 | 2023-02-20 | Y | 10 | (qqq),ttt,www,yyy,uuuu,vvvv,xxxx,yyyy,kkkkk,lllll,iiiiii,jjjjjj,llllll,mmmmmm | N | Wilkins 950XLD 3/4" (VU) | (O), M | Lead free compliant version: By-pass Assembly Starting Serial # 3863325 and identified with NSF61 mark on meter
DCDA | Wilkins | 350ASTDA | 10 | H | 2014-02-20 | 2023-02-20 | Y | 10 | (qqq),ttt,www,yyy,uuuu,vvvv,xxxx,yyyy,kkkkk,lllll,iiiiii,jjjjjj,llllll,mmmmmm | N | Wilkins 950XLD 3/4" (H) | (O), M | Lead free compliant version: By-pass Assembly Starting Serial # 3863325 and identified with NSF61 mark on meter
DCDA | Wilkins | 350ASTDA | 10 | VU | 2014-02-20 | 2023-02-20 | Y | 10 | (qqq),ttt,www,yyy,uuuu,vvvv,xxxx,yyyy,kkkkk,lllll,iiiiii,jjjjjj,llllll,mmmmmm | N | Wilkins 950XLD 3/4" (VU) | (O), M | Lead free compliant version: By-pass Assembly Starting Serial # 3863325 and identified with NSF61 mark on meter
DCDA | Wilkins | 350ASTDAR | 2.5 | H | 2014-10-09 | 2023-10-09 | Y | 10 | (yyyy),ttt,www,yyy,uuuu,vvvv,xxxx,kkkkk,lllll,iiiiii,jjjjjj,llllll,mmmmmm | N | Wilkins 950XLD 3/4" (H) | (O), M | Integral grooved spool between the #2 ck and #2 SOV - assembly length: min. 31" and max. 47 1/8"
DCDA | Wilkins | 350ASTDAR | 2.5 | VU | 2014-10-09 | 2023-10-09 | Y | 10 | (yyyy),ttt,www,yyy,uuuu,vvvv,xxxx,kkkkk,lllll,iiiiii,jjjjjj,llllll,mmmmmm | N | Wilkins 950XLD 3/4" (VU) | (O), M | Integral grooved spool between the #2 ck and #2 SOV - assembly length: min. 31" and max. 47 1/8"
DCDA | Wilkins | 350ASTDAR | 3 | H | 2014-10-09 | 2023-10-09 | Y | 10 | (yyyy),ttt,www,yyy,uuuu,vvvv,xxxx,kkkkk,lllll,iiiiii,jjjjjj,llllll,mmmmmm | N | Wilkins 950XLD 3/4" (H) | (O), M | Integral grooved spool between the #2 ck and #2 SOV - assembly length: min. 31 1/2" and max. 48 1/8"
DCDA | Wilkins | 350ASTDAR | 3 | VU | 2014-10-09 | 2023-10-09 | Y | 10 | (yyyy),ttt,www,yyy,uuuu,vvvv,xxxx,kkkkk,lllll,iiiiii,jjjjjj,llllll,mmmmmm | N | Wilkins 950XLD 3/4" (VU) | (O), M | Integral grooved spool between the #2 ck and #2 SOV - assembly length: min. 31 1/2" and max. 48 1/8"
DCDA | Wilkins | 350ASTDAR | 4 | H | 2014-10-09 | 2023-10-09 | Y | 10 | (yyyy),ttt,www,yyy,uuuu,vvvv,xxxx,kkkkk,lllll,iiiiii,jjjjjj,llllll,mmmmmm | N | Wilkins 950XLD 3/4" (H) | (O), M | Integral grooved spool between the #2 ck and #2 SOV - assembly length: min. 32 5/8" and max. 62 1/4"
DCDA | Wilkins | 350ASTDAR | 4 | VU | 2014-10-09 | 2023-10-09 | Y | 10 | (yyyy),ttt,www,yyy,uuuu,vvvv,xxxx,kkkkk,lllll,iiiiii,jjjjjj,llllll,mmmmmm | N | Wilkins 950XLD 3/4" (VU) | (O), M | Integral grooved spool between the #2 ck and #2 SOV - assembly length: min. 32 5/8" and max. 62 1/4"
DCDA | Wilkins | 350ASTDAR | 6 | H | 2014-09-18 | 2023-09-18 | Y | 10 | (yyyy),ttt,www,yyy,uuuu,vvvv,xxxx,kkkkk,lllll,iiiiii,jjjjjj,llllll,mmmmmm | N | Wilkins 950XLD 3/4" (H) | (O), M | Integral grooved spool between the #2 ck and #2 SOV - assembly length: min. 39" and max. 71 1/4"
DCDA | Wilkins | 350ASTDAR | 6 | VU | 2014-09-18 | 2023-09-18 | Y | 10 | (yyyy),ttt,www,yyy,uuuu,vvvv,xxxx,kkkkk,lllll,iiiiii,jjjjjj,llllll,mmmmmm | N | Wilkins 950XLD 3/4" (VU) | (O), M | Integral grooved spool between the #2 ck and #2 SOV - assembly length: min. 39" and max. 71 1/4"
DCDA | Wilkins | 350ASTDAR | 8 | H | 2014-09-18 | 2023-09-18 | Y | 10 | (yyyy),ttt,www,yyy,uuuu,vvvv,xxxx,kkkkk,lllll,iiiiii,jjjjjj,llllll,mmmmmm | N | Wilkins 950XLD 3/4" (H) | (O), M | Integral grooved spool between the #2 ck and #2 SOV - assembly length: min. 48 3/4" and max. 86"
DCDA | Wilkins | 350ASTDAR | 8 | VU | 2014-09-18 | 2023-09-18 | Y | 10 | (yyyy),ttt,www,yyy,uuuu,vvvv,xxxx,kkkkk,lllll,iiiiii,jjjjjj,llllll,mmmmmm | N | Wilkins 950XLD 3/4" (VU) | (O), M | Integral grooved spool between the #2 ck and #2 SOV - assembly length: min. 48 3/4" and max. 86"
DCDA | Wilkins | 350ASTDAR | 10 | H | 2014-09-18 | 2023-09-18 | Y | 10 | (yyyy),ttt,www,yyy,uuuu,vvvv,xxxx,kkkkk,lllll,iiiiii,jjjjjj,llllll,mmmmmm | N | Wilkins 950XLD 3/4" (H) | (O), M | Integral grooved spool between the #2 ck and #2 SOV - assembly length: min. 52 5/8" and max. 100 5/8"
DCDA | Wilkins | 350ASTDAR | 10 | VU | 2014-09-18 | 2023-09-18 | Y | 10 | (yyyy),ttt,www,yyy,uuuu,vvvv,xxxx,kkkkk,lllll,iiiiii,jjjjjj,llllll,mmmmmm | N | Wilkins 950XLD 3/4" (VU) | (O), M | Integral grooved spool between the #2 ck and #2 SOV - assembly length: min. 52 5/8" and max. 100 5/8"
DCDA | Wilkins | 350DA | 2.5 | H | 2002-04-03 | 2023-04-03 | N | 9 | (hh),ff,mm,uu,zz,vvvv,wwww,yyyy,zzzz,kkkkk,jjjjjj,kkkkkk,mmmmmm,nnnnnn | N | Wilkins 950XLD 3/4" (H) | (M),A,B,C,D,E,F,G,H,I,J,K,L,N,O,P,Q,T | Up to Serial # N4230
DCDA | Wilkins | 350DA | 2.5 | H | 2014-02-18 | 2023-02-18 | Y | 9 | (hh),qqq,vvv,www,yyyy,zzzz,kkkkk,mmmmmm,nnnnnn | N | Wilkins 950XLD 3/4" (H) | (O), M | Lead free compliant version: Starting Serial # N4231; By-pass Assembly Starting Serial # 3863325 and identified with NSF61 mark on meter
DCDA | Wilkins | 350DA | 2.5 | VU | 2002-10-08 | 2023-10-08 | N | 9 | (hh),ff,mm,uu,zz,vvvv,wwww,yyyy,zzzz,kkkkk,jjjjjj,kkkkkk,mmmmmm,nnnnnn | N | Wilkins 950XLD 3/4" (VU) | (M),A,B,C,D,E,F,G,H,I,J,K,L,N,O,P,Q,T | Up to Serial # N4230
DCDA | Wilkins | 350DA | 2.5 | VU | 2014-02-18 | 2023-02-18 | Y | 9 | (hh),qqq,vvv,www,yyyy,zzzz,kkkkk,mmmmmm,nnnnnn | N | Wilkins 950XLD 3/4" (VU) | (O), M | Lead free compliant version: Starting Serial # N4231; By-pass Assembly Starting Serial # 3863325 and identified with NSF61 mark on meter
DCDA | Wilkins | 350DA | 3 | H | 2002-04-03 | 2023-04-03 | N | 9 | (hh),ff,mm,uu,zz,vvvv,wwww,yyyy,zzzz,kkkkk,jjjjjj,kkkkkk,mmmmmm,nnnnnn | N | Wilkins 950XLD 3/4" (H) | (M),A,B,C,D,E,F,G,H,I,J,K,L,N,O,P,Q,T | Up to Serial # N4230
DCDA | Wilkins | 350DA | 3 | H | 2002-04-03 | 2023-04-03 | Y | 9 | (hh),ff,mm,uu,zz,vvvv,wwww,yyyy,zzzz,kkkkk,jjjjjj,kkkkkk,mmmmmm,nnnnnn | N | Wilkins 950XLD 3/4" (H) | (M),A,B,C,D,E,F,G,H,I,J,K,L,N,O,P,Q,T | Starting Serial # N4231; By-pass Assembly Starting Serial # 3863325 and Lead free compliant version identified with NSF61 mark on meter
DCDA | Wilkins | 350DA | 3 | H | 2014-02-18 | 2023-02-18 | Y | 9 | (hh),qqq,vvv,www,yyyy,zzzz,mmmmmm,nnnnnn | N | Wilkins 950XLD 3/4" (H) | (O), M | Lead free compliant version: Starting Serial # N4231; By-pass Assembly Starting Serial # 3863325 and identified with NSF61 mark on meter
DCDA | Wilkins | 350DA | 3 | VU | 2002-10-08 | 2023-10-08 | N | 9 | (hh),ff,mm,uu,zz,vvvv,wwww,yyyy,zzzz,kkkkk,jjjjjj,kkkkkk,mmmmmm,nnnnnn | N | Wilkins 950XLD 3/4" (VU) | (M),A,B,C,D,E,F,G,H,I,J,K,L,N,O,P,Q,T | Up to Serial # N4230
DCDA | Wilkins | 350DA | 3 | VU | 2002-10-08 | 2023-10-08 | Y | 9 | (hh),ff,mm,uu,zz,vvvv,wwww,yyyy,zzzz,kkkkk,jjjjjj,kkkkkk,mmmmmm,nnnnnn | N | Wilkins 950XLD 3/4" (VU) | (M),A,B,C,D,E,F,G,H,I,J,K,L,N,O,P,Q,T | Starting Serial # N4231; By-pass Assembly Starting Serial # 3863325 and Lead free compliant version identified with NSF61 mark on meter
DCDA | Wilkins | 350DA | 3 | VU | 2014-02-18 | 2023-02-18 | Y | 9 | (hh),qqq,vvv,www,yyyy,zzzz,mmmmmm,nnnnnn | N | Wilkins 950XLD 3/4" (VU) | (O), M | Lead free compliant version: Starting Serial # N4231; By-pass Assembly Starting Serial # 3863325 and identified with NSF61 mark on meter
DCDA | Wilkins | 350DA | 4 | H | 1999-09-15 | 2023-09-15 | N | 9 | (hh),ff,mm,uu,zz,qqq,vvv,www,zzz,eeee,vvvv,wwww,yyyy,zzzz,kkkkk,jjjjjj,kkkkkk,mmmmmm,nnnnnn | N | Wilkins 950XLD 3/4" (H) | (M),A,B,C,D,E,F,G,H,I,J,K,L,N,O,P,Q,T | Up to Serial # N4230
DCDA | Wilkins | 350DA | 4 | H | 1999-09-15 | 2023-09-15 | Y | 9 | (hh),ff,mm,uu,zz,qqq,vvv,www,zzz,eeee,vvvv,wwww,yyyy,zzzz,kkkkk,jjjjjj,kkkkkk,mmmmmm,nnnnnn | N | Wilkins 950XLD 3/4" (H) | (M),A,B,C,D,E,F,G,H,I,J,K,L,N,O,P,Q,T | Starting Serial # N4231; By-pass Assembly Starting Serial # 3863325 and Lead free compliant version identified with NSF61 mark on meter
DCDA | Wilkins | 350DA | 4 | H | 2014-02-18 | 2023-02-18 | Y | 9 | (hh),qqq,vvv,www,yyyy,zzzz,mmmmmm,nnnnnn | N | Wilkins 950XLD 3/4" (H) | (O), M | Lead free compliant version: Starting Serial # N4231; By-pass Assembly Starting Serial # 3863325 and identified with NSF61 mark on meter
DCDA | Wilkins | 350DA | 4 | VU | 2000-09-09 | 2024-09-09 | N | 9 | (hh),ff,mm,uu,zz,qqq,vvv,www,zzz,eeee,vvvv,wwww,yyyy,zzzz,kkkkk,jjjjjj,kkkkkk,mmmmmm,nnnnnn | N | Wilkins 950XLD 3/4" (VU) | (M),A,B,C,D,E,F,G,H,I,J,K,L,N,O,P,Q,T | Up to Serial # N4230
DCDA | Wilkins | 350DA | 4 | VU | 2000-09-09 | 2024-09-09 | Y | 9 | (hh),ff,mm,uu,zz,qqq,vvv,www,zzz,eeee,vvvv,wwww,yyyy,zzzz,kkkkk,jjjjjj,kkkkkk,mmmmmm,nnnnnn | N | Wilkins 950XLD 3/4" (VU) | (M),A,B,C,D,E,F,G,H,I,J,K,L,N,O,P,Q,T | Starting Serial # N4231; By-pass Assembly Starting Serial # 3863325 and Lead free compliant version identified with NSF61 mark on meter
DCDA | Wilkins | 350DA | 4 | VU | 2014-02-18 | 2023-02-18 | Y | 9 | (hh),qqq,vvv,www,yyyy,zzzz,mmmmmm,nnnnnn | N | Wilkins 950XLD 3/4" (VU) | (O), M | Lead free compliant version: Starting Serial # N4231; By-pass Assembly Starting Serial # 3863325 and identified with NSF61 mark on meter
DCDA | Wilkins | 350DA | 6 | H | 1999-10-18 | 2023-10-18 | N | 9 | (hh),ff,mm,uu,zz,qqq,vvv,www,zzz,eeee,vvvv,wwww,yyyy,zzzz,kkkkk,jjjjjj,kkkkkk,mmmmmm,nnnnnn | N | Wilkins 950XLD 3/4" (H) | (M),A,B,C,D,E,F,G,H,I,J,K,L,N,O,P,Q,T | Up to Serial # N4230
DCDA | Wilkins | 350DA | 6 | H | 1999-10-18 | 2023-10-18 | Y | 9 | (hh),ff,mm,uu,zz,qqq,vvv,www,zzz,eeee,vvvv,wwww,yyyy,zzzz,kkkkk,jjjjjj,kkkkkk,mmmmmm,nnnnnn | N | Wilkins 950XLD 3/4" (H) | (M),A,B,C,D,E,F,G,H,I,J,K,L,N,O,P,Q,T | Starting Serial # N4231; By-pass Assembly Starting Serial # 3863325 and Lead free compliant version identified with NSF61 mark on meter
DCDA | Wilkins | 350DA | 6 | H | 2014-02-18 | 2023-02-18 | Y | 9 | (hh),qqq,vvv,www,yyyy,zzzz,mmmmmm,nnnnnn | N | Wilkins 950XLD 3/4" (H) | (O), M | Lead free compliant version: Starting Serial # N4231; By-pass Assembly Starting Serial # 3863325 and identified with NSF61 mark on meter
DCDA | Wilkins | 350DA | 6 | VU | 2000-01-05 | 2023-01-05 | N | 9 | (hh),ff,mm,uu,zz,qqq,vvv,www,zzz,eeee,vvvv,wwww,yyyy,zzzz,kkkkk,jjjjjj,kkkkkk,mmmmmm,nnnnnn | N | Wilkins 950XLD 3/4" (VU) | (M),A,B,C,D,E,F,G,H,I,J,K,L,N,O,P,Q,T | Up to Serial # N4230
DCDA | Wilkins | 350DA | 6 | VU | 2000-01-05 | 2023-01-05 | Y | 9 | (hh),ff,mm,uu,zz,qqq,vvv,www,zzz,eeee,vvvv,wwww,yyyy,zzzz,kkkkk,jjjjjj,kkkkkk,mmmmmm,nnnnnn | N | Wilkins 950XLD 3/4" (VU) | (M),A,B,C,D,E,F,G,H,I,J,K,L,N,O,P,Q,T | Starting Serial # N4231; By-pass Assembly Starting Serial # 3863325 and Lead free compliant version identified with NSF61 mark on meter
DCDA | Wilkins | 350DA | 6 | VU | 2014-02-18 | 2023-02-18 | Y | 9 | (hh),qqq,vvv,www,yyyy,zzzz,mmmmmm,nnnnnn | N | Wilkins 950XLD 3/4" (VU) | (O), M | Lead free compliant version: Starting Serial # N4231; By-pass Assembly Starting Serial # 3863325 and identified with NSF61 mark on meter
DCDA | Wilkins | 350DA | 8 | H | 2002-07-03 | 2023-07-03 | N | 9 | (hh),ff,mm,uu,zz,qqq,vvv,www,zzz,eeee,vvvv,wwww,yyyy,zzzz,kkkkk,jjjjjj,kkkkkk,mmmmmm,nnnnnn | N | Wilkins 950XLD 3/4" (H) | (N),F,G,H,I,J,K,L,M,O,P,Q,T | Up to Serial # N4230
DCDA | Wilkins | 350DA | 8 | H | 2002-07-03 | 2023-07-03 | Y | 9 | (hh),ff,mm,uu,zz,qqq,vvv,www,zzz,eeee,vvvv,wwww,yyyy,zzzz,kkkkk,jjjjjj,kkkkkk,mmmmmm,nnnnnn | N | Wilkins 950XLD 3/4" (H) | (N),F,G,H,I,J,K,L,M,O,P,Q,T | Starting Serial # N4231; By-pass Assembly Starting Serial # 3863325 and Lead free compliant version identified with NSF61 mark on meter
DCDA | Wilkins | 350DA | 8 | H | 2014-02-18 | 2023-02-18 | Y | 9 | (hh),qqq,vvv,www,yyyy,zzzz,mmmmmm,nnnnnn | N | Wilkins 950XLD 3/4" (H) | (O), M | Lead free compliant version: Starting Serial # N4231; By-pass Assembly Starting Serial # 3863325 and identified with NSF61 mark on meter
DCDA | Wilkins | 350DA | 8 | VU | 2003-01-16 | 2024-01-16 | N | 9 | (hh),ff,mm,uu,zz,qqq,vvv,www,zzz,eeee,vvvv,wwww,yyyy,zzzz,kkkkk,jjjjjj,kkkkkk,mmmmmm,nnnnnn | N | Wilkins 950XLD 3/4" (VU) | (N),F,G,H,I,J,K,L,M,O,P,Q,T | Up to Serial # N4230
DCDA | Wilkins | 350DA | 8 | VU | 2003-01-16 | 2024-01-16 | Y | 9 | (hh),ff,mm,uu,zz,qqq,vvv,www,zzz,eeee,vvvv,wwww,yyyy,zzzz,kkkkk,jjjjjj,kkkkkk,mmmmmm,nnnnnn | N | Wilkins 950XLD 3/4" (VU) | (N),F,G,H,I,J,K,L,M,O,P,Q,T | Starting Serial # N4231; By-pass Assembly Starting Serial # 3863325 and Lead free compliant version identified with NSF61 mark on meter
DCDA | Wilkins | 350DA | 8 | VU | 2014-02-18 | 2023-02-18 | Y | 9 | (hh),qqq,vvv,www,yyyy,zzzz,mmmmmm,nnnnnn | N | Wilkins 950XLD 3/4" (VU) | (O), M | Lead free compliant version: Starting Serial # N4231; By-pass Assembly Starting Serial # 3863325 and identified with NSF61 mark on meter
DCDA | Wilkins | 350DA | 10 | H | 2002-08-28 | 2023-08-28 | N | 9 | (hh),ff,mm,uu,zz,qqq,vvv,www,zzz,eeee,vvvv,wwww,yyyy,zzzz,kkkkk,jjjjjj,kkkkkk,mmmmmm,nnnnnn | N | Wilkins 950XLD 3/4" (H) | (N),F,G,H,I,J,K,L,M,O,P,Q,T | Up to Serial # N4230
DCDA | Wilkins | 350DA | 10 | H | 2002-08-28 | 2023-08-28 | Y | 9 | (hh),ff,mm,uu,zz,qqq,vvv,www,zzz,eeee,vvvv,wwww,yyyy,zzzz,kkkkk,jjjjjj,kkkkkk,mmmmmm,nnnnnn | N | Wilkins 950XLD 3/4" (H) | (N),F,G,H,I,J,K,L,M,O,P,Q,T | Starting Serial # N4231; By-pass Assembly Starting Serial # 3863325 and Lead free compliant version identified with NSF61 mark on meter
DCDA | Wilkins | 350DA | 10 | H | 2014-02-18 | 2023-02-18 | Y | 9 | (hh),qqq,vvv,www,yyyy,zzzz,mmmmmm,nnnnnn | N | Wilkins 950XLD 3/4" (H) | (O), M | Lead free compliant version: Starting Serial # N4231; By-pass Assembly Starting Serial # 3863325 and identified with NSF61 mark on meter
DCDA | Wilkins | 350DA | 10 | VU | 2003-03-14 | 2024-03-14 | N | 9 | (hh),ff,mm,uu,zz,qqq,vvv,www,zzz,eeee,vvvv,wwww,yyyy,zzzz,kkkkk,jjjjjj,kkkkkk,mmmmmm,nnnnnn | N | Wilkins 950XLD 3/4" (VU) | (N),F,G,H,I,J,K,L,M,O,P,Q,T | Up to Serial # N4230
DCDA | Wilkins | 350DA | 10 | VU | 2003-03-14 | 2024-03-14 | Y | 9 | (hh),ff,mm,uu,zz,qqq,vvv,www,zzz,eeee,vvvv,wwww,yyyy,zzzz,kkkkk,jjjjjj,kkkkkk,mmmmmm,nnnnnn | N | Wilkins 950XLD 3/4" (VU) | (N),F,G,H,I,J,K,L,M,O,P,Q,T | Starting Serial # N4231; By-pass Assembly Starting Serial # 3863325 and Lead free compliant version identified with NSF61 mark on meter
DCDA | Wilkins | 350DA | 10 | VU | 2014-02-18 | 2023-02-18 | Y | 9 | (hh),qqq,vvv,www,yyyy,zzzz,mmmmmm,nnnnnn | N | Wilkins 950XLD 3/4" (VU) | (O), M | Lead free compliant version: Starting Serial # N4231; By-pass Assembly Starting Serial # 3863325 and identified with NSF61 mark on meter
DCDA | Wilkins | 350DA | 12 | H | 2009-10-20 | 2024-10-20 | N | 9 | (hh),vvvv,wwww,yyyy,zzzz,kkkkk,jjjjjj,kkkkkk,mmmmmm,nnnnnn | N | Wilkins 950XLD 3/4" (H) | (N),F,G,H,I,J,K,L,M,O,P,Q,T | Up to Serial # N4230
DCDA | Wilkins | 350DA | 12 | H | 2009-10-20 | 2024-10-20 | Y | 9 | (hh),ssss,tttt,vvvv,wwww,yyyy,zzzz,jjjjjj,kkkkkk,mmmmmm,nnnnnn | N | Wilkins 950XLD 3/4" (H) | (N),F,G,H,I,J,K,L,M,O,P,Q,T | Starting Serial # N4231; By-pass Assembly Starting Serial # 3863325 and Lead free compliant version identified with NSF61 mark on meter
DCDA | Wilkins | 350DA | 12 | H | 2014-02-18 | 2023-02-18 | Y | 9 | (hh),vvvv,wwww,yyyy,zzzz,kkkkk,jjjjjj,kkkkkk,mmmmmm,nnnnnn | N | Wilkins 950XLD 3/4" (H) | (O) | Lead free compliant version: Starting Serial # N4231; By-pass Assembly Starting Serial # 3863325 and identified with NSF61 mark on meter
DCDA | Wilkins | 450DA | 4 | VUVD | 2000-04-12 | 2024-04-12 | N | 9 | (qqq),ttt,www,yyy,zzz,eeee,uuuu,vvvv,xxxx,yyyy,kkkkk,lllll,iiiiii,jjjjjj,llllll,mmmmmm | N | Wilkins 950XLD 3/4" (H) | (M),A,B,C,D,E,F,G,H,I,J,K,L,N,O,P,Q,T
DCDA | Wilkins | 450DA | 4 | VUVD | 2014-02-18 | 2023-02-18 | Y | 9 | (hh),qqq,vvv,www,yyyy,zzzz,mmmmmm,nnnnnn | N | Wilkins 950XLD 3/4" (H) | (O), M | Lead free compliant version: Starting Serial # P07372; By-pass Assembly Starting Serial # 3863325 and identified with NSF61 mark on meter
DCDA | Wilkins | 450DA | 6 | VUVD | 2000-05-24 | 2024-05-24 | N | 9 | (qqq),ttt,www,yyy,zzz,eeee,uuuu,vvvv,xxxx,yyyy,kkkkk,lllll,iiiiii,jjjjjj,llllll,mmmmmm | N | Wilkins 950XLD 3/4" (H) | (M),C,D,E,F,G,H,I,J,K,L,N,O,P,Q,T
DCDA | Wilkins | 450DA | 6 | VUVD | 2014-02-18 | 2023-02-18 | Y | 9 | (hh),qqq,vvv,www,yyyy,zzzz,mmmmmm,nnnnnn | N | Wilkins 950XLD 3/4" (H) | (O), M | Lead free compliant version: Starting Serial # P07372; By-pass Assembly Starting Serial # 3863325 and identified with NSF61 mark on meter
DCDA | Wilkins | 450DA | 8 | VUVD | 2004-08-03 | 2022-08-03 | N | 9 | (qqq),ttt,www,yyy,zzz,eeee,uuuu,vvvv,xxxx,yyyy,kkkkk,lllll,iiiiii,jjjjjj,llllll,mmmmmm | N | Wilkins 950XLD 3/4" (H) | (N),F,G,H,I,J,K,L,M,O,P,Q,T
DCDA | Wilkins | 450DA | 8 | VUVD | 2014-02-18 | 2023-02-18 | Y | 9 | (hh),qqq,vvv,www,yyyy,zzzz,mmmmmm,nnnnnn | N | Wilkins 950XLD 3/4" (H) | (O), M | Lead free compliant version: Starting Serial # P07372; By-pass Assembly Starting Serial # 3863325 and identified with NSF61 mark on meter
DCDA | Wilkins | 450DA | 10 | VUVD | 2004-08-03 | 2022-08-03 | N | 9 | (qqq),ttt,www,yyy,zzz,eeee,uuuu,vvvv,xxxx,yyyy,kkkkk,lllll | N | Wilkins 950XLD 3/4" (H) | (N),F,G,H,I,J,K,L,M,O,P,Q,T
DCDA | Wilkins | 450DA | 10 | VUVD | 2014-02-18 | 2023-02-18 | Y | 9 | (hh),qqq,vvv,www,yyyy,zzzz,mmmmmm,nnnnnn | N | Wilkins 950XLD 3/4" (H) | (O), M | Lead free compliant version: Starting Serial # P07372; By-pass Assembly Starting Serial # 3863325 and identified with NSF61 mark on meter
DCDA | Wilkins | 450STDA | 4 | VUVD | 2018-12-18 | 2024-12-18 | Y | 10 | (kkkkk),yyy,ssss,uuuu,vvvv,xxxx,yyyy,aaaaa,lllll,gggggg,iiiiii,jjjjjj,llllll,mmmmmm,oooooo | N | Wilkins 950XLDTCU 3/4" (H) | (O),G,H,I,J,K,L,M,N,Q,T
DCDA | Wilkins | 450STDA | 6 | VUVD | 2018-12-18 | 2024-12-18 | Y | 10 | (kkkkk),yyy,ssss,uuuu,vvvv,xxxx,yyyy,aaaaa,lllll,gggggg,iiiiii,jjjjjj,llllll,mmmmmm,oooooo | N | Wilkins 950XLDTCU 3/4" (H) | (O),G,H,I,J,K,L,M,N,Q,T
DCDA | Wilkins | 450STDA | 8 | VUVD | 2018-12-18 | 2024-12-18 | Y | 10 | (kkkkk),yyy,ssss,uuuu,vvvv,xxxx,yyyy,aaaaa,lllll,gggggg,iiiiii,jjjjjj,llllll,mmmmmm,oooooo | N | Wilkins 950XLDTCU 3/4" (H) | (O),G,H,I,J,K,L,M,N,Q,T
DCDA | Wilkins | 450STDA | 10 | VUVD | 2018-12-18 | 2024-12-18 | Y | 10 | (kkkkk),yyy,ssss,uuuu,vvvv,xxxx,yyyy,aaaaa,lllll,gggggg,iiiiii,jjjjjj,llllll,mmmmmm,oooooo | N | Wilkins 950XLDTCU 3/4" (H) | (O),G,H,I,J,K,L,M,N,Q,T
DCDA | Wilkins | 450STDAR | 4 | VUVD | 2018-12-18 | 2024-12-18 | Y | 10 | (kkkkk),yyy,ssss,uuuu,vvvv,xxxx,yyyy,aaaaa,lllll,gggggg,iiiiii,jjjjjj,llllll,mmmmmm,oooooo | N | Wilkins 950XLD 3/4" (H) | (O),G,H,I,J,K,L,M,N,Q,T
DCDA | Wilkins | 450STDAR | 6 | VUVD | 2018-12-18 | 2024-12-18 | Y | 10 | (kkkkk),yyy,ssss,uuuu,vvvv,xxxx,yyyy,aaaaa,lllll,gggggg,iiiiii,jjjjjj,llllll,mmmmmm,oooooo | N | Wilkins 950XLD 3/4" (H) | (O),G,H,I,J,K,L,M,N,Q,T
DCDA | Wilkins | 450STDAR | 8 | VUVD | 2018-12-18 | 2024-12-18 | Y | 10 | (kkkkk),yyy,ssss,uuuu,vvvv,xxxx,yyyy,aaaaa,lllll,gggggg,iiiiii,jjjjjj,llllll,mmmmmm,oooooo | N | Wilkins 950XLD 3/4" (H) | (O),G,H,I,J,K,L,M,N,Q,T
DCDA | Wilkins | 450STDAR | 10 | VUVD | 2018-12-18 | 2024-12-18 | Y | 10 | (kkkkk),yyy,ssss,uuuu,vvvv,xxxx,yyyy,aaaaa,lllll,gggggg,iiiiii,jjjjjj,llllll,mmmmmm,oooooo | N | Wilkins 950XLD 3/4" (H) | (O),G,H,I,J,K,L,M,N,Q,T
DCDA | Wilkins | 950DA | 2.5 | H | 1994-01-02 | 2023-01-02 | N | 8 | (hh),ff,mm,uu,zz,vvvv,wwww,yyyy,zzzz | Y | Wilkins 950XL 3/4" (H), Wilkins 950 3/4" (H) | (M),A,B,C,D,E,F,G,H,I,J,K,L,N,O,P,Q,T
DCDA | Wilkins | 950DA | 2.5 | VU | 1996-12-12 | 2023-12-12 | N | 8 | (hh),ff,mm,uu,zz,vvvv,wwww,yyyy,zzzz | Y | Wilkins 950XL 3/4" (VU) | (M),D,E,F,G,H,I,J,K,L,N,O,P,Q,T
DCDA | Wilkins | 950DA | 3 | H | 1994-01-02 | 2023-01-02 | N | 8 | (hh),ff,mm,uu,zz,vvvv,wwww,yyyy,zzzz | Y | Wilkins 950XL 3/4" (H), Wilkins 950 3/4" (H) | (M),A,B,C,D,E,F,G,H,I,J,K,L,N,O,P,Q,T
DCDA | Wilkins | 950DA | 3 | VU | 1996-12-12 | 2023-12-12 | N | 8 | (hh),ff,mm,uu,zz,vvvv,wwww,yyyy,zzzz | Y | Wilkins 950XL 3/4" (VU) | (M),D,E,F,G,H,I,J,K,L,N,O,P,Q,T
DCDA | Wilkins | 950DA | 4 | H | 1993-06-09 | 2023-06-09 | N | 8 | hh,ff,mm,uu,zz,vvvv,wwww,yyyy,zzzz | Y | Wilkins 950XL 3/4" (H), Wilkins 950 3/4" (H) | (M),E,F,G,H,I,J,K,L,N,O,P,Q,T
DCDA | Wilkins | 950DA | 4 | VU | 1996-12-12 | 2023-12-12 | N | 8 | hh,ff,mm,uu,zz,vvvv,wwww,yyyy,zzzz | Y | Wilkins 950XL 3/4" (VU) | (M),A,B,C,D,E,F,G,H,I,J,K,L,N,O,P,Q,T
DCDA | Wilkins | 950DA | 6 | H | 1993-06-09 | 2023-06-09 | N | 8 | hh,ff,mm,uu,zz,vvvv,wwww,yyyy,zzzz | Y | Wilkins 950XL 3/4" (H), Wilkins 950 3/4" (H) | (M),A,B,C,D,E,F,G,H,I,J,K,L,N,O,P,Q,T
DCDA | Wilkins | 950DA | 6 | VU | 1996-12-12 | 2023-12-12 | N | 8 | hh,ff,mm,uu,zz,vvvv,wwww,yyyy,zzzz | Y | Wilkins 950XL 3/4" (VU) | (M),D,E,F,G,H,I,J,K,L,N,O,P,Q,T
DCDA | Wilkins | 950DA | 8 | H | 1993-06-09 | 2023-06-09 | N | 8 | (hh),ff,mm,uu,zz,vvvv,wwww,yyyy.zzzz | Y | Wilkins 950XL 3/4" (H), Wilkins 950 3/4" (H) | (M),E,F,G,H,I,J,K,L,N,O,P,Q,T
DCDA | Wilkins | 950DA | 8 | VU | 1996-12-12 | 2023-12-12 | N | 8 | (hh),ff,mm,uu,zz,vvvv,wwww,yyyy.zzzz | Y | Wilkins 950XL 3/4" (VU) | (M),A,B,C,D,E,F,G,H,I,J,K,L,N,O,P,Q,T
DCDA | Wilkins | 950DA | 10 | H | 1994-06-23 | 2024-06-23 | N | 8 | (hh),ff,mm,uu,zz,vvvv,wwww,yyyy.zzzz | Y | Wilkins 950XL 3/4" (H), Wilkins 950 3/4" (H) | (M),A,B,C,D,E,F,G,H,I,J,K,L,N,O,P,Q,T
DCDA | Wilkins | 950XLTDA | 2 | H | 2009-05-19 | 2024-05-19 | N | 9 | (bbb) | N | Wilkins 350D 3/4" (H) | (N),F,G,H,I,J,K,L,M,O,P,Q,T
DCDA | Wilkins | 950XLTDA | 2 | VU | 2009-06-22 | 2024-06-22 | N | 9 | (bbb) | N | Wilkins 350D 3/4" (VU) | (N),F,G,H,I,J,K,L,M,O,P,Q,T
DCDA | Wilkins | 950XLTDABF | 2 | H | 2009-05-19 | 2024-05-19 | N | 9 | (bbbbb), ccccc,pppppp | N | Wilkins 350D 3/4" (H) | (N),F,G,H,I,J,K,L,M,O,P,Q,T
DCDA | Wilkins | 950XLTDABF | 2 | VU | 2009-06-22 | 2024-06-22 | N | 9 | (bbbbb), ccccc,pppppp | N | Wilkins 350D 3/4" (VU) | (N),F,G,H,I,J,K,L,M,O,P,Q,T
DCDA | Wilkins | DCDA | 2.5 | H | 1987-03-05 | 2023-03-05 | N | 7 | hh,ff,mm,uu,zz | Y | Wilkins 550A 3/4" (H) | (M),B,C,D,E,F,G,H,I,J,K,L,N,O,P,Q,T
DCDA | Wilkins | DCDA | 3 | H | 1987-03-05 | 2023-03-05 | N | 7 | hh,ff,mm,uu,zz | Y | Wilkins 550A 3/4" (H) | (M),B,C,D,E,F,G,H,I,J,K,L,N,O,P,Q,T
DCDA | Wilkins | DCDA | 4 | H | 1988-05-18 | 2024-05-18 | N | 7 | hh,ff,mm,uu,zz | Y | Wilkins 550A 3/4" (H) | (M),A,B,C,D,E,F,G,H,I,J,K,L,N,O,P,Q,T
DCDA | Wilkins | DCDA | 6 | H | 1988-06-02 | 2024-06-01 | N | 7 | hh,ff,mm,uu,zz | Y | Wilkins 550A 3/4" (H) | (M),A,B,C,D,E,F,G,H,I,J,K,L,N,O,P,Q,T
DCDA-II | Ames | Deringer 30 | 2.5 | H | 2020-03-26 | 2023-03-26 | Y | 10 | (int) | N | Backflow Direct 1/2" CV(HVD) | (O),G,H,I,J,K,L,M,N,Q,T
DCDA-II | Ames | Deringer 30 | 2.5 | VU | 2020-03-26 | 2023-03-26 | Y | 10 | (int) | N | Backflow Direct 1/2" CV(VUH) | (O),G,H,I,J,K,L,M,N,Q,T
DCDA-II | Ames | Deringer 30 | 3 | H | 2020-03-26 | 2023-03-26 | Y | 10 | (int) | N | Backflow Direct 1/2" CV(HVD) | (O),G,H,I,J,K,L,M,N,Q,T
DCDA-II | Ames | Deringer 30 | 3 | VU | 2020-03-26 | 2023-03-26 | Y | 10 | (int) | N | Backflow Direct 1/2" CV(VUH) | (O),G,H,I,J,K,L,M,N,Q,T
DCDA-II | Ames | Deringer 30 | 4 | H | 2020-03-26 | 2023-03-26 | Y | 10 | (int) | N | Backflow Direct 1/2" CV(HVD) | (O),G,H,I,J,K,L,M,N,Q,T
DCDA-II | Ames | Deringer 30 | 4 | VU | 2020-03-26 | 2023-03-26 | Y | 10 | (int) | N | Backflow Direct 1/2" CV(VUH) | (O),G,H,I,J,K,L,M,N,Q,T
DCDA-II | Ames | Deringer 30 | 6 | H | 2020-03-26 | 2023-03-26 | Y | 10 | (int) | N | Backflow Direct 1/2" CV(HVD) | (O),G,H,I,J,K,L,M,N,Q,T
DCDA-II | Ames | Deringer 30 | 6 | VU | 2020-03-26 | 2023-03-26 | Y | 10 | (int) | N | Backflow Direct 1/2" CV(VUH) | (O),G,H,I,J,K,L,M,N,Q,T
DCDA-II | Ames | Deringer 30 | 8 | H | 2020-03-26 | 2023-03-26 | Y | 10 | (int) | N | Backflow Direct 1/2" CV(HVD) | (O),G,H,I,J,K,L,M,N,Q,T
DCDA-II | Ames | Deringer 30 | 8 | VU | 2020-03-26 | 2023-03-26 | Y | 10 | (int) | N | Backflow Direct 1/2" CV(VUH) | (O),G,H,I,J,K,L,M,N,Q,T
DCDA-II | Ames | Deringer 30G | 2.5 | H | 2020-03-26 | 2023-03-26 | Y | 10 | (ssssss), tttttt | N | Backflow Direct 1/2" CV(HVD) | (O),G,H,I,J,K,L,M,N,Q,T
DCDA-II | Ames | Deringer 30G | 2.5 | VU | 2020-03-26 | 2023-03-26 | Y | 10 | (ssssss), tttttt | N | Backflow Direct 1/2" CV(VUH) | (O),G,H,I,J,K,L,M,N,Q,T
DCDA-II | Ames | Deringer 30G | 3 | H | 2020-03-26 | 2023-03-26 | Y | 10 | (ssssss), tttttt | N | Backflow Direct 1/2" CV(HVD) | (O),G,H,I,J,K,L,M,N,Q,T
DCDA-II | Ames | Deringer 30G | 3 | VU | 2020-03-26 | 2023-03-26 | Y | 10 | (ssssss), tttttt | N | Backflow Direct 1/2" CV(VUH) | (O),G,H,I,J,K,L,M,N,Q,T
DCDA-II | Ames | Deringer 30G | 4 | H | 2020-03-26 | 2023-03-26 | Y | 10 | (ssssss), tttttt | N | Backflow Direct 1/2" CV(HVD) | (O),G,H,I,J,K,L,M,N,Q,T
DCDA-II | Ames | Deringer 30G | 4 | VU | 2020-03-26 | 2023-03-26 | Y | 10 | (ssssss), tttttt | N | Backflow Direct 1/2" CV(VUH) | (O),G,H,I,J,K,L,M,N,Q,T
DCDA-II | Ames | Deringer 30G | 6 | H | 2020-03-26 | 2023-03-26 | Y | 10 | (ssssss), tttttt | N | Backflow Direct 1/2" CV(HVD) | (O),G,H,I,J,K,L,M,N,Q,T
DCDA-II | Ames | Deringer 30G | 6 | VU | 2020-03-26 | 2023-03-26 | Y | 10 | (ssssss), tttttt | N | Backflow Direct 1/2" CV(VUH) | (O),G,H,I,J,K,L,M,N,Q,T
DCDA-II | Ames | Deringer 30G | 8 | H | 2020-03-26 | 2023-03-26 | Y | 10 | (ssssss), tttttt | N | Backflow Direct 1/2" CV(HVD) | (O),G,H,I,J,K,L,M,N,Q,T
DCDA-II | Ames | Deringer 30G | 8 | VU | 2020-03-26 | 2023-03-26 | Y | 10 | (ssssss), tttttt | N | Backflow Direct 1/2" CV(VUH) | (O),G,H,I,J,K,L,M,N,Q,T
DCDA-II | Ames | Deringer 30GX | 4 | H | 2020-03-26 | 2023-03-26 | Y | 10 | (ssssss), tttttt | N | Backflow Direct 1/2" CV(HVD) | (O),G,H,I,J,K,L,M,N,Q,T
DCDA-II | Ames | Deringer 30GX | 4 | VU | 2020-03-26 | 2023-03-26 | Y | 10 | (ssssss), tttttt | N | Backflow Direct 1/2" CV(VUH) | (O),G,H,I,J,K,L,M,N,Q,T
DCDA-II | Ames | Deringer 30GX | 6 | H | 2020-03-26 | 2023-03-26 | Y | 10 | (ssssss), tttttt | N | Backflow Direct 1/2" CV(HVD) | (O),G,H,I,J,K,L,M,N,Q,T
DCDA-II | Ames | Deringer 30GX | 6 | VU | 2020-03-26 | 2023-03-26 | Y | 10 | (ssssss), tttttt | N | Backflow Direct 1/2" CV(VUH) | (O),G,H,I,J,K,L,M,N,Q,T
DCDA-II | Ames | Deringer 30X | 4 | H | 2020-03-26 | 2023-03-26 | Y | 10 | (int) | N | Backflow Direct 1/2" CV(HVD) | (O),G,H,I,J,K,L,M,N,Q,T
DCDA-II | Ames | Deringer 30X | 4 | VU | 2020-03-26 | 2023-03-26 | Y | 10 | (int) | N | Backflow Direct 1/2" CV(VUH) | (O),G,H,I,J,K,L,M,N,Q,T
DCDA-II | Ames | Deringer 30X | 6 | H | 2020-03-26 | 2023-03-26 | Y | 10 | (int) | N | Backflow Direct 1/2" CV(HVD) | (O),G,H,I,J,K,L,M,N,Q,T
DCDA-II | Ames | Deringer 30X | 6 | VU | 2020-03-26 | 2023-03-26 | Y | 10 | (int) | N | Backflow Direct 1/2" CV(VUH) | (O),G,H,I,J,K,L,M,N,Q,T
DCDA-II | Apollo/Conbraco | DCDA24A | 1.5 | H | 2016-10-31 | 2022-10-31 | N | 10 | (dddddd) | N | Apollo 1/2" Model CVA4A (HVD) | (M),G,H,I,J,K,L,N,O,P,Q,T
DCDA-II | Apollo/Conbraco | DCDA24A | 1.5 | VU | 2016-10-31 | 2022-10-31 | N | 10 | (dddddd) | N | Apollo 1/2" Model CVA4A (VUH) | (M),G,H,I,J,K,L,N,O,P,Q,T
DCDA-II | Apollo/Conbraco | DCDA24A | 2 | H | 2016-10-31 | 2022-10-31 | N | 10 | (dddddd) | N | Apollo 1/2" Model CVA4A (HVD) | (M),G,H,I,J,K,L,N,O,P,Q,T
DCDA-II | Apollo/Conbraco | DCDA24A | 2 | VU | 2016-10-31 | 2022-10-31 | N | 10 | (dddddd) | N | Apollo 1/2" Model CVA4A (VUH) | (M),G,H,I,J,K,L,N,O,P,Q,T
DCDA-II | Apollo/Conbraco | DCDA2LF4A | 1.5 | H | 2016-10-31 | 2022-10-31 | N | 10 | (eeeeee) | N | Apollo 1/2" Model CVALF4A (HVD) | (M),G,H,I,J,K,L,N,O,P,Q,T
DCDA-II | Apollo/Conbraco | DCDA2LF4A | 1.5 | VU | 2016-10-31 | 2022-10-31 | N | 10 | (eeeeee) | N | Apollo 1/2" Model CVALF4A (VUH) | (M),G,H,I,J,K,L,N,O,P,Q,T
DCDA-II | Apollo/Conbraco | DCDA2LF4A | 2 | H | 2016-10-31 | 2022-10-31 | N | 10 | (eeeeee) | N | Apollo 1/2" Model CVALF4A (HVD) | (M),G,H,I,J,K,L,N,O,P,Q,T
DCDA-II | Apollo/Conbraco | DCDA2LF4A | 2 | VU | 2016-10-31 | 2022-10-31 | N | 10 | (eeeeee) | N | Apollo 1/2" Model CVALF4A (VUH) | (M),G,H,I,J,K,L,N,O,P,Q,T
DCDA-II | Apollo/Conbraco | DCDA2LF4A | 2.5 | H | 2017-12-15 | 2023-12-15 | Y | 10 | (xxxxx),yyy,yyyyy,zzzzz,aaaaaa,xxxxxx | N | Apollo 1/2" Model CVALF4A (HVD) | (M),G,H,I,J,K,L,N,O,P,Q,T
DCDA-II | Apollo/Conbraco | DCDA2LF4A | 2.5 | VU | 2017-12-15 | 2023-12-15 | Y | 10 | (xxxxx),yyy,yyyyy,zzzzz,aaaaaa,xxxxxx | N | Apollo 1/2" Model CVALF4A (VUH) | (M),G,H,I,J,K,L,N,O,P,Q,T
DCDA-II | Apollo/Conbraco | DCDA2LF4A | 3 | H | 2017-12-15 | 2023-12-15 | Y | 10 | (xxxxx),yyy,yyyyy,zzzzz,aaaaaa,xxxxxx | N | Apollo 1/2" Model CVALF4A (HVD) | (M),G,H,I,J,K,L,N,O,P,Q,T
DCDA-II | Apollo/Conbraco | DCDA2LF4A | 3 | VU | 2017-12-15 | 2023-12-15 | Y | 10 | (xxxxx),yyy,yyyyy,zzzzz,aaaaaa,xxxxxx | N | Apollo 1/2" Model CVALF4A (VUH) | (M),G,H,I,J,K,L,N,O,P,Q,T
DCDA-II | Apollo/Conbraco | DCDA2LF4A | 4 | H | 2017-12-15 | 2023-12-15 | Y | 10 | (xxxxx),yyy,yyyyy,zzzzz,aaaaaa,xxxxxx | N | Apollo 1/2" Model CVALF4A (HVD) | (M),G,H,I,J,K,L,N,O,P,Q,T
DCDA-II | Apollo/Conbraco | DCDA2LF4A | 4 | VU | 2017-12-15 | 2023-12-15 | Y | 10 | (xxxxx),yyy,yyyyy,zzzzz,aaaaaa,xxxxxx | N | Apollo 1/2" Model CVALF4A (H) | (M),G,H,I,J,K,L,N,O,P,Q,T
DCDA-II | Apollo/Conbraco | DCDA2LF4A | 6 | H | 2017-12-15 | 2023-12-15 | Y | 10 | (xxxxx),yyy,yyyyy,zzzzz,aaaaaa,xxxxxx | N | Apollo 1/2" Model CVALF4A (HVD) | (M),G,H,I,J,K,L,N,O,P,Q,T
DCDA-II | Apollo/Conbraco | DCDA2LF4A | 6 | VU | 2017-12-15 | 2023-12-15 | Y | 10 | (xxxxx),yyy,yyyyy,zzzzz,aaaaaa,xxxxxx | N | Apollo 1/2" Model CVALF4A (H) | (M),G,H,I,J,K,L,N,O,P,Q,T
DCDA-II | Apollo/Conbraco | DCDA2LF4A | 8 | H | 2017-12-15 | 2023-12-15 | Y | 10 | (xxxxx),yyy,yyyyy,zzzzz,aaaaaa,xxxxxx | N | Apollo 1/2" Model CVALF4A (HVD) | (M),G,H,I,J,K,L,N,O,P,Q,T
DCDA-II | Apollo/Conbraco | DCDA2LF4A | 8 | VU | 2017-12-15 | 2023-12-15 | Y | 10 | (xxxxx),yyy,yyyyy,zzzzz,aaaaaa,xxxxxx | N | Apollo 1/2" Model CVALF4A (H) | (M),G,H,I,J,K,L,N,O,P,Q,T
DCDA-II | Apollo/Conbraco | DCDA2LF4A | 10 | H | 2021-11-05 | 2024-11-05 | Y | 10 | (zzzzz), zzz,cccc,dddd,kkkk,llll,mmmm,nnnn,xxxxx, yyyyy,aaaaaa | N | Apollo 1/2" Model CVALF4A (HVD) | (M),G,H,I,J,K,L,N,O,P,Q,T
DCDA-II | Apollo/Conbraco | DCDA2LF4A | 12 | H | 2021-11-05 | 2024-11-05 | Y | 10 | (bbbbbb), ll,mm,cccccc | N | Apollo 1/2" Model CVALF4A (HVD) | (M),G,H,I,J,K,L,N,O,P,Q,T
DCDA-II | Apollo/Conbraco | DCDA2LF4AN | 10 | VUVD | 2022-04-12 |  | Y | 10 | (zzzzz), yyy,zzz,cccc,dddd,kkkk,llll,mmmm,nnnn,xxxxx, yyyyy,aaaaaa | N | Apollo 1/2" Model CVALF4A (HVD) | (M),G,H,I,J,K,L,N,O,P,Q,T
DCDA-II | Apollo/Conbraco | DCDA2LF4AN | 12 | VUVD | 2022-04-12 |  | Y | 10 | (bbbbbb), ll,mm,cccccc | N | Apollo 1/2" Model CVALF4A (HVD) | (M),G,H,I,J,K,L,N,O,P,Q,T
DCDA-II | Apollo/Conbraco | DCDA2LF4AR | 2.5 | H | 2018-03-27 | 2024-03-27 | Y | 10 | (xxxxx),zzz,cccc,dddd,kkkk,llll,mmmm,nnnn,yyyyy,zzzzz,aaaaaa | Y | Apollo 1/2" Model CVALF4A (HVD) | (M),G,H,I,J,K,L,N,O,Q,T | Integral Stainless Steel grooved spool between the #2 ck and #2 SOV - assembly length: min. 34" and max. 47 1/8"
DCDA-II | Apollo/Conbraco | DCDA2LF4AR | 2.5 | VU | 2018-03-27 | 2024-03-27 | Y | 10 | (xxxxx),zzz,cccc,dddd,kkkk,llll,mmmm,nnnn,yyyyy,zzzzz,aaaaaa | Y | Apollo 1/2" Model CVALF4A (VUH) | (M),G,H,I,J,K,L,N,O,Q,T | Integral Stainless Steel grooved spool between the #2 ck and #2 SOV - assembly length: min. 34" and max. 47 1/8"
DCDA-II | Apollo/Conbraco | DCDA2LF4AR | 3 | H | 2018-03-27 | 2024-03-27 | Y | 10 | (xxxxx),zzz,cccc,dddd,kkkk,llll,mmmm,nnnn,yyyyy,zzzzz,aaaaaa | Y | Apollo 1/2" Model CVALF4A (HVD) | (M),G,H,I,J,K,L,N,O,Q,T | Integral Stainless Steel grooved spool between the #2 ck and #2 SOV - assembly length: min. 35" and max. 48 1/8"
DCDA-II | Apollo/Conbraco | DCDA2LF4AR | 3 | VU | 2018-03-27 | 2024-03-27 | Y | 10 | (xxxxx),zzz,cccc,dddd,kkkk,llll,mmmm,nnnn,yyyyy,zzzzz,aaaaaa | Y | Apollo 1/2" Model CVALF4A (VUH) | (M),G,H,I,J,K,L,N,O,Q,T | Integral Stainless Steel grooved spool between the #2 ck and #2 SOV - assembly length: min. 35" and max. 48 1/8"
DCDA-II | Apollo/Conbraco | DCDA2LF4AR | 4 | H | 2018-03-27 | 2024-03-27 | Y | 10 | (xxxxx),zzz,cccc,dddd,kkkk,llll,mmmm,nnnn,yyyyy,zzzzz,aaaaaa | Y | Apollo 1/2" Model CVALF4A (HVD) | (M),G,H,I,J,K,L,N,O,Q,T | Integral Stainless Steel grooved spool between the #2 ck and #2 SOV - assembly length: min. 37 3/8" and max. 62 1/4"
DCDA-II | Apollo/Conbraco | DCDA2LF4AR | 4 | VU | 2018-03-27 | 2024-03-27 | Y | 10 | (xxxxx),zzz,cccc,dddd,kkkk,llll,mmmm,nnnn,yyyyy,zzzzz,aaaaaa | Y | Apollo 1/2" Model CVALF4A (H) | (M),G,H,I,J,K,L,N,O,Q,T | Integral Stainless Steel grooved spool between the #2 ck and #2 SOV - assembly length: min. 37 3/8" and max. 62 1/4"
DCDA-II | Apollo/Conbraco | DCDA2LF4AR | 6 | H | 2018-03-27 | 2024-03-27 | Y | 10 | (xxxxx),zzz,cccc,dddd,kkkk,llll,mmmm,nnnn,yyyyy,zzzzz,aaaaaa | Y | Apollo 1/2" Model CVALF4A (HVD) | (M),G,H,I,J,K,L,N,O,Q,T | Integral Stainless Steel grooved spool between the #2 ck and #2 SOV - assembly length: min. 46" and max. 71 1/4"
DCDA-II | Apollo/Conbraco | DCDA2LF4AR | 6 | VU | 2018-03-27 | 2024-03-27 | Y | 10 | (xxxxx),zzz,cccc,dddd,kkkk,llll,mmmm,nnnn,yyyyy,zzzzz,aaaaaa | Y | Apollo 1/2" Model CVALF4A (H) | (M),G,H,I,J,K,L,N,O,Q,T | Integral Stainless Steel grooved spool between the #2 ck and #2 SOV - assembly length: min. 46" and max. 71 1/4"
DCDA-II | Apollo/Conbraco | DCDA2LF4AR | 8 | H | 2018-03-27 | 2024-03-27 | Y | 10 | (xxxxx),zzz,cccc,dddd,kkkk,llll,mmmm,nnnn,yyyyy,zzzzz,aaaaaa | Y | Apollo 1/2" Model CVALF4A (HVD) | (M),G,H,I,J,K,L,N,O,Q,T | Integral Stainless Steel grooved spool between the #2 ck and #2 SOV - assembly length: min. 55 3/4" and max. 86"
DCDA-II | Apollo/Conbraco | DCDA2LF4AR | 8 | VU | 2018-03-27 | 2024-03-27 | Y | 10 | (xxxxx),zzz,cccc,dddd,kkkk,llll,mmmm,nnnn,yyyyy,zzzzz,aaaaaa | Y | Apollo 1/2" Model CVALF4A (H) | (M),G,H,I,J,K,L,N,O,Q,T | Integral Stainless Steel grooved spool between the #2 ck and #2 SOV - assembly length: min. 55 3/4" and max. 86"
DCDA-II | Apollo/Conbraco | DCDA2LF4AR | 10 | H | 2021-11-05 | 2024-11-05 | Y | 10 | (zzzzz), zzz,cccc,dddd,kkkk,llll,mmmm,nnnn,xxxxx, yyyyy,aaaaaa | Y | Apollo 1/2" Model CVALF4A (HVD) | (M),G,H,I,J,K,L,N,O,P,Q,T | Integral Stainless Steel grooved spool between the #2 ck and #2 SOV - assembly length: min. 65 3/4" and max. 100 5/8"
DCDA-II | Backflow Direct | Deringer 30 | 2.5 | H | 2015-12-21 | 2024-12-21 | Y | 10 | (int) | N | Backflow Direct 1/2" CV(HVD) | (O),G,H,I,J,K,L,M,N,Q,T
DCDA-II | Backflow Direct | Deringer 30 | 2.5 | VU | 2015-12-21 | 2024-12-21 | Y | 10 | (int) | N | Backflow Direct 1/2" CV(VUH) | (O),G,H,I,J,K,L,M,N,Q,T
DCDA-II | Backflow Direct | Deringer 30 | 3 | H | 2015-12-21 | 2024-12-21 | Y | 10 | (int) | N | Backflow Direct 1/2" CV(HVD) | (O),G,H,I,J,K,L,M,N,Q,T
DCDA-II | Backflow Direct | Deringer 30 | 3 | VU | 2015-12-21 | 2024-12-21 | Y | 10 | (int) | N | Backflow Direct 1/2" CV(VUH) | (O),G,H,I,J,K,L,M,N,Q,T
DCDA-II | Backflow Direct | Deringer 30 | 4 | H | 2015-09-30 | 2024-09-30 | Y | 10 | (int) | N | Backflow Direct 1/2" CV(HVD) | (O),G,H,I,J,K,L,M,N,Q,T
DCDA-II | Backflow Direct | Deringer 30 | 4 | VU | 2015-09-30 | 2024-09-30 | Y | 10 | (int) | N | Backflow Direct 1/2" CV(VUH) | (O),G,H,I,J,K,L,M,N,Q,T
DCDA-II | Backflow Direct | Deringer 30 | 6 | H | 2019-10-30 | 2022-10-30 | Y | 10 | (int) | N | Backflow Direct 1/2" CV(HVD) | (O),G,H,I,J,K,L,M,N,Q,T
DCDA-II | Backflow Direct | Deringer 30 | 6 | VU | 2019-10-30 | 2022-10-30 | Y | 10 | (int) | N | Backflow Direct 1/2" CV(VUH) | (O),G,H,I,J,K,L,M,N,Q,T
DCDA-II | Backflow Direct | Deringer 30 | 8 | H | 2016-12-23 | 2022-12-23 | Y | 10 | (int) | N | Backflow Direct 1/2" CV(HVD) | (O),G,H,I,J,K,L,M,N,Q,T
DCDA-II | Backflow Direct | Deringer 30 | 8 | VU | 2016-12-23 | 2022-12-23 | Y | 10 | (int) | N | Backflow Direct 1/2" CV(VUH) | (O),G,H,I,J,K,L,M,N,Q,T
DCDA-II | Backflow Direct | Deringer 30G | 2.5 | H | 2018-12-07 | 2024-12-07 | Y | 10 | (ssssss), tttttt | N | Backflow Direct 1/2" CV(HVD) | (O),G,H,I,J,K,L,M,N,Q,T
DCDA-II | Backflow Direct | Deringer 30G | 2.5 | VU | 2018-12-07 | 2024-12-07 | Y | 10 | (ssssss), tttttt | N | Backflow Direct 1/2" CV(VUH) | (O),G,H,I,J,K,L,M,N,Q,T
DCDA-II | Backflow Direct | Deringer 30G | 3 | H | 2018-12-07 | 2024-12-07 | Y | 10 | (ssssss), tttttt | N | Backflow Direct 1/2" CV(HVD) | (O),G,H,I,J,K,L,M,N,Q,T
DCDA-II | Backflow Direct | Deringer 30G | 3 | VU | 2018-12-07 | 2024-12-07 | Y | 10 | (ssssss), tttttt | N | Backflow Direct 1/2" CV(VUH) | (O),G,H,I,J,K,L,M,N,Q,T
DCDA-II | Backflow Direct | Deringer 30G | 4 | H | 2018-12-07 | 2024-12-07 | Y | 10 | (ssssss), tttttt | N | Backflow Direct 1/2" CV(HVD) | (O),G,H,I,J,K,L,M,N,Q,T
DCDA-II | Backflow Direct | Deringer 30G | 4 | VU | 2018-12-07 | 2024-12-07 | Y | 10 | (ssssss), tttttt | N | Backflow Direct 1/2" CV(VUH) | (O),G,H,I,J,K,L,M,N,Q,T
DCDA-II | Backflow Direct | Deringer 30G | 6 | H | 2020-01-16 | 2023-01-16 | Y | 10 | (ssssss), tttttt | N | Backflow Direct 1/2" CV(HVD) | (O),G,H,I,J,K,L,M,N,Q,T
DCDA-II | Backflow Direct | Deringer 30G | 6 | VU | 2020-01-16 | 2023-01-16 | Y | 10 | (ssssss), tttttt | N | Backflow Direct 1/2" CV(VUH) | (O),G,H,I,J,K,L,M,N,Q,T
DCDA-II | Backflow Direct | Deringer 30G | 8 | H | 2018-07-31 | 2024-07-31 | Y | 10 | (ssssss), tttttt | N | Backflow Direct 1/2" CV(HVD) | (O),G,H,I,J,K,L,M,N,Q,T
DCDA-II | Backflow Direct | Deringer 30G | 8 | VU | 2018-07-31 | 2024-07-31 | Y | 10 | (ssssss), tttttt | N | Backflow Direct 1/2" CV(VUH) | (O),G,H,I,J,K,L,M,N,Q,T
DCDA-II | Backflow Direct | Deringer 30GX | 4 | H | 2020-01-16 | 2023-01-16 | Y | 10 | (ssssss), tttttt | N | Backflow Direct 1/2" CV(HVD) | (O),G,H,I,J,K,L,M,N,Q,T
DCDA-II | Backflow Direct | Deringer 30GX | 4 | VU | 2020-01-16 | 2023-01-16 | Y | 10 | (ssssss), tttttt | N | Backflow Direct 1/2" CV(VUH) | (O),G,H,I,J,K,L,M,N,Q,T
DCDA-II | Backflow Direct | Deringer 30GX | 6 | H | 2018-07-31 | 2024-07-31 | Y | 10 | (ssssss), tttttt | N | Backflow Direct 1/2" CV(HVD) | (O),G,H,I,J,K,L,M,N,Q,T
DCDA-II | Backflow Direct | Deringer 30GX | 6 | VU | 2018-07-31 | 2024-07-31 | Y | 10 | (ssssss), tttttt | N | Backflow Direct 1/2" CV(VUH) | (O),G,H,I,J,K,L,M,N,Q,T
DCDA-II | Backflow Direct | Deringer 30X | 4 | H | 2019-10-30 | 2022-10-30 | Y | 10 | (int) | N | Backflow Direct 1/2" CV(HVD) | (O),G,H,I,J,K,L,M,N,Q,T
DCDA-II | Backflow Direct | Deringer 30X | 4 | VU | 2019-10-30 | 2022-10-30 | Y | 10 | (int) | N | Backflow Direct 1/2" CV(VUH) | (O),G,H,I,J,K,L,M,N,Q,T
DCDA-II | Backflow Direct | Deringer 30X | 6 | H | 2016-12-23 | 2022-12-23 | Y | 10 | (int) | N | Backflow Direct 1/2" CV(HVD) | (O),G,H,I,J,K,L,M,N,Q,T
DCDA-II | Backflow Direct | Deringer 30X | 6 | VU | 2016-12-23 | 2022-12-23 | Y | 10 | (int) | N | Backflow Direct 1/2" CV(VUH) | (O),G,H,I,J,K,L,M,N,Q,T
DCDA-II | Febco | LF856 | 2.5 | H | 2015-03-20 | 2024-03-20 | Y | 10 | (mm), ll,oo,pp,zzz,cccc,dddd,eeee,ffff,gggg,nnnnn,aaaaaaa | N | Watts 3/4" LF619 (H) | (O),G,H,I,J,K,L,M,N,P,Q,T
DCDA-II | Febco | LF856 | 2.5 | VU | 2015-03-20 | 2024-03-20 | Y | 10 | (mm), ll,oo,pp,zzz,cccc,dddd,eeee,ffff,gggg,nnnnn,aaaaaaa | N | Watts 3/4" LF619 (HVU) | (O),G,H,I,J,K,L,M,N,P,Q,T
DCDA-II | Febco | LF856 | 3 | H | 2015-03-20 | 2024-03-20 | Y | 10 | (mm), ll,oo,pp,zzz,cccc,dddd,eeee,ffff,gggg,nnnnn,aaaaaaa | N | Watts 3/4" LF619 (H) | (O),G,H,I,J,K,L,M,N,P,Q,T
DCDA-II | Febco | LF856 | 3 | VU | 2015-03-20 | 2024-03-20 | Y | 10 | (mm), ll,oo,pp,zzz,cccc,dddd,eeee,ffff,gggg,nnnnn,aaaaaaa | N | Watts 3/4" LF619 (HVU) | (O),G,H,I,J,K,L,M,N,P,Q,T
DCDA-II | Febco | LF856 | 4 | H | 2015-01-26 | 2024-01-26 | Y | 10 | (mm), ll,oo,pp,zzz,cccc,dddd,eeee,ffff,gggg,nnnnn,aaaaaaa | N | Watts 3/4" LF619 (H) | (O),G,H,I,J,K,L,M,N,P,Q,T
DCDA-II | Febco | LF856 | 4 | VU | 2015-01-26 | 2024-01-26 | Y | 10 | (mm), ll,oo,pp,zzz,cccc,dddd,eeee,ffff,gggg,nnnnn,aaaaaaa | N | Watts 3/4" LF619 (HVU) | (O),G,H,I,J,K,L,M,N,P,Q,T
DCDA-II | Febco | LF856 | 6 | H | 2015-03-13 | 2024-03-13 | Y | 10 | (mm), ll,oo,pp,zzz,cccc,dddd,eeee,ffff,gggg,nnnnn,aaaaaaa | N | Watts 3/4" LF619 (H) | (O),G,H,I,J,K,L,M,N,P,Q,T
DCDA-II | Febco | LF856 | 6 | VU | 2015-03-13 | 2024-03-13 | Y | 10 | (mm), ll,oo,pp,zzz,cccc,dddd,eeee,ffff,gggg,nnnnn,aaaaaaa | N | Watts 3/4" LF619 (HVU) | (O),G,H,I,J,K,L,M,N,P,Q,T
DCDA-II | Febco | LF856 | 8 | H | 2015-07-07 | 2024-07-07 | Y | 10 | (mm), ll,oo,pp,zzz,cccc,dddd,eeee,ffff,gggg,nnnnn,aaaaaaa | N | Watts 3/4" LF619 (H) | (O),G,H,I,J,K,L,M,N,P,Q,T
DCDA-II | Febco | LF856 | 8 | VU | 2015-07-07 | 2024-07-07 | Y | 10 | (mm), ll,oo,pp,zzz,cccc,dddd,eeee,ffff,gggg,nnnnn,aaaaaaa | N | Watts 3/4" LF619 (HVU) | (O),G,H,I,J,K,L,M,N,P,Q,T
DCDA-II | Febco | LF856 | 10 | H | 2015-07-07 | 2024-07-07 | Y | 10 | (mm), ll,oo,pp,zzz,cccc,dddd,eeee,ffff,gggg,nnnnn | N | Watts 3/4" LF619 (H) | (O),G,H,I,J,K,L,M,N,P,Q,T
DCDA-II | Febco | LF856 | 10 | VU | 2015-07-07 | 2024-07-07 | Y | 10 | (mm), ll,oo,pp,zzz,cccc,dddd,eeee,ffff,gggg,nnnnn | N | Watts 3/4" LF619 (HVU) | (O),G,H,I,J,K,L,M,N,P,Q,T
DCDA-II | Febco | LF876V | 2.5 | VUVD | 2015-03-20 | 2024-03-20 | Y | 10 | (mm), ll,oo,pp,zzz,cccc,dddd,eeee,ffff,gggg,nnnnn,aaaaaaa | N | Watts 3/4" LF619 (HVD) | (O),G,H,I,J,K,L,M,N,P,Q,T
DCDA-II | Febco | LF876V | 2.5 | VUVU | 2015-03-20 | 2024-03-20 | Y | 10 | (mm), ll,oo,pp,zzz,cccc,dddd,eeee,ffff,gggg,nnnnn,aaaaaaa | N | Watts 3/4" LF619 (HVD) | (O),G,H,I,J,K,L,M,N,P,Q,T
DCDA-II | Febco | LF876V | 3 | VUVD | 2015-03-20 | 2024-03-20 | Y | 10 | (mm), ll,oo,pp,zzz,cccc,dddd,eeee,ffff,gggg,nnnnn,aaaaaaa | N | Watts 3/4" LF619 (HVU) | (O),G,H,I,J,K,L,M,N,P,Q,T
DCDA-II | Febco | LF876V | 3 | VUVU | 2015-03-20 | 2024-03-20 | Y | 10 | (mm), ll,oo,pp,zzz,cccc,dddd,eeee,ffff,gggg,nnnnn,aaaaaaa | N | Watts 3/4" LF619 (HVD) | (O),G,H,I,J,K,L,M,N,P,Q,T
DCDA-II | Febco | LF876V | 4 | VUVD | 2015-01-26 | 2024-01-26 | Y | 10 | (mm), ll,oo,pp,zzz,cccc,dddd,eeee,ffff,gggg,nnnnn,aaaaaaa | N | Watts 3/4" LF619 (HVU) | (O),G,H,I,J,K,L,M,N,P,Q,T
DCDA-II | Febco | LF876V | 4 | VUVU | 2015-01-26 | 2024-01-26 | Y | 10 | (mm), ll,oo,pp,zzz,cccc,dddd,eeee,ffff,gggg,nnnnn,aaaaaaa | N | Watts 3/4" LF619 (HVD) | (O),G,H,I,J,K,L,M,N,P,Q,T
DCDA-II | Febco | LF876V | 6 | VUVD | 2015-01-26 | 2024-01-26 | Y | 10 | (mm), ll,oo,pp,zzz,cccc,dddd,eeee,ffff,gggg,nnnnn,aaaaaaa | N | Watts 3/4" LF619 (HVU) | (O),G,H,I,J,K,L,M,N,P,Q,T
DCDA-II | Febco | LF876V | 6 | VUVU | 2015-01-26 | 2024-01-26 | Y | 10 | (mm), ll,oo,pp,zzz,cccc,dddd,eeee,ffff,gggg,nnnnn,aaaaaaa | N | Watts 3/4" LF619 (HVD) | (O),J,K,L,M,N,P,Q
DCDA-II | Febco | LF876V | 8 | VUVD | 2015-07-07 | 2024-07-07 | Y | 10 | (mm), ll,oo,pp,zzz,cccc,dddd,eeee,ffff,gggg,nnnnn,aaaaaaa | N | Watts 3/4" LF619 (HVU) | (O),G,H,I,J,K,L,M,N,P,Q,T
DCDA-II | Febco | LF876V | 8 | VUVU | 2015-07-07 | 2024-07-07 | Y | 10 | (mm), ll,oo,pp,zzz,cccc,dddd,eeee,ffff,gggg,nnnnn,aaaaaaa | N | Watts 3/4" LF619 (HVD) | (O),G,H,I,J,K,L,M,N,P,Q,T
DCDA-II | Febco | LF876V | 10 | VUVD | 2018-05-29 | 2024-05-29 | Y | 10 | (mm),ll,oo,pp,zzz,cccc,dddd,eeee,ffff,gggg,nnnnn | N | Watts 3/4" LF619 (HVU) | (O),G,H,I,J,K,L,M,N,P,Q,T
DCDA-II | Febco | LF876V | 10 | VUVU | 2018-05-29 | 2024-05-29 | Y | 10 | (mm),ll,oo,pp,zzz,cccc,dddd,eeee,ffff,gggg,nnnnn | N | Watts 3/4" LF619 (HVD) | (O),G,H,I,J,K,L,M,N,P,Q,T
DCDA-II | Febco | LF876W | 4 | VUVD | 2020-03-26 | 2023-03-26 | Y | 10 | (mm), ll,oo,pp,zzz,cccc,dddd,eeee,ffff,gggg,nnnnn,aaaaaaa | N | Watts 3/4" LF619 (HVU) | (O),G,H,I,J,K,L,M,N,P,Q,T
DCDA-II | Febco | LF876W | 4 | VUVU | 2020-03-26 | 2023-03-26 | Y | 10 | (mm), ll,oo,pp,zzz,cccc,dddd,eeee,ffff,gggg,nnnnn,aaaaaaa | N | Watts 3/4" LF619 (HVD) | (O),G,H,I,J,K,L,M,N,P,Q,T
DCDA-II | Febco | LF876W | 6 | VUVD | 2020-03-26 | 2023-03-26 | Y | 10 | (mm), ll,oo,pp,zzz,cccc,dddd,eeee,ffff,gggg,nnnnn,aaaaaaa | N | Watts 3/4" LF619 (HVU) | (O),G,H,I,J,K,L,M,N,P,Q,T
DCDA-II | Febco | LF876W | 6 | VUVU | 2020-03-26 | 2023-03-26 | Y | 10 | (mm), ll,oo,pp,zzz,cccc,dddd,eeee,ffff,gggg,nnnnn,aaaaaaa | N | Watts 3/4" LF619 (HVD) | (O),G,H,I,J,K,L,M,N,P,Q,T
DCDA-II | Febco | LF876W | 8 | VUVD | 2020-05-15 | 2023-05-15 | Y | 10 | (mm), ll,oo,pp,zzz,cccc,dddd,eeee,ffff,gggg,nnnnn,aaaaaaa | N | Watts 3/4" LF619 (HVU) | (O),G,H,I,J,K,L,M,N,P,Q,T
DCDA-II | Febco | LF876W | 8 | VUVU | 2020-05-15 | 2023-05-15 | Y | 10 | (mm), ll,oo,pp,zzz,cccc,dddd,eeee,ffff,gggg,nnnnn,aaaaaaa | N | Watts 3/4" LF619 (HVD) | (O),G,H,I,J,K,L,M,N,P,Q,T
DCDA-II | Febco | LF876W | 10 | VUVD | 2020-05-15 | 2023-05-15 | Y | 10 | (mm),ll,oo,pp,zzz,cccc,dddd,eeee,ffff,gggg,nnnnn | N | Watts 3/4" LF619 (HVU) | (O),G,H,I,J,K,L,M,N,P,Q,T
DCDA-II | Febco | LF876W | 10 | VUVU | 2020-05-15 | 2023-05-15 | Y | 10 | (mm),ll,oo,pp,zzz,cccc,dddd,eeee,ffff,gggg,nnnnn | N | Watts 3/4" LF619 (HVD) | (O),G,H,I,J,K,L,M,N,P,Q,T
DCDA-II | Febco | LF876WZ | 4 | VUVD | 2020-03-26 | 2023-03-26 | Y | 10 | (mm), ll,oo,pp,zzz,cccc,dddd,eeee,ffff,gggg,nnnnn,aaaaaaa | N | Watts 3/4" LF619 (HVU) | (O),G,H,I,J,K,L,M,N,P,Q,T
DCDA-II | Febco | LF876WZ | 4 | VUVU | 2020-03-26 | 2023-03-26 | Y | 10 | (mm), ll,oo,pp,zzz,cccc,dddd,eeee,ffff,gggg,nnnnn,aaaaaaa | N | Watts 3/4" LF619 (HVD) | (O),G,H,I,J,K,L,M,N,P,Q,T
DCDA-II | Febco | LF876WZ | 6 | VUVD | 2020-03-26 | 2023-03-26 | Y | 10 | (mm), ll,oo,pp,zzz,cccc,dddd,eeee,ffff,gggg,nnnnn,aaaaaaa | N | Watts 3/4" LF619 (HVU) | (O),G,H,I,J,K,L,M,N,P,Q,T
DCDA-II | Febco | LF876WZ | 6 | VUVU | 2020-03-26 | 2023-03-26 | Y | 10 | (mm), ll,oo,pp,zzz,cccc,dddd,eeee,ffff,gggg,nnnnn,aaaaaaa | N | Watts 3/4" LF619 (HVD) | (O),G,H,I,J,K,L,M,N,P,Q,T
DCDA-II | Febco | LF876WZ | 8 | VUVD | 2020-05-15 | 2023-05-15 | Y | 10 | (mm), ll,oo,pp,zzz,cccc,dddd,eeee,ffff,gggg,nnnnn,aaaaaaa | N | Watts 3/4" LF619 (HVU) | (O),G,H,I,J,K,L,M,N,P,Q,T
DCDA-II | Febco | LF876WZ | 8 | VUVU | 2020-05-15 | 2023-05-15 | Y | 10 | (mm), ll,oo,pp,zzz,cccc,dddd,eeee,ffff,gggg,nnnnn,aaaaaaa | N | Watts 3/4" LF619 (HVD) | (O),G,H,I,J,K,L,M,N,P,Q,T
DCDA-II | Febco | LF876WZ | 10 | VUVD | 2020-05-15 | 2023-05-15 | Y | 10 | (mm),ll,oo,pp,zzz,cccc,dddd,eeee,ffff,gggg,nnnnn | N | Watts 3/4" LF619 (HVU) | (O),G,H,I,J,K,L,M,N,P,Q,T
DCDA-II | Febco | LF876WZ | 10 | VUVU | 2020-05-15 | 2023-05-15 | Y | 10 | (mm),ll,oo,pp,zzz,cccc,dddd,eeee,ffff,gggg,nnnnn | N | Watts 3/4" LF619 (HVD) | (O),G,H,I,J,K,L,M,N,P,Q,T
PVB | Ames | A200 | 0.75 | VUH | 1993-04-06 | 2023-04-06 | N | 8 | (vv),xx,ooo,hhhh,pppp | Y
PVB | Ames | A200 | 1 | VUH | 1993-05-25 | 2023-05-25 | N | 8 | (vv),xx,ooo,hhhh,pppp | Y
PVB | Ames | A200 | 1.5 | VUH | 1993-06-21 | 2023-06-21 | N | 8 | (vv),xx,ooo,hhhh,pppp | Y
PVB | Ames | A200 | 2 | VUH | 1993-06-21 | 2023-06-21 | N | 8 | (vv),xx,ooo,hhhh,pppp | Y
PVB | Apollo/Conbraco | 4050302 | 0.5 | VUH | 1991-09-06 | 2024-09-06 | N | 8 | dd | Y
PVB | Apollo/Conbraco | 4050402 | 0.75 | VUH | 1991-09-06 | 2024-09-06 | N | 8 | (dd) | Y
PVB | Apollo/Conbraco | 4050502 | 1 | VUH | 1991-09-06 | 2024-09-06 | N | 8 | (dd) | Y
PVB | Apollo/Conbraco | 4050602 | 1.25 | VUH | 1993-12-01 | 2023-12-01 | N | 8 | (dd) | Y
PVB | Apollo/Conbraco | 4050702 | 1.5 | VUH | 1993-12-01 | 2023-12-01 | N | 8 | (dd) | Y
PVB | Apollo/Conbraco | 4050802 | 2 | VUH | 1993-12-01 | 2023-12-01 | N | 8 | (dd) | Y
PVB | Apollo/Conbraco | PVB | 0.5 | [9 empty] | model designation changed to PVB4V
PVB | Apollo/Conbraco | PVB | 0.75 | [9 empty] | model designation changed to PVB4V
PVB | Apollo/Conbraco | PVB | 1 | [9 empty] | model designation changed to PVB4V
PVB | Apollo/Conbraco | PVB | 1.25 | [9 empty] | model designation changed to PVB4V
PVB | Apollo/Conbraco | PVB | 1.5 | [9 empty] | model designation changed to PVB4V
PVB | Apollo/Conbraco | PVB | 2 | [9 empty] | model designation changed to PVB4V
PVB | Apollo/Conbraco | PVB4A | 0.5 | VUH | 2010-11-18 | 2022-11-18 | N | 9 | (iiiii),sssss | N
PVB | Apollo/Conbraco | PVB4A | 0.75 | VUH | 2010-11-18 | 2022-11-18 | N | 9 | (iiiii),sssss | N
PVB | Apollo/Conbraco | PVB4A | 1 | VUH | 2010-11-18 | 2022-11-18 | N | 9 | (iiiii),sssss | N
PVB | Apollo/Conbraco | PVB4A | 1.25 | VUH | 2011-04-27 | 2023-04-27 | N | 9 | (iiiii),sssss | N
PVB | Apollo/Conbraco | PVB4A | 1.5 | VUH | 2011-04-27 | 2023-04-27 | N | 9 | (iiiii),sssss | N
PVB | Apollo/Conbraco | PVB4A | 2 | VUH | 2012-01-30 | 2024-01-30 | N | 9 | (iiiii),sssss | N
PVB | Apollo/Conbraco | PVB4V | 0.5 | VUH | 1999-09-23 | 2023-09-23 | N | 9 | (dd) | Y |  |  | formerly PVB
PVB | Apollo/Conbraco | PVB4V | 0.75 | VUH | 1999-09-23 | 2023-09-23 | N | 9 | (dd) | Y |  |  | formerly PVB
PVB | Apollo/Conbraco | PVB4V | 1 | VUH | 1999-09-23 | 2023-09-23 | N | 9 | (dd) | Y |  |  | formerly PVB
PVB | Apollo/Conbraco | PVB4V | 1.25 | VUH | 2002-10-07 | 2023-10-07 | N | 9 | (dd) | Y |  |  | formerly PVB
PVB | Apollo/Conbraco | PVB4V | 1.5 | VUH | 2002-10-07 | 2023-10-07 | N | 9 | (dd) | Y |  |  | formerly PVB
PVB | Apollo/Conbraco | PVB4V | 2 | VUH | 2003-06-18 | 2024-06-18 | N | 9 | (dd) | Y |  |  | formerly PVB
PVB | ARI | VB-501 | 0.5 | VUH | 2018-09-06 | 2024-09-06 | N | 10 | (int) | N
PVB | ARI | VB-501 | 0.75 | VUH | 2018-06-13 | 2024-06-13 | N | 10 | (int) | N
PVB | ARI | VB-501 | 1 | VUH | 2018-06-13 | 2024-06-13 | N | 10 | (int) | N
PVB | Conbraco | [5 empty] | N | [5 empty] | See Apollo/Conbraco
PVB | Febco | 765 | 0.5 | VUH | 1974-03-26 | 2022-03-26 | N | 5 | (ii),fff,jjj,ooo | N
PVB | Febco | 765 | 0.75 | VUH | 1974-03-26 | 2022-03-26 | N | 5 | (ii),fff,jjj,ooo,xxx | N
PVB | Febco | 765 | 1 | VUH | 1974-03-26 | 2022-03-26 | N | 5 | (ii),fff,jjj,ooo,xxx | N
PVB | Febco | 765 | 1.25 | VUH | 1974-03-26 | 2022-03-26 | N | 5 | (ii),fff,jjj,ooo | N
PVB | Febco | 765 | 1.5 | VUH | 1974-03-26 | 2022-03-26 | N | 5 | (ii),fff,jjj,ooo,xxx | N
PVB | Febco | 765 | 2 | VUH | 1974-03-26 | 2022-03-26 | N | 5 | (ii),fff,ooo,xxx | N
PVB | Febco | 767-FR | 0.5 | VUH | 2006-08-01 | 2024-08-01 | N | 9 | (vv), xx,pppp,rrrrr | Y
PVB | Febco | 767-FR | 0.75 | VUH | 2006-08-01 | 2024-08-01 | N | 9 | (vv), xx,pppp,rrrrr | Y
PVB | Febco | 767-FR | 1 | VUH | 2006-08-01 | 2024-08-01 | N | 9 | (vv), xx,pppp,rrrrr | Y
PVB | Febco | 767-FR | 1.25 | VUH | 2006-08-01 | 2024-08-01 | N | 9 | (vv), xx,pppp,rrrrr | Y
PVB | Febco | 767-FR | 1.5 | VUH | 2006-08-01 | 2024-08-01 | N | 9 | (vv), xx,pppp,rrrrr | Y
PVB | Febco | 767-FR | 2 | VUH | 2006-08-01 | 2024-08-01 | N | 9 | (vv), xx,pppp,rrrrr | Y
PVB | Febco | LF767FR | 0.5 | VUH | 2010-05-04 | 2022-05-04 | Y | 9 | (hhhh),rrrrr | N
PVB | Febco | LF767FR | 0.75 | VUH | 2010-05-04 | 2022-05-04 | Y | 9 | (hhhh),rrrrr | N
PVB | Febco | LF767FR | 1 | VUH | 2010-05-04 | 2022-05-04 | Y | 9 | (hhhh),rrrrr | N
PVB | Febco | LF767FR | 1.25 | VUH | 2010-05-04 | 2022-05-04 | Y | 9 | (hhhh),rrrrr | N
PVB | Febco | LF767FR | 1.5 | VUH | 2010-05-04 | 2022-05-04 | Y | 9 | (hhhh),rrrrr | N
PVB | Febco | LF767FR | 2 | VUH | 2010-05-04 | 2022-05-04 | Y | 9 | (hhhh),rrrrr | N
PVB | Neptune | [5 empty] | N | [5 empty] | See Wilkins
PVB | Watts | 800CMQT | 0.5 | VUH | 1989-07-18 | 2022-07-18 | N | 8 | vv,xx,ooo,hhhh,pppp | Y
PVB | Watts | 800CMQT | 0.75 | VUH | 1989-07-18 | 2022-07-18 | N | 8 | vv,xx,ooo,hhhh,pppp | Y
PVB | Watts | 800M2QT | 0.5 | VUH | 1991-07-09 | 2024-07-09 | N | 8 | vv,xx,ooo,hhhh,pppp | Y
PVB | Watts | 800M2QT | 0.75 | VUH | 1991-07-09 | 2024-07-09 | N | 8 | vv,xx,ooo,hhhh,pppp | Y
PVB | Watts | 800M2QT | 1 | VUH | 1991-07-09 | 2024-07-09 | N | 8 | vv,xx,ooo,hhhh,pppp | Y
PVB | Watts | 800M2QT | 1.25 | VUH | 1993-03-25 | 2023-03-25 | N | 8 | vv,xx,ooo,hhhh,pppp | Y
PVB | Watts | 800M2QT | 1.5 | VUH | 1993-03-25 | 2023-03-25 | N | 8 | vv,xx,ooo,hhhh,pppp | Y
PVB | Watts | 800M2QT | 2 | VUH | 1993-03-25 | 2023-03-25 | N | 8 | vv,xx,ooo,hhhh,pppp | Y
PVB | Watts | 800M3QT | 0.5 | VUH | 1992-02-24 | 2022-02-24 | N | 8 | vv,xx,ooo,hhhh,pppp | Y
PVB | Watts | 800M3QT | 0.75 | VUH | 1992-02-24 | 2022-02-24 | N | 8 | vv,xx,ooo,hhhh,pppp | Y
PVB | Watts | 800M4FR | 0.5 | VUH | 1998-05-12 | 2022-05-12 | N | 9 | (vv),xx,ooo,hhhh,pppp,rrrrr | N
PVB | Watts | 800M4FR | 0.75 | VUH | 1998-05-12 | 2022-05-12 | N | 9 | (vv),xx,ooo,hhhh,pppp,rrrrr | N
PVB | Watts | 800M4FR | 1 | VUH | 1995-09-01 | 2022-09-01 | N | 9 | (vv),xx,ooo,hhhh,pppp,rrrrr | N
PVB | Watts | 800M4FR | 1.25 | VUH | 1997-05-13 | 2024-05-13 | N | 9 | (vv),xx,ooo,hhhh,pppp,rrrrr | N
PVB | Watts | 800M4FR | 1.5 | VUH | 1997-05-13 | 2024-05-13 | N | 9 | (vv),xx,ooo,hhhh,pppp,rrrrr | N
PVB | Watts | 800M4FR | 2 | VUH | 1997-05-13 | 2024-05-13 | N | 9 | (vv),xx,ooo,hhhh,pppp,rrrrr | N
PVB | Watts | 800M4QT | 0.5 | VUH | 1993-09-06 | 2023-09-06 | N | 8 | (vv),xx,ooo,hhhh,pppp,rrrrr | N
PVB | Watts | 800M4QT | 0.75 | VUH | 1993-04-06 | 2023-04-06 | N | 8 | (vv),xx,ooo,hhhh,pppp,rrrrr | N
PVB | Watts | 800M4QT | 1 | VUH | 1993-05-25 | 2023-05-25 | N | 8 | (vv),xx,ooo,hhhh,pppp,rrrrr | N
PVB | Watts | 800M4QT | 1.25 | VUH | 1994-05-24 | 2024-05-24 | N | 8 | (vv),xx,ooo,hhhh,pppp,rrrrr | N
PVB | Watts | 800M4QT | 1.5 | VUH | 1993-06-21 | 2023-06-21 | N | 8 | (vv),xx,ooo,hhhh,pppp,rrrrr | N
PVB | Watts | 800M4QT | 2 | VUH | 1993-06-21 | 2023-06-21 | N | 8 | (vv),xx,ooo,hhhh,pppp,rrrrr | N
PVB | Watts | 800MQT | 0.5 | VUH | 1989-07-18 | 2022-07-18 | N | 8 | vv,xx,ooo,hhhh,pppp | Y
PVB | Watts | 800MQT | 0.75 | VUH | 1989-07-18 | 2022-07-18 | N | 8 | vv,xx,ooo,hhhh,pppp | Y
PVB | Watts | 800QT | 0.75 | VUH | 1978-02-14 | 2023-02-14 | N | 5 | vv,xx,ooo,hhhh,pppp | Y
PVB | Watts | 800QT | 1 | VUH | 1978-02-14 | 2023-02-14 | N | 5 | vv,xx,ooo,hhhh,pppp | Y
PVB | Watts | 800QT | 1.25 | VUH | 1978-02-14 | 2023-02-14 | N | 5 | vv,xx,ooo,hhhh,pppp | Y
PVB | Watts | 800QT | 1.5 | VUH | 1978-02-14 | 2023-02-14 | N | 5 | vv,xx,ooo,hhhh,pppp | Y
PVB | Watts | 800QT | 2 | VUH | 1978-02-14 | 2023-02-14 | N | 5 | vv,xx,ooo,hhhh,pppp | Y
PVB | Watts | LF800M4FR | 0.5 | VUH | 2010-01-12 | 2022-01-12 | Y | 9 | (hhhh),rrrrr | N
PVB | Watts | LF800M4FR | 0.75 | VUH | 2010-01-12 | 2022-01-12 | Y | 9 | (hhhh),rrrrr | N
PVB | Watts | LF800M4FR | 1 | VUH | 2014-12-05 | 2023-12-05 | Y | 9 | (hhhh),rrrrr | N
PVB | Watts | LF800M4FR | 1.25 | VUH | 2010-01-12 | 2022-01-12 | Y | 9 | (hhhh),rrrrr | N
PVB | Watts | LF800M4FR | 1.5 | VUH | 2010-01-12 | 2022-01-12 | Y | 9 | (hhhh),rrrrr | N
PVB | Watts | LF800M4FR | 2 | VUH | 2010-01-12 | 2022-01-12 | Y | 9 | (hhhh),rrrrr | N
PVB | Watts | LF800M4QT | 0.5 | VUH | 2010-01-12 | 2022-01-12 | Y | 9 | (hhhh),rrrrr | N
PVB | Watts | LF800M4QT | 0.75 | VUH | 2010-01-12 | 2022-01-12 | Y | 9 | (hhhh),rrrrr | N
PVB | Watts | LF800M4QT | 1 | VUH | 2014-12-05 | 2023-12-05 | Y | 9 | (hhhh),rrrrr | N
PVB | Watts | LF800M4QT | 1.25 | VUH | 2010-01-12 | 2022-01-12 | Y | 9 | (hhhh),rrrrr | N
PVB | Watts | LF800M4QT | 1.5 | VUH | 2010-01-12 | 2022-01-12 | Y | 9 | (hhhh),rrrrr | N
PVB | Watts | LF800M4QT | 2 | VUH | 2010-01-12 | 2022-01-12 | Y | 9 | (hhhh),rrrrr | N
PVB | Wilkins | 420 | 0.5 | VUH | 1999-07-17 | 2023-07-17 | N | 9 | (ii),ooo | N
PVB | Wilkins | 420 | 0.75 | VUH | 1999-07-17 | 2023-07-17 | N | 9 | (ii),ooo | N
PVB | Wilkins | 420 | 1 | VUH | 2000-09-29 | 2024-09-29 | N | 9 | (ii),ooo | N
PVB | Wilkins | 710 | 0.75 | VUH | 2020-01-16 | 2023-01-16 | N | 10 | (ooo) | N |  |  | Testcocks: Female Threaded End or 45 degree male SAE flare
PVB | Wilkins | 710 | 1 | VUH | 2020-01-16 | 2023-01-16 | N | 10 | (ooo) | N |  |  | Testcocks: Female Threaded End or 45 degree male SAE flare
PVB | Wilkins | 420XL | 0.5 | VUH | 2011-03-21 | 2023-03-21 | Y | 9 | (iiii) | N |  |  | Testcocks: Female Threaded End or 45 degree male SAE flare
PVB | Wilkins | 420XL | 0.75 | VUH | 2011-03-21 | 2023-03-21 | Y | 9 | (iiii) | N |  |  | Testcocks: Female Threaded End or 45 degree male SAE flare
PVB | Wilkins | 420XL | 1 | VUH | 2011-08-03 | 2023-08-03 | Y | 9 | (iiii) | Y |  |  | Testcocks: Female Threaded End or 45 degree male SAE flare
PVB | Wilkins | 720A | 0.5 | VUH | 1978-08-28 | 2023-08-28 | N | 5 | (ii),ooo | N |  |  | Beginning with Serial No. T00001 the test cocks were moved from the body to the shutoff valves. Testcocks: Female Threaded End or 45 degree male SAE flare.
PVB | Wilkins | 720A | 0.75 | VUH | 1978-08-28 | 2023-08-28 | N | 5 | (ii),ooo | N |  |  | Beginning with Serial No. T00001 the test cocks were moved from the body to the shutoff valves. Testcocks: Female Threaded End or 45 degree male SAE flare.
PVB | Wilkins | 720A | 1 | VUH | 1978-08-28 | 2023-08-28 | N | 5 | (ii),ooo | N |  |  | Beginning with Serial No. T00001 the test cocks were moved from the body to the shutoff valves. Testcocks: Female Threaded End or 45 degree male SAE flare.
PVB | Wilkins | 720A | 1.25 | VUH | 1978-08-28 | 2023-08-28 | N | 5 | (ii),ooo | N |  |  | Beginning with Serial No. T00001 the test cocks were moved from the body to the shutoff valves.
PVB | Wilkins | 720A | 1.5 | VUH | 1978-08-28 | 2023-08-28 | N | 5 | (ii),ooo | N |  |  | Beginning with Serial No. T00001 the test cocks were moved from the body to the shutoff valves.
PVB | Wilkins | 720A | 2 | VUH | 1978-08-28 | 2023-08-28 | N | 5 | (ii),ooo | N |  |  | Beginning with Serial No. T00001 the test cocks were moved from the body to the shutoff valves.
RP | Ames | 4000B | 0.5 | H | 1996-09-10 | 2023-09-10 | N | 9 | (vv),xx,ooo,hhhh,pppp,rrrrr | N |  |  | Previously Approved 8th Ed. (26 May 1993)
RP | Ames | 4000B | 0.75 | H | 1992-10-31 | 2022-10-31 | N | 8 | (vv),xx,ooo,hhhh,pppp,rrrrr | N
RP | Ames | 4000B | 1 | H | 1988-01-11 | 2024-01-11 | N | 7 | (vv),xx,ooo,hhhh,pppp,rrrrr | N
RP | Ames | 4000B | 1.25 | H | 1993-08-24 | 2023-08-24 | N | 8 | (vv),xx,ooo,hhhh,pppp,rrrrr | N
RP | Ames | 4000B | 1.5 | H | 1993-08-24 | 2023-08-24 | N | 8 | (vv),xx,ooo,hhhh,pppp,rrrrr | N
RP | Ames | 4000B | 2 | H | 1996-09-10 | 2023-09-10 | N | 9 | (vv),xx,ooo,hhhh,pppp,rrrrr | N
RP | Ames | 4000B-FP | 0.75 | H | 2009-09-01 | 2024-09-01 | N | 9 | (eeeee) | Y
RP | Ames | 4000B-FP | 1 | H | 2009-09-01 | 2024-09-01 | N | 9 | (eeeee) | Y
RP | Ames | 4000B-FP | 1.25 | H | 2009-09-01 | 2024-09-01 | N | 9 | (eeeee) | N |  |  | Model Designation Changed to 4000BM2-FP
RP | Ames | 4000B-FP | 1.5 | H | 2009-09-01 | 2024-09-01 | N | 9 | (eeeee) | N |  |  | Model Designation Changed to 4000BM2-FP
RP | Ames | 4000B-FP | 2 | H | 2009-09-01 | 2024-09-01 | N | 9 | (eeeee) | N |  |  | Model Designation Changed to 4000BM2-FP
RP | Ames | 4000BM2 | 1 | H | 1998-05-18 | 2022-05-18 | N | 9 | (vv),xx,ooo,hhhh,pppp,rrrrr | N
RP | Ames | 4000BM2-FP | 1 | H | 2009-09-01 | 2024-09-01 | N | 9 | (eeeee),uuuuuu | N
RP | Ames | 4000BM2-FP | 1.25 | H | 2018-03-15 | 2024-03-15 | N | 9 | (eeeee),uuuuuu | N |  |  | formerly Mod 4000B-FP
RP | Ames | 4000BM2-FP | 1.5 | H | 2018-03-15 | 2024-03-15 | N | 9 | (eeeee),uuuuuu | N |  |  | formerly Mod 4000B-FP
RP | Ames | 4000BM2-FP | 2 | H | 2018-03-15 | 2024-03-15 | N | 9 | (eeeee),uuuuuu | N |  |  | formerly Mod 4000B-FP
RP | Ames | 4000BM3 | 0.75 | H | 2000-03-27 | 2023-03-27 | N | 9 | (vv),xx,ooo,hhhh,pppp,rrrrr | N
RP | Ames | 4000BM3-FP | 0.75 | H | 2009-09-01 | 2024-09-01 | N | 9 | (eeeee) | Y
RP | Ames | 4000CIV | 2.5 | H | 2000-07-07 | 2024-07-07 | N | 7 | (oo),gg,hh,ll,mm,pp,tt,uu | Y
RP | Ames | 4000CIV | 3 | H | 2000-07-07 | 2024-07-07 | N | 7 | (oo),gg,hh,ll,mm,pp,tt,uu | Y
RP | Ames | 4000CIV | 4 | H | 2000-06-19 | 2024-06-19 | N | 6 | (oo),gg,hh,ll,mm,pp,tt,uu,eee | Y
RP | Ames | 4000CIV | 6 | H | 2000-06-19 | 2024-06-19 | N | 6 | (oo),gg,hh,ll,mm,pp,tt,uu,eee | Y
RP | Ames | 4000CIV | 8 | H | 2000-06-19 | 2024-06-19 | N | 8 | (oo),gg,hh,ll,mm,pp,tt,uu | Y
RP | Ames | 4000CIV | 10 | H | 2000-06-19 | 2024-06-19 | N | 8 | (oo),gg,hh,ll,mm,pp,tt,uu | Y
RP | Ames | 4000RP | 4 | H | 1987-10-13 | 2023-10-13 | N | 7 | (tt),ee,ff,gg,hh,ll,mm,oo,pp,uu,ccc,ddd,ffff,gggg | Y |  |  | formerly Model RP
RP | Ames | 4000RP | 6 | H | 1987-10-13 | 2023-10-13 | N | 7 | (tt),ee,ff,gg,hh,ll,mm,oo,pp,uu,ccc,ddd,ffff,gggg | Y |  |  | formerly Model RP
RP | Ames | 4000RP | 8 | H | 1987-10-13 | 2023-10-13 | N | 7 | (tt),ee,ff,gg,hh,ll,mm,oo,pp,uu,ccc,ddd,ffff,gggg | Y |  |  | formerly Model RP
RP | Ames | 4000RP | 10 | H | 1987-10-13 | 2023-10-13 | N | 7 | (tt),ee,ff,gg,hh,ll,mm,oo,pp,uu,ccc,ddd,ffff,gggg | Y |  |  | formerly Model RP
RP | Ames | 4000SS | 2.5 | H | 1994-04-15 | 2024-04-15 | N | 8 | (tt),ee,ff,gg,hh,pp,uu,ccc,ddd | N
RP | Ames | 4000SS | 2.5 | H | 1994-04-15 | 2024-04-15 | Y | 8 | ll,mm,oo,ffff,gggg | N
RP | Ames | 4000SS | 3 | H | 1994-04-15 | 2024-04-15 | N | 8 | (tt),ee,ff,gg,hh,pp,uu,ccc,ddd | N
RP | Ames | 4000SS | 3 | H | 1994-04-15 | 2024-04-15 | Y | 8 | ll,mm,oo,ffff,gggg | N
RP | Ames | 4000SS | 4 | H | 1994-04-15 | 2024-04-15 | N | 8 | (tt),ee,ff,gg,hh,pp,uu,ccc,ddd | N
RP | Ames | 4000SS | 4 | H | 1994-04-15 | 2024-04-15 | Y | 8 | ll,mm,oo,ffff,gggg | N
RP | Ames | 4000SS | 6 | H | 1997-09-22 | 2024-09-22 | N | 8 | (tt),ee,ff,gg,hh,pp,uu,ccc,ddd | N
RP | Ames | 4000SS | 6 | H | 1997-09-22 | 2024-09-22 | Y | 8 | ll,mm,oo,ffff,gggg | N
RP | Ames | 400B | 0.75 | H | 2006-06-20 | 2024-06-20 | N | 9 | (vv),xx,ooo,hhhh,pppp,rrrrr | Y
RP | Ames | 400B | 0.75 | VD | 2006-08-30 | 2024-08-30 | N | 9 | (vv),xx,ooo,hhhh,pppp,rrrrr | Y
RP | Ames | 400B | 1 | H | 2006-06-20 | 2024-06-20 | N | 9 | (vv),xx,ooo,hhhh,pppp,rrrrr | Y
RP | Ames | 400B | 1 | VD | 2006-08-30 | 2024-08-30 | N | 9 | (vv),xx,ooo,hhhh,pppp,rrrrr | Y
RP | Ames | 400B | 1.25 | H | 2006-06-20 | 2024-06-20 | N | 9 | (vv),xx,ooo,hhhh,pppp,rrrrr | Y
RP | Ames | 400B | 1.25 | VD | 2006-08-30 | 2024-08-30 | N | 9 | (vv),xx,ooo,hhhh,pppp,rrrrr | Y
RP | Ames | 400B | 1.5 | H | 2006-06-20 | 2024-06-20 | N | 9 | (vv),xx,ooo,hhhh,pppp,rrrrr | Y
RP | Ames | 400B | 1.5 | VD | 2006-08-30 | 2024-08-30 | N | 9 | (vv),xx,ooo,hhhh,pppp,rrrrr | Y
RP | Ames | 400B | 2 | H | 2006-06-20 | 2024-06-20 | N | 9 | (vv),xx,ooo,hhhh,pppp,rrrrr | Y
RP | Ames | 400B | 2 | VD | 2006-08-30 | 2024-08-30 | N | 9 | (vv),xx,ooo,hhhh,pppp,rrrrr | Y
RP | Ames | 400B-A | 0.75 | VUVD | 2006-06-20 | 2024-06-20 | N | 9 | (vv),xx,ooo,hhhh,pppp,rrrrr | Y
RP | Ames | 400B-A | 1 | VUVD | 2006-06-20 | 2024-06-20 | N | 9 | (vv),xx,ooo,hhhh,pppp,rrrrr | Y
RP | Ames | 400B-A | 1.25 | VUVD | 2006-09-05 | 2024-09-05 | N | 9 | (vv),xx,ooo,hhhh,pppp,rrrrr | Y
RP | Ames | 400B-A | 1.5 | VUVD | 2006-06-20 | 2024-06-20 | N | 9 | (vv),xx,ooo,hhhh,pppp,rrrrr | Y
RP | Ames | 400B-A | 2 | VUVD | 2006-06-20 | 2024-06-20 | N | 9 | (vv),xx,ooo,hhhh,pppp,rrrrr | Y
RP | Ames | 400B-Z | 0.75 | VUVU | 2006-06-20 | 2024-06-20 | N | 9 | (vv),xx,ooo,hhhh,pppp,rrrrr | Y
RP | Ames | 400B-Z | 1 | VUVU | 2006-06-20 | 2024-06-20 | N | 9 | (vv),xx,ooo,hhhh,pppp,rrrrr | Y
RP | Ames | 400B-Z | 1.25 | VUVU | 2006-06-20 | 2024-06-20 | N | 9 | (vv),xx,ooo,hhhh,pppp,rrrrr | Y
RP | Ames | 400B-Z | 1.5 | VUVU | 2006-06-20 | 2024-06-20 | N | 9 | (vv),xx,ooo,hhhh,pppp,rrrrr | Y
RP | Ames | 400B-Z | 2 | VUVU | 2006-06-20 | 2024-06-20 | N | 9 | (vv),xx,ooo,hhhh,pppp,rrrrr | Y
RP | Ames | Colt 400 | 2.5 | H | 2002-10-07 | 2023-10-07 | N | 9 | (ppp),qqq,aaaa,bbbb,nnnnn | N |  |  | Check valve discs may be black EPDM or orange Silicone
RP | Ames | Colt 400 | 2.5 | H | 2002-10-07 | 2023-10-07 | Y | 9 | zzz,dddd,eeee,gggg,kkkk,llll,mmmm,nnnn | N |  |  | Check valve discs may be black EPDM or orange Silicone
RP | Ames | Colt 400 | 3 | H | 2002-10-07 | 2023-10-07 | N | 9 | (ppp),qqq,aaaa,bbbb,nnnnn | N |  |  | Check valve discs may be black EPDM or orange Silicone
RP | Ames | Colt 400 | 3 | H | 2002-10-07 | 2023-10-07 | Y | 9 | zzz,dddd,eeee,gggg,kkkk,llll,mmmm,nnnn | N |  |  | Check valve discs may be black EPDM or orange Silicone
RP | Ames | Colt 400 | 4 | H | 2002-10-07 | 2023-10-07 | N | 9 | (ppp),qqq,aaaa,bbbb,nnnnn | N |  |  | Check valve discs may be black EPDM or orange Silicone
RP | Ames | Colt 400 | 4 | H | 2002-10-07 | 2023-10-07 | Y | 9 | zzz,dddd,eeee,gggg,kkkk,llll,mmmm,nnnn | N |  |  | Check valve discs may be black EPDM or orange Silicone
RP | Ames | Colt 400 | 6 | H | 2004-09-29 | 2022-09-29 | N | 9 | (ppp),qqq,aaaa,bbbb,nnnnn | N
RP | Ames | Colt 400 | 6 | H | 2004-09-29 | 2022-09-29 | Y | 9 | zzz,dddd,eeee,gggg,kkkk,llll,mmmm,nnnn | N
RP | Ames | Colt 400 | 8 | H | 2007-08-13 | 2022-08-13 | N | 9 | (ppp),qqq,aaaa,bbbb,nnnnn | N
RP | Ames | Colt 400 | 8 | H | 2007-08-13 | 2022-08-13 | Y | 9 | zzz,dddd,eeee,gggg,kkkk,llll,mmmm,nnnn | N
RP | Ames | Colt 400 | 10 | H | 2009-07-22 | 2024-07-22 | N | 9 | (ppp),qqq,sss,ttt,aaaa,bbbb,nnnnn | N
RP | Ames | Colt 400 | 10 | H | 2009-07-22 | 2024-07-22 | Y | 9 | zzz,cccc,dddd,eeee,gggg,kkkk,llll,mmmm,nnnn | N
RP | Ames | Colt 400BF | 4 | H | 2007-09-17 | 2022-09-17 | Y | 9 | (yyy) | N |  |  | Check valve discs may be black EPDM or orange Silicone
RP | Ames | Colt 400BF | 6 | H | 2007-09-17 | 2022-09-17 | Y | 9 | (yyy) | N
RP | Ames | Colt 400N | 2.5 | VUVD | 2003-04-14 | 2024-04-14 | N | 9 | (ppp),qqq,aaaa,bbbb,nnnnn | N |  |  | Check valve discs may be black EPDM or orange Silicone
RP | Ames | Colt 400N | 2.5 | VUVD | 2003-04-14 | 2024-04-14 | Y | 9 | yyy,zzz,dddd,eeee,gggg,kkkk,llll,mmmm,nnnn | N |  |  | Check valve discs may be black EPDM or orange Silicone
RP | Ames | Colt 400N | 2.5 | VUVU | 2021-07-26 | 2024-07-26 | N | 9 | (ppp),qqq,aaaa,bbbb,nnnnn | N |  |  | Check valve discs may be black EPDM or orange Silicone
RP | Ames | Colt 400N | 2.5 | VUVU | 2021-07-26 | 2024-07-26 | Y | 9 | yyy,zzz,dddd,eeee,gggg,kkkk,llll,mmmm,nnnn | N |  |  | Check valve discs may be black EPDM or orange Silicone
RP | Ames | Colt 400N | 3 | VUVD | 2003-04-14 | 2024-04-14 | N | 9 | (ppp),qqq,aaaa,bbbb,nnnnn | N |  |  | Check valve discs may be black EPDM or orange Silicone
RP | Ames | Colt 400N | 3 | VUVD | 2003-04-14 | 2024-04-14 | Y | 9 | yyy,zzz,dddd,eeee,gggg,kkkk,llll,mmmm,nnnn | N |  |  | Check valve discs may be black EPDM or orange Silicone
RP | Ames | Colt 400N | 3 | VUVU | 2021-07-26 | 2024-07-26 | N | 9 | (ppp),qqq,aaaa,bbbb,nnnnn | N |  |  | Check valve discs may be black EPDM or orange Silicone
RP | Ames | Colt 400N | 3 | VUVU | 2021-07-26 | 2024-07-26 | Y | 9 | yyy,zzz,dddd,eeee,gggg,kkkk,llll,mmmm,nnnn | N |  |  | Check valve discs may be black EPDM or orange Silicone
RP | Ames | Colt 400N | 4 | VUVD | 2003-04-14 | 2024-04-14 | N | 9 | (ppp),qqq,aaaa,bbbb,nnnnn | N |  |  | Check valve discs may be black EPDM or orange Silicone
RP | Ames | Colt 400N | 4 | VUVD | 2003-04-14 | 2024-04-14 | Y | 9 | yyy,zzz,dddd,eeee,gggg,kkkk,llll,mmmm,nnnn | N |  |  | Check valve discs may be black EPDM or orange Silicone
RP | Ames | Colt 400N | 4 | VUVU | 2021-07-26 | 2024-07-26 | N | 9 | (ppp),qqq,aaaa,bbbb,nnnnn | N |  |  | Check valve discs may be black EPDM or orange Silicone
RP | Ames | Colt 400N | 4 | VUVU | 2021-07-26 | 2024-07-26 | Y | 9 | yyy,zzz,dddd,eeee,gggg,kkkk,llll,mmmm,nnnn | N |  |  | Check valve discs may be black EPDM or orange Silicone
RP | Ames | Colt 400N | 6 | VUVD | 2010-11-15 | 2022-11-15 | N | 9 | ppp,qqq,aaaa,bbbb,nnnnn
RP | Ames | Colt 400N | 6 | VUVD | 2010-11-15 | 2022-11-15 | Y | 9 | zzz,dddd,eeee,gggg,kkkk,llll,mmmm,nnnn
RP | Ames | Colt 400N | 6 | VUVU | 2021-07-26 | 2024-07-26 | N | 9 | ppp,qqq,aaaa,bbbb,nnnnn | N
RP | Ames | Colt 400N | 6 | VUVU | 2021-07-26 | 2024-07-26 | Y | 9 | zzz,dddd,eeee,gggg,kkkk,llll,mmmm,nnnn | N
RP | Ames | Colt 400N | 8 | VUVD | 2013-06-14 | 2022-06-14 | Y | 9 | (yyy), zzz, dddd, eeee, gggg, kkkk, llll, mmmm, nnnn
RP | Ames | Colt 400N | 8 | VUVU | 2021-07-26 | 2024-07-26 | Y | 9 | (yyy), zzz, dddd, eeee, gggg, kkkk, llll, mmmm, nnnn | N
RP | Ames | Colt 400Z | 2.5 | VUVD | 2021-07-26 | 2024-07-26 | N | 9 | (ppp),qqq,aaaa,bbbb,nnnnn | N |  |  | Check valve discs may be black EPDM or orange Silicone
RP | Ames | Colt 400Z | 2.5 | VUVD | 2021-07-26 | 2024-07-26 | Y | 9 | yyy,zzz,dddd,eeee,gggg,kkkk,llll,mmmm,nnnn | N |  |  | Check valve discs may be black EPDM or orange Silicone
RP | Ames | Colt 400Z | 2.5 | VUVU | 2003-04-14 | 2024-04-14 | N | 9 | (ppp),qqq,aaaa,bbbb,nnnnn | N |  |  | Check valve discs may be black EPDM or orange Silicone
RP | Ames | Colt 400Z | 2.5 | VUVU | 2003-04-14 | 2024-04-14 | Y | 9 | yyy,zzz,dddd,eeee,gggg,kkkk,llll,mmmm,nnnn | N |  |  | Check valve discs may be black EPDM or orange Silicone
RP | Ames | Colt 400Z | 3 | VUVD | 2021-07-26 | 2024-07-26 | N | 9 | (ppp),qqq,aaaa,bbbb,nnnnn | N |  |  | Check valve discs may be black EPDM or orange Silicone
RP | Ames | Colt 400Z | 3 | VUVD | 2021-07-26 | 2024-07-26 | Y | 9 | yyy,zzz,dddd,eeee,gggg,kkkk,llll,mmmm,nnnn | N |  |  | Check valve discs may be black EPDM or orange Silicone
RP | Ames | Colt 400Z | 3 | VUVU | 2003-04-14 | 2024-04-14 | N | 9 | (ppp),qqq,aaaa,bbbb,nnnnn | N |  |  | Check valve discs may be black EPDM or orange Silicone
RP | Ames | Colt 400Z | 3 | VUVU | 2003-04-14 | 2024-04-14 | Y | 9 | yyy,zzz,dddd,eeee,gggg,kkkk,llll,mmmm,nnnn | N |  |  | Check valve discs may be black EPDM or orange Silicone
RP | Ames | Colt 400Z | 4 | VUVD | 2021-07-26 | 2024-07-26 | N | 9 | (ppp),qqq,aaaa,bbbb,nnnnn | N |  |  | Check valve discs may be black EPDM or orange Silicone
RP | Ames | Colt 400Z | 4 | VUVD | 2021-07-26 | 2024-07-26 | Y | 9 | yyy,zzz,dddd,eeee,gggg,kkkk,llll,mmmm,nnnn | N |  |  | Check valve discs may be black EPDM or orange Silicone
RP | Ames | Colt 400Z | 4 | VUVU | 2003-04-14 | 2024-04-14 | N | 9 | (ppp),qqq,aaaa,bbbb,nnnnn | N |  |  | Check valve discs may be black EPDM or orange Silicone
RP | Ames | Colt 400Z | 4 | VUVU | 2003-04-14 | 2024-04-14 | Y | 9 | yyy,zzz,dddd,eeee,gggg,kkkk,llll,mmmm,nnnn | N |  |  | Check valve discs may be black EPDM or orange Silicone
RP | Ames | Colt 400Z | 8 | VUVD | 2021-07-26 | 2024-07-26 | N | 9 | ppp, qqq, aaaa, bbbb, | N
RP | Ames | Colt 400Z | 8 | VUVD | 2021-07-26 | 2024-07-26 | Y | 9 | (yyy), zzz, dddd, eeee, gggg, kkkk, llll, mmmm, nnnn | N
RP | Ames | Colt 400Z | 8 | VUVU | 2013-06-14 | 2022-06-14 | N | 9 | ppp, qqq, aaaa, bbbb,
RP | Ames | Colt 400Z | 8 | VUVU | 2013-06-14 | 2022-06-14 | Y | 9 | (yyy), zzz, dddd, eeee, gggg, kkkk, llll, mmmm, nnnn
RP | Ames | Deringer 40 | 2.5 | H | 2020-03-26 | 2023-03-26 | Y | 10 | (int) | N
RP | Ames | Deringer 40 | 3 | H | 2020-03-26 | 2023-03-26 | Y | 10 | (int) | N
RP | Ames | Deringer 40 | 4 | H | 2020-03-26 | 2023-03-26 | Y | 10 | (int) | N
RP | Ames | Deringer 40 | 6 | H | 2022-08-03 |  | Y | 10 | (int) | N
RP | Ames | Deringer 40 | 8 | H | 2020-03-26 | 2023-03-26 | Y | 10 | (int) | N
RP | Ames | Deringer 40G | 2.5 | H | 2020-03-26 | 2023-03-26 | Y | 10 | (ssssss), tttttt | N
RP | Ames | Deringer 40G | 3 | H | 2020-03-26 | 2023-03-26 | Y | 10 | (ssssss), tttttt | N
RP | Ames | Deringer 40G | 4 | H | 2020-03-26 | 2023-03-26 | Y | 10 | (ssssss), tttttt | N
RP | Ames | Deringer 40G | 6 | H | 2024-10-01 |  | Y | 10 | (ssssss), tttttt
RP | Ames | Deringer 40G | 8 | H | 2020-03-26 | 2023-03-26 | Y | 10 | (ssssss), tttttt | N
RP | Ames | Deringer 40GX | 4 | H | 2024-10-01 |  | Y | 10 | (ssssss), tttttt
RP | Ames | Deringer 40GX | 6 | H | 2020-03-26 | 2023-03-26 | Y | 10 | (ssssss), tttttt | N
RP | Ames | Deringer 40X | 4 | H | 2022-08-03 |  | Y | 10 | (int) | N
RP | Ames | Deringer 40X | 6 | H | 2020-03-26 | 2023-03-26 | Y | 10 | (int) | N
RP | Ames | LF4000B | 0.5 | H | 2013-09-25 | 2022-09-25 | Y | 9 | (hhhh) | N
RP | Ames | LF4000BM2 | 1 | H | 2013-09-25 | 2022-09-25 | Y | 9 | (hhhh) | N
RP | Ames | LF4000BM2 | 1.25 | H | 2013-09-25 | 2022-09-25 | Y | 8 | (hhhh) | N
RP | Ames | LF4000BM2 | 1.5 | H | 2013-09-25 | 2022-09-25 | Y | 8 | (hhhh) | N
RP | Ames | LF4000BM2 | 2 | H | 2013-09-25 | 2022-09-25 | Y | 9 | (hhhh) | N
RP | Ames | LF4000BM2-FP | 1 | H | 2019-03-12 | 2022-03-12 | Y | 9 | (eeeee),uuuuuu | N
RP | Ames | LF4000BM2-FP | 1.25 | H | 2019-03-12 | 2022-03-12 | Y | 9 | (eeeee),uuuuuu | N
RP | Ames | LF4000BM2-FP | 1.5 | H | 2019-03-12 | 2022-03-12 | Y | 9 | (eeeee),uuuuuu | N
RP | Ames | LF4000BM2-FP | 2 | H | 2019-03-12 | 2022-03-12 | Y | 9 | (eeeee),uuuuuu | N
RP | Ames | LF4000BM3 | 0.75 | H | 2013-09-25 | 2022-09-25 | Y | 9 | (hhhh) | N
RP | Ames | Maxim 400 | 2.5 | H | 2002-10-07 | 2023-10-07 | N | 9 | (ppp),qqq,aaa,bbbb,nnnnn | N |  |  | Check valve discs may be black EPDM or orange Silicone
RP | Ames | Maxim 400 | 2.5 | H | 2002-10-07 | 2023-10-07 | Y | 9 | zzz,dddd,eeee,gggg,kkkk,llll,mmmm,nnnn | N |  |  | Check valve discs may be black EPDM or orange Silicone
RP | Ames | Maxim 400 | 3 | H | 2002-10-07 | 2023-10-07 | N | 9 | (ppp),qqq,aaa,bbbb,nnnnn | N |  |  | Check valve discs may be black EPDM or orange Silicone
RP | Ames | Maxim 400 | 3 | H | 2002-10-07 | 2023-10-07 | Y | 9 | zzz,dddd,eeee,gggg,kkkk,llll,mmmm,nnnn | N |  |  | Check valve discs may be black EPDM or orange Silicone
RP | Ames | Maxim 400 | 4 | H | 2005-01-18 | 2023-01-18 | N | 9 | (ppp),qqq,aaa,bbbb,nnnnn | N
RP | Ames | Maxim 400 | 4 | H | 2005-01-18 | 2023-01-18 | Y | 9 | kkkk,llll,mmmm,nnnn | N
RP | Ames | Maxim 400 | 6 | H | 2007-08-13 | 2022-08-13 | N | 9 | (ppp),qqq,sss,ttt,aaaa,bbbb,nnnnn | N
RP | Ames | Maxim 400 | 6 | H | 2007-08-13 | 2022-08-13 | Y | 9 | cccc,dddd,kkkk,llll,mmmm,nnnn | N
RP | Ames | Maxim 400 | 8 | H | 2009-07-22 | 2024-07-22 | N | 9 | (ppp),qqq,sss,ttt,aaaa,bbbb,nnnnn | N
RP | Ames | Maxim 400 | 8 | H | 2009-07-22 | 2024-07-22 | Y | 9 | zzz,cccc,dddd,eeee,gggg,kkkk,llll,mmmm,nnnn | N
RP | Ames | Maxim 400 | 10 | H | 2009-07-22 | 2024-07-22 | N | 9 | (ppp),qqq,sss,ttt,aaaa,bbbb | N
RP | Ames | Maxim 400 | 10 | H | 2009-07-22 | 2024-07-22 | Y | 9 | zzz,cccc,dddd,eeee,gggg,kkkk,llll,mmmm,nnnn | N
RP | Ames | Maxim 400N | 2.5 | VUVD | 2003-04-14 | 2024-04-14 | N | 9 | (ppp),qqq,aaaa,bbbb,nnnnn | N
RP | Ames | Maxim 400N | 2.5 | VUVD | 2003-04-14 | 2024-04-14 | Y | 9 | yyy,zzz,dddd,eeee,gggg,kkkk,llll,mmmm,nnnn | N
RP | Ames | Maxim 400N | 2.5 | VUVU | 2021-07-26 | 2024-07-26 | N | 9 | (ppp),qqq,aaaa,bbbb,nnnnn | N
RP | Ames | Maxim 400N | 2.5 | VUVU | 2021-07-26 | 2024-07-26 | Y | 9 | yyy,zzz,dddd,eeee,gggg,kkkk,llll,mmmm,nnnn | N
RP | Ames | Maxim 400N | 3 | VUVD | 2003-04-14 | 2024-04-14 | N | 9 | (ppp),qqq,aaaa,bbbb,nnnnn | N
RP | Ames | Maxim 400N | 3 | VUVD | 2003-04-14 | 2024-04-14 | Y | 9 | yyy,zzz,dddd,eeee,gggg,kkkk,llll,mmmm,nnnn | N
RP | Ames | Maxim 400N | 3 | VUVU | 2021-07-26 | 2024-07-26 | N | 9 | (ppp),qqq,aaaa,bbbb,nnnnn | N
RP | Ames | Maxim 400N | 3 | VUVU | 2021-07-26 | 2024-07-26 | Y | 9 | yyy,zzz,dddd,eeee,gggg,kkkk,llll,mmmm,nnnn | N
RP | Ames | Maxim 400N | 4 | VUVD | 2010-11-15 | 2022-11-15 | N | 9 | ppp,qqq,aaaa,bbbb,nnnnn
RP | Ames | Maxim 400N | 4 | VUVD | 2010-11-15 | 2022-11-15 | Y | 9 | yyy,zzz,dddd,eeee,gggg,kkkk,llll,mmmm,nnnn
RP | Ames | Maxim 400N | 4 | VUVU | 2021-07-26 | 2024-07-26 | N | 9 | ppp,qqq,aaaa,bbbb,nnnnn | N
RP | Ames | Maxim 400N | 4 | VUVU | 2021-07-26 | 2024-07-26 | Y | 9 | yyy,zzz,dddd,eeee,gggg,kkkk,llll,mmmm,nnnn | N
RP | Ames | Maxim 400N | 6 | VUVD | 2013-06-14 | 2022-06-14 | N | 9 | ppp, qqq, aaaa, bbbb,
RP | Ames | Maxim 400N | 6 | VUVD | 2013-06-14 | 2022-06-14 | Y | 9 | (yyy), zzz, dddd, eeee, gggg, kkkk, llll, mmmm, nnnn
RP | Ames | Maxim 400Z | 2.5 | VUVD | 2021-07-26 | 2024-07-26 | N | 9 | (ppp),qqq,aaaa,bbbb,nnnnn | N
RP | Ames | Maxim 400Z | 2.5 | VUVD | 2021-07-26 | 2024-07-26 | Y | 9 | yyy,zzz,dddd,eeee,gggg,kkkk,llll,mmmm,nnnn | N
RP | Ames | Maxim 400Z | 2.5 | VUVU | 2003-04-14 | 2024-04-14 | N | 9 | (ppp),qqq,aaaa,bbbb,nnnnn | N
RP | Ames | Maxim 400Z | 2.5 | VUVU | 2003-04-14 | 2024-04-14 | Y | 9 | yyy,zzz,dddd,eeee,gggg,kkkk,llll,mmmm,nnnn | N
RP | Ames | Maxim 400Z | 3 | VUVD | 2021-07-26 | 2024-07-26 | N | 9 | (ppp),qqq,aaaa,bbbb,nnnnn | N
RP | Ames | Maxim 400Z | 3 | VUVD | 2021-07-26 | 2024-07-26 | Y | 9 | yyy,zzz,dddd,eeee,gggg,kkkk,llll,mmmm,nnnn | N
RP | Ames | Maxim 400Z | 3 | VUVU | 2003-04-14 | 2024-04-14 | N | 9 | (ppp),qqq,aaaa,bbbb,nnnnn | N
RP | Ames | Maxim 400Z | 3 | VUVU | 2003-04-14 | 2024-04-14 | Y | 9 | yyy,zzz,dddd,eeee,gggg,kkkk,llll,mmmm,nnnn | N
RP | Ames | Maxim 400Z | 6 | VUVD | 2021-07-26 | 2024-07-26 | N | 9 | ppp, qqq, aaaa, bbbb, | N
RP | Ames | Maxim 400Z | 6 | VUVD | 2021-07-26 | 2024-07-26 | Y | 9 | (yyy), zzz, dddd, eeee, gggg, kkkk, llll, mmmm, nnnn | N
RP | Ames | Maxim 400Z | 6 | VUVU | 2013-06-14 | 2022-06-14 | N | 9 | ppp, qqq, aaaa, bbbb,
RP | Ames | Maxim 400Z | 6 | VUVU | 2013-06-14 | 2022-06-14 | Y | 9 | (yyy), zzz, dddd, eeee, gggg, kkkk, llll, mmmm, nnnn
RP | Ames | RP | 4 | [9 empty] | model designation changed to 4000RP
RP | Ames | RP | 6 | [9 empty] | model designation changed to 4000RP
RP | Ames | RP | 8 | [9 empty] | model designation changed to 4000RP
RP | Ames | RP | 10 | [9 empty] | model designation changed to 4000RP
RP | Ames | U400B | 1 | H | 2006-06-20 | 2024-06-20 | N | 9 | (vv),xx,ooo,hhhh,pppp | Y
RP | Ames | U400B | 1 | VD | 2006-08-30 | 2024-08-30 | N | 9 | (vv),xx,ooo,hhhh,pppp | Y
RP | Ames | U400B | 1.25 | H | 2006-06-20 | 2024-06-20 | N | 9 | (vv),xx,ooo,hhhh,pppp | Y
RP | Ames | U400B | 1.25 | VD | 2006-08-30 | 2024-08-30 | N | 9 | (vv),xx,ooo,hhhh,pppp | Y
RP | Ames | U400B | 1.5 | H | 2006-06-20 | 2024-06-20 | N | 9 | (vv),xx,ooo,hhhh,pppp | Y
RP | Ames | U400B | 1.5 | VD | 2006-08-30 | 2024-08-30 | N | 9 | (vv),xx,ooo,hhhh,pppp | Y
RP | Ames | U400B | 2 | H | 2006-06-20 | 2024-06-20 | N | 9 | (vv),xx,ooo,hhhh,pppp | Y
RP | Ames | U400B | 2 | VD | 2006-08-30 | 2024-08-30 | N | 9 | (vv),xx,ooo,hhhh,pppp | Y
RP | Ames | U400B-A | 0.75 | VUVD | 2006-06-20 | 2024-06-20 | N | 9 | (vv),xx,ooo,hhhh,pppp | Y
RP | Ames | U400B-A | 1 | VUVD | 2006-06-20 | 2024-06-20 | N | 9 | (vv),xx,ooo,hhhh,pppp | Y
RP | Ames | U400B-A | 1.25 | VUVD | 2006-06-20 | 2024-06-20 | N | 9 | (vv),xx,ooo,hhhh,pppp | Y
RP | Ames | U400B-A | 1.5 | VUVD | 2006-06-20 | 2024-06-20 | N | 9 | (vv),xx,ooo,hhhh,pppp | Y
RP | Ames | U400B-A | 2 | VUVD | 2006-06-20 | 2024-06-20 | N | 9 | (vv),xx,ooo,hhhh,pppp | Y
RP | Apollo/Conbraco | 4020102 | 0.25 | H | 1991-05-03 | 2024-05-03 | N | 8 | dd | Y
RP | Apollo/Conbraco | 4020202 | 0.375 | H | 1991-05-03 | 2024-05-03 | N | 8 | dd | Y
RP | Apollo/Conbraco | 4020302 | 0.5 | H | 1991-05-03 | 2023-05-03 | N | 8 | dd | Y
RP | Apollo/Conbraco | 4020402 | 0.75 | H | 1989-05-08 | 2022-05-08 | N | 8 | dd | Y
RP | Apollo/Conbraco | 4020502 | 1 | H | 1989-05-08 | 2022-05-08 | N | 8 | dd | Y
RP | Apollo/Conbraco | 4020602 | 1.25 | H | 1992-04-06 | 2022-04-06 | N | 8 | dd | Y
RP | Apollo/Conbraco | 4020702 | 1.5 | H | 1989-03-17 | 2022-03-17 | N | 8 | dd | Y
RP | Apollo/Conbraco | 4020802 | 2 | H | 1989-03-17 | 2022-03-17 | N | 8 | dd | Y
RP | Apollo/Conbraco | 4020002 | 3 | [9 empty] | model designation changed to RP40
RP | Apollo/Conbraco | 4020003 | 3 | [9 empty] | model designation changed to RP40
RP | Apollo/Conbraco | 4020005 | 3 | [9 empty] | model designation changed to RP40
RP | Apollo/Conbraco | 4020199T | 0.25 | [9 empty] | model designation changed to RP40
RP | Apollo/Conbraco | 40201A2 | 0.25 | H | 1996-04-19 | 2023-04-19 | N | 8 | dd | Y
RP | Apollo/Conbraco | 40201A2S | 0.25 | [9 empty] | model designation changed to RPS40
RP | Apollo/Conbraco | 40201T2 | 0.25 | [9 empty] | model designation changed to RP40
RP | Apollo/Conbraco | 40201T2S | 0.25 | [9 empty] | model designation changed to RPS40
RP | Apollo/Conbraco | 4020299T | 0.375 | [9 empty] | model designation changed to RP40
RP | Apollo/Conbraco | 40202A2 | 0.375 | H | 1996-04-19 | 2023-04-19 | N | 8 | dd | Y
RP | Apollo/Conbraco | 40202A2S | 0.375 | [9 empty] | model designation changed to RPS40
RP | Apollo/Conbraco | 40202T2 | 0.375 | [9 empty] | model designation changed to RP40
RP | Apollo/Conbraco | 40202T2S | 0.375 | [9 empty] | model designation changed to RPS40
RP | Apollo/Conbraco | 4020399T | 0.5 | [9 empty] | model designation changed to RP40
RP | Apollo/Conbraco | 40203A2 | 0.5 | H | 1996-04-19 | 2023-04-19 | N | 8 | dd | Y
RP | Apollo/Conbraco | 40203A2S | 0.5 | [9 empty] | model designation changed to RPS40
RP | Apollo/Conbraco | 40203T2 | 0.5 | [9 empty] | model designation changed to RP40
RP | Apollo/Conbraco | 40203T2S | 0.5 | [9 empty] | model designation changed to RPS40
RP | Apollo/Conbraco | 4020499T | 0.75 | [9 empty] | model designation changed to RP40
RP | Apollo/Conbraco | 40204A2 | 0.75 | H | 1991-11-27 | 2024-11-27 | N | 8 | dd | Y
RP | Apollo/Conbraco | 40204A2S | 0.75 | [9 empty] | model designation changed to RPS40
RP | Apollo/Conbraco | 40204A2U | 0.75 | [9 empty] | model designation changed to RP40N
RP | Apollo/Conbraco | 40204A2Z | 0.75 | [9 empty] | model designation changed to RP40Z
RP | Apollo/Conbraco | 40204T2 | 0.75 | [9 empty] | model designation changed to RP40
RP | Apollo/Conbraco | 40204T2S | 0.75 | [9 empty] | model designation changed to RPS40
RP | Apollo/Conbraco | 40204TC2 | 0.75 | [9 empty] | model designation changed to RP40
RP | Apollo/Conbraco | 40204TCU | 0.75 | VUVD | 1998-11-30 | 2022-11-30 | N | 8 | (dd) | Y
RP | Apollo/Conbraco | 4020599T | 1 | [9 empty] | model designation changed to RP40
RP | Apollo/Conbraco | 40205A2 | 1 | H | 1991-11-27 | 2024-11-27 | N | 8 | dd | Y
RP | Apollo/Conbraco | 40205A2S | 1 | [9 empty] | model designation changed to RPS40
RP | Apollo/Conbraco | 40205A2U | 1 | [9 empty] | model designation changed to 40205T2U
RP | Apollo/Conbraco | 40205A2Z | 1 | [9 empty] | model designation changed to 40205T2Z
RP | Apollo/Conbraco | 40205T2 | 1 | [9 empty] | model designation changed to RP40
RP | Apollo/Conbraco | 40205T2S | 1 | [9 empty] | model designation changed to RPS40
RP | Apollo/Conbraco | 40205T2U | 1 | VUVD | 1993-09-15 | 2023-09-15 | N | 8 | (dd) | Y |  |  | formerly 40205A2U
RP | Apollo/Conbraco | 40205T2Z | 1 | VUVU | 1993-09-15 | 2023-09-15 | N | 8 | (dd) | Y |  |  | formerly 40205A2Z
RP | Apollo/Conbraco | 40205TC2 | 1 | [9 empty] | model designation changed to RP40
RP | Apollo/Conbraco | 40205TCU | 1 | VUVD | 1998-11-30 | 2022-11-30 | N | 8 | (dd) | Y
RP | Apollo/Conbraco | 4020699T | 1.25 | [9 empty] | model designation changed to RP40
RP | Apollo/Conbraco | 40206A2 | 1.25 | H | 1993-06-21 | 2023-06-21 | N | 8 | dd | Y
RP | Apollo/Conbraco | 40206A2U | 1.25 | [9 empty] | model designation changed to RP40N
RP | Apollo/Conbraco | 40206A2Z | 1.25 | [9 empty] | model designation changed to RP40Z
RP | Apollo/Conbraco | 40206T2 | 1.25 | [9 empty] | model designation changed to RP40
RP | Apollo/Conbraco | 40206T2U | 1.25 | [9 empty] | model designation changed to RP40N
RP | Apollo/Conbraco | 40206T2Z | 1.25 | [9 empty] | model designation changed to RP40Z
RP | Apollo/Conbraco | 4020799T | 1.5 | [9 empty] | model designation changed to RP40
RP | Apollo/Conbraco | 40207A2 | 1.5 | H | 1992-09-16 | 2022-09-16 | N | 8 | dd | Y
RP | Apollo/Conbraco | 40207A2U | 1.5 | [9 empty] | model designation changed to RP40U
RP | Apollo/Conbraco | 40207A2Z | 1.5 | [9 empty] | model designation changed to RP40Z
RP | Apollo/Conbraco | 40207T2 | 1.5 | [9 empty] | model designation changed to RP40
RP | Apollo/Conbraco | 40207T2U | 1.5 | [9 empty] | model designation changed to RP40U
RP | Apollo/Conbraco | 40207T2Z | 1.5 | [9 empty] | model designation changed to RP40Z
RP | Apollo/Conbraco | 4020899T | 2 | [9 empty] | model designation changed to RP40
RP | Apollo/Conbraco | 40208A2 | 2 | H | 1992-09-16 | 2022-09-16 | N | 8 | dd | Y
RP | Apollo/Conbraco | 40208A2U | 2 | [9 empty] | model designation changed to RP40U
RP | Apollo/Conbraco | 40208A4 | 2 | H | 2000-05-24 | 2024-05-24 | N | 8 | rrr | Y
RP | Apollo/Conbraco | 40208AZ2 | 2 | [9 empty] | model designation changed to RP40Z
RP | Apollo/Conbraco | 40208T2 | 2 | [9 empty] | model designation changed to RP40
RP | Apollo/Conbraco | 40208T2U | 2 | [9 empty] | model designation changed to RP40U
RP | Apollo/Conbraco | 40208T2Z | 2 | [9 empty] | model designation changed to RP40Z
RP | Apollo/Conbraco | 4020902 | 2.5 | [9 empty] | model designation changed to RP40
RP | Apollo/Conbraco | 4020903 | 2.5 | [9 empty] | model designation changed to RP40
RP | Apollo/Conbraco | 4020905 | 2.5 | [9 empty] | model designation changed to RP40
RP | Apollo/Conbraco | 4020A02 | 4 | [9 empty] | model designation changed to RP40
RP | Apollo/Conbraco | 4020A03 | 4 | [9 empty] | model designation changed to RP40
RP | Apollo/Conbraco | 4020A05 | 4 | [9 empty] | model designation changed to RP40
RP | Apollo/Conbraco | 4020C02 | 6 | [9 empty] | model designation changed to RP40
RP | Apollo/Conbraco | 4020C03 | 6 | [9 empty] | model designation changed to RP40
RP | Apollo/Conbraco | 4020C05 | 6 | [9 empty] | model designation changed to RP40
RP | Apollo/Conbraco | 4020E02 | 8 | [9 empty] | model designation changed to RP40
RP | Apollo/Conbraco | 4020E03 | 8 | [9 empty] | model designation changed to RP40
RP | Apollo/Conbraco | 4020G02 | 10 | [9 empty] | model designation changed to RP40
RP | Apollo/Conbraco | 4020G03 | 10 | [9 empty] | model designation changed to RP40
RP | Apollo/Conbraco | 4D-200 | 2.5 | H | 2009-03-11 | 2024-03-11 | N | 9 | (yyy), cccc, dddd | Y
RP | Apollo/Conbraco | 4D-200 | 3 | H | 2009-03-11 | 2024-03-11 | N | 9 | (yyy), cccc, dddd | Y
RP | Apollo/Conbraco | 4D-200 | 4 | H | 2009-03-11 | 2024-03-11 | N | 9 | (yyy), cccc, dddd | Y
RP | Apollo/Conbraco | 4D-200U | 2.5 | VUVD | 2009-03-11 | 2024-03-11 | N | 9 | (yyy), cccc, dddd | Y
RP | Apollo/Conbraco | 4D-200U | 3 | VUVD | 2009-03-11 | 2024-03-11 | N | 9 | (yyy), cccc, dddd | Y
RP | Apollo/Conbraco | 4D-200U | 4 | VUVD | 2009-03-11 | 2024-03-11 | N | 9 | (yyy), cccc, dddd | Y
RP | Apollo/Conbraco | RP40 | 0.25 | H | 1998-09-16 | 2022-09-16 | N | 8 | (dd) | Y |  |  | formerly 4020199T, 40201T2
RP | Apollo/Conbraco | RP40 | 0.375 | H | 1998-09-16 | 2022-09-16 | N | 8 | (dd) | Y |  |  | formerly 4020299T, 40202T2
RP | Apollo/Conbraco | RP40 | 0.5 | H | 1994-09-15 | 2022-09-15 | N | 8 | (dd) | Y |  |  | formerly 4020399T, 40203T2
RP | Apollo/Conbraco | RP40 | 0.75 | H | 1998-09-16 | 2022-09-16 | N | 8 | (dd) | Y |  |  | formerly 4020499T, 40204T2, 40204TC2
RP | Apollo/Conbraco | RP40 | 1 | H | 1998-09-16 | 2022-09-16 | N | 8 | (dd) | Y |  |  | formerly 4020599T, 40205T2, 40205TC2
RP | Apollo/Conbraco | RP40 | 1.25 | H | 1998-09-16 | 2022-09-16 | N | 8 | (dd) | Y |  |  | formerly 4020699T, 40206T2
RP | Apollo/Conbraco | RP40 | 1.5 | H | 1998-09-16 | 2022-09-16 | N | 8 | (dd) | Y |  |  | formerly 4020799T, 40207T2
RP | Apollo/Conbraco | RP40 | 2 | H | 1998-09-16 | 2022-09-16 | N | 8 | (dd) | Y |  |  | formerly 4020899T, 40208T2
RP | Apollo/Conbraco | RP40 | 2.5 | H | 1991-04-08 | 2024-04-08 | N | 8 | (tt),bb,cc,ee,ll,mm,uu,mmm | Y |  |  | formerly 4020902, 4020903, 4020905
RP | Apollo/Conbraco | RP40 | 3 | H | 1991-04-08 | 2024-04-08 | N | 8 | (tt),bb,cc,ee,ll,mm,uu,mmm | Y |  |  | formerly 4020002, 4020003, 4020005
RP | Apollo/Conbraco | RP40 | 4 | H | 1991-04-08 | 2024-04-08 | N | 8 | (tt),bb,cc,ee.ll,mm,uu,mmm | Y |  |  | formerly 4020A02, 4020A03, 4020A05
RP | Apollo/Conbraco | RP40 | 6 | H | 1991-04-08 | 2024-04-08 | N | 8 | (tt),bb,ee,ll | Y |  |  | formerly 4020C02, 4020C03, 4020C05
RP | Apollo/Conbraco | RP40 | 8 | H | 1991-10-22 | 2024-10-22 | N | 8 | (tt),bb,cc,ee,ll,mm,uu | Y |  |  | formerly 4020E02, 4020E03
RP | Apollo/Conbraco | RP40 | 10 | H | 1993-04-13 | 2023-04-13 | N | 8 | (tt),bb,cc,ee,ll,mm,uu | Y |  |  | formerly 4020G02, 4020G03
RP | Apollo/Conbraco | RP40N | 0.75 | VUVD | 1992-11-06 | 2022-11-06 | N | 8 | (dd) | Y |  |  | formerly 40204A2U
RP | Apollo/Conbraco | RP40N | 1.25 | VUVD | 1995-02-02 | 2022-02-02 | N | 8 | (dd) | Y |  |  | formerly 40206A2U, 40206T2U
RP | Apollo/Conbraco | RP40U | 1.5 | VUVD | 1995-02-02 | 2022-02-02 | N | 8 | (dd) | Y |  |  | formerly 40207A2U, 40207T2U
RP | Apollo/Conbraco | RP40U | 2 | VUVD | 1995-02-02 | 2022-02-02 | N | 8 | (dd) | Y |  |  | formerly 40208A2U, 40208T2U
RP | Apollo/Conbraco | RP40Z | 0.75 | VUVU | 1992-11-06 | 2022-11-06 | N | 8 | (dd) | Y |  |  | formerly 40204A2Z
RP | Apollo/Conbraco | RP40Z | 1.25 | VUVU | 1995-02-02 | 2022-02-02 | N | 8 | (dd) | Y |  |  | formerly 40206A2Z, 40206T2Z
RP | Apollo/Conbraco | RP40Z | 1.5 | VUVU | 1995-02-02 | 2022-02-02 | N | 8 | (dd) | Y |  |  | formerly 40207A2Z, 40207T2Z
RP | Apollo/Conbraco | RP40Z | 2 | VUVU | 1995-02-02 | 2022-02-02 | N | 8 | (dd) | Y |  |  | formerly 40208AZ2, 40208T2Z
RP | Apollo/Conbraco | RP4A | 0.5 | H | 2011-11-29 | 2023-11-29 | N | 9 | (iiiii),sssss | N
RP | Apollo/Conbraco | RP4A | 0.75 | H | 2011-06-14 | 2023-06-14 | N | 9 | (iiiii),sssss,wwwww | N
RP | Apollo/Conbraco | RP4A | 1 | H | 2011-09-27 | 2023-09-27 | N | 9 | (iiiii),sssss,wwwww | N
RP | Apollo/Conbraco | RP4A | 1.25 | H | 2013-12-11 | 2022-12-11 | N | 9 | (iiiii),sssss,wwwww | N
RP | Apollo/Conbraco | RP4A | 1.5 | H | 2013-12-11 | 2022-12-11 | N | 9 | (iiiii),sssss,wwwww | N
RP | Apollo/Conbraco | RP4A | 2 | H | 2011-11-29 | 2023-11-29 | N | 9 | (iiiii),sssss,wwwww | N
RP | Apollo/Conbraco | RP4AN | 0.75 | VUVD | 2020-01-16 | 2023-01-16 | N | 10 | (sssss), wwwww | N
RP | Apollo/Conbraco | RP4AN | 1 | VUVD | 2019-01-16 | 2022-01-16 | N | 10 | (sssss), wwwww | N
RP | Apollo/Conbraco | RPLF40 | 0.5 | H | 2010-11-18 | 2022-11-18 | Y | 9 | (jjjjj) | Y
RP | Apollo/Conbraco | RPLF40 | 1.25 | H | 2010-11-18 | 2022-11-18 | Y | 9 | (jjjjj) | Y
RP | Apollo/Conbraco | RPLF40 | 1.5 | H | 2010-11-18 | 2022-11-18 | Y | 9 | (jjjjj) | Y
RP | Apollo/Conbraco | RPLF40 | 2 | H | 2010-11-18 | 2022-11-18 | Y | 9 | (jjjjj) | Y
RP | Apollo/Conbraco | RPLF4A | 0.5 | H | 2011-11-29 | 2023-11-29 | Y | 9 | (jjjjj),ttttt,uuuuu | N
RP | Apollo/Conbraco | RPLF4A | 0.75 | H | 2011-06-14 | 2023-06-14 | Y | 9 | (jjjjj),ttttt,vvvvv | N
RP | Apollo/Conbraco | RPLF4A | 1 | H | 2011-09-27 | 2023-09-27 | Y | 9 | (jjjjj),ttttt,vvvvv | N
RP | Apollo/Conbraco | RPLF4A | 1.25 | H | 2013-12-11 | 2022-12-11 | Y | 9 | (jjjjj),ttttt,vvvvv | N
RP | Apollo/Conbraco | RPLF4A | 1.5 | H | 2013-12-11 | 2022-12-11 | Y | 9 | (jjjjj),ttttt,vvvvv | N
RP | Apollo/Conbraco | RPLF4A | 2 | H | 2011-11-29 | 2023-11-29 | Y | 9 | (jjjjj),ttttt,vvvvv | N
RP | Apollo/Conbraco | RPLF4A | 2.5 | H | 2014-02-25 | 2023-02-25 | Y | 10 | (yyy), cccc, dddd, mmmm, nnnn, xxxxx, yyyyy, zzzzz, aaaaaa, xxxxxx | N
RP | Apollo/Conbraco | RPLF4A | 3 | H | 2014-02-25 | 2023-02-25 | Y | 10 | (yyy), cccc, dddd, mmmm, nnnn, xxxxx, yyyyy, zzzzz, aaaaaa, xxxxxx | N
RP | Apollo/Conbraco | RPLF4A | 4 | H | 2013-06-24 | 2022-06-24 | Y | 10 | (yyy), cccc, dddd, mmmm, nnnn, xxxxx, yyyyy, zzzzz, aaaaaa, xxxxxx | N
RP | Apollo/Conbraco | RPLF4A | 6 | H | 2013-06-24 | 2022-06-24 | Y | 10 | (yyy), cccc, dddd, mmmm, nnnn, xxxxx, yyyyy, zzzzz, aaaaaa, xxxxxx | N
RP | Apollo/Conbraco | RPLF4A | 8 | H | 2017-01-20 | 2023-01-20 | Y | 10 | (yyy), cccc, dddd, mmmm, nnnn, xxxxx, yyyyy, zzzzz, aaaaaa, xxxxxx | N
RP | Apollo/Conbraco | RPLF4A | 10 | H | 2021-11-05 | 2024-11-05 | Y | 10 | (zzzzz), zzz,cccc,dddd,kkkk,llll,mmmm,nnnn,xxxxx, yyyyy,aaaaaa | N
RP | Apollo/Conbraco | RPLF4A | 12 | H | 2021-11-05 | 2024-11-05 | Y | 10 | (bbbbbb), ll,mm,cccccc | N
RP | Apollo/Conbraco | RPLF4AN | 0.75 | VUVD | 2020-01-16 | 2023-01-16 | Y | 10 | (ttttt), vvvvv | N
RP | Apollo/Conbraco | RPLF4AN | 1 | VUVD | 2019-01-16 | 2022-01-16 | Y | 10 | (ttttt), vvvvv | N
RP | Apollo/Conbraco | RPLF4AN | 2.5 | VUVD | 2015-04-27 | 2024-04-27 | Y | 10 | (yyy), cccc, dddd, mmmm, nnnn, xxxxx, yyyyy, zzzzz, aaaaaa, xxxxxx | N
RP | Apollo/Conbraco | RPLF4AN | 2.5 | VUVU | 2015-04-27 | 2024-04-27 | Y | 10 | (yyy), cccc, dddd, mmmm, nnnn, xxxxx, yyyyy, zzzzz, aaaaaa, xxxxxx | N
RP | Apollo/Conbraco | RPLF4AN | 3 | VUVD | 2015-04-27 | 2024-04-27 | Y | 10 | (yyy), cccc, dddd, mmmm, nnnn, xxxxx, yyyyy, zzzzz, aaaaaa, xxxxxx | N
RP | Apollo/Conbraco | RPLF4AN | 3 | VUVU | 2015-04-27 | 2024-04-27 | Y | 10 | (yyy), cccc, dddd, mmmm, nnnn, xxxxx, yyyyy, zzzzz, aaaaaa, xxxxxx | N
RP | Apollo/Conbraco | RPLF4AN | 4 | VUVD | 2014-05-15 | 2023-05-15 | Y | 10 | (yyy), cccc, dddd, mmmm, nnnn, xxxxx, yyyyy, zzzzz, aaaaaa, xxxxxx | N
RP | Apollo/Conbraco | RPLF4AN | 4 | VUVU | 2014-06-11 | 2023-06-11 | Y | 10 | (yyy), cccc, dddd, mmmm, nnnn, xxxxx, yyyyy, zzzzz, aaaaaa, xxxxxx | N
RP | Apollo/Conbraco | RPLF4AN | 6 | VUVD | 2014-06-10 | 2023-06-10 | Y | 10 | (yyy), cccc, dddd, mmmm, nnnn, xxxxx, yyyyy, zzzzz, aaaaaa, xxxxxx | N
RP | Apollo/Conbraco | RPLF4AN | 6 | VUVU | 2014-06-11 | 2023-06-11 | Y | 10 | (yyy), cccc, dddd, mmmm, nnnn, xxxxx, yyyyy, zzzzz, aaaaaa, xxxxxx | N
RP | Apollo/Conbraco | RPLF4AN | 8 | VUVD | 2017-03-20 | 2023-03-20 | Y | 10 | (yyy), cccc, dddd, mmmm, nnnn, xxxxx, yyyyy, zzzzz, aaaaaa, xxxxxx | N
RP | Apollo/Conbraco | RPLF4AN | 8 | VUVU | 2017-03-20 | 2023-03-20 | Y | 10 | (yyy), cccc, dddd, mmmm, nnnn, xxxxx, yyyyy, zzzzz, aaaaaa, xxxxxx | N
RP | Apollo/Conbraco | RPLF4AN | 10 | VUVD | 2021-11-05 | 2024-11-05 | Y | 10 | (zzzzz), yyy,zzz,cccc,dddd,kkkk,llll,mmmm,nnnn,xxxxx, yyyyy,aaaaaa | N
RP | Apollo/Conbraco | RPLF4AN | 12 | VUVD | 2021-11-05 | 2024-11-05 | Y | 10 | (bbbbbb), ll,mm,cccccc | N
RP | Apollo/Conbraco | RPLF4AR | 2.5 | H | 2015-12-21 | 2024-12-21 | Y | 10 | (cccc), dddd, mmmm, nnnn, xxxxx, yyyyy, zzzzz, aaaaaa | Y |  |  | Integral Stainless Steel grooved spool between the #2 ck and #2 SOV - assembly length: min. 34" and max. 47 1/8"
RP | Apollo/Conbraco | RPLF4AR | 3 | H | 2015-12-21 | 2024-12-21 | Y | 10 | (cccc), dddd, mmmm, nnnn, xxxxx, yyyyy, zzzzz, aaaaaa | Y |  |  | Integral Stainless Steel grooved spool between the #2 ck and #2 SOV - assembly length: min. 35" and max. 48 1/8"
RP | Apollo/Conbraco | RPLF4AR | 4 | H | 2015-12-21 | 2024-12-21 | Y | 10 | (cccc), dddd, mmmm, nnnn, xxxxx, yyyyy, zzzzz, aaaaaa | Y |  |  | Integral Stainless Steel grooved spool between the #2 ck and #2 SOV - assembly length: min. 37 3/8" and max. 62 1/4"
RP | Apollo/Conbraco | RPLF4AR | 6 | H | 2015-12-21 | 2024-12-21 | Y | 10 | (cccc), dddd, mmmm, nnnn, xxxxx, yyyyy, zzzzz, aaaaaa | Y |  |  | Integral Stainless Steel grooved spool between the #2 ck and #2 SOV - assembly length: min. 46" and max. 71 1/4"
RP | Apollo/Conbraco | RPLF4AR | 8 | H | 2018-02-22 | 2024-02-22 | Y | 10 | (xxxxx), cccc, dddd, mmmm, nnnn, yyyyy, zzzzz, aaaaaa | Y |  |  | Integral Stainless Steel grooved spool between the #2 ck and #2 SOV - assembly length: min. 55 3/4" and max. 86"
RP | Apollo/Conbraco | RPLF4AR | 10 | H | 2021-11-05 | 2024-11-05 | Y | 10 | (zzzzz), zzz,cccc,dddd,kkkk,llll,mmmm,nnnn,xxxxx, yyyyy,aaaaaa | Y |  |  | Integral Stainless Steel grooved spool between the #2 ck and #2 SOV - assembly length: min. 65 3/4" and max. 100 5/8"
RP | Apollo/Conbraco | RPS40 | 0.25 | H | 1996-04-19 | 2023-04-19 | N | 8 | (uuu) | Y |  |  | formerly 40201A2S, 40201T2S
RP | Apollo/Conbraco | RPS40 | 0.375 | H | 1996-04-19 | 2023-04-19 | N | 8 | (uuu) | Y |  |  | formerly 40202A2S, 40202T2S
RP | Apollo/Conbraco | RPS40 | 0.5 | H | 1996-04-19 | 2023-04-19 | N | 8 | (dd) | Y |  |  | formerly 40203A2S, 40203T2S
RP | Apollo/Conbraco | RPS40 | 0.75 | H | 1994-08-16 | 2024-08-16 | N | 8 | (uuu) | Y |  |  | formerly 40204A2S
RP | Apollo/Conbraco | RPS40 | 1 | H | 1994-08-16 | 2024-08-16 | N | 8 | (uuu) | Y |  |  | formerly 40204A2S, 40204T2S
RP | ARI | RP 500 | 0.5 | H | 2013-01-03 | 2022-01-03 | N | 9 | (ooooo), ii, ooo,ffffff | N
RP | ARI | RP 500 | 0.5 | H | 2014-02-18 | 2023-02-18 | Y | 9 | (ooooo),ffffff | N
RP | ARI | RP 500 | 0.75 | H | 2007-03-02 | 2022-03-02 | N | 9 | (ii),ooo, ooooo, ffffff | N
RP | ARI | RP 500 | 0.75 | H | 2014-02-18 | 2023-02-18 | Y | 9 | (ooooo), ffffff | N
RP | ARI | RP 500 | 1 | H | 2007-03-02 | 2022-03-02 | N | 9 | (ii),ooo, ooooo, ffffff | N
RP | ARI | RP 500 | 1 | H | 2014-02-18 | 2023-02-18 | Y | 9 | (ooooo), ffffff | N
RP | ARI | RP 500 | 1.25 | H | 2014-02-18 | 2023-02-18 | Y | 10 | (ooooo), ffffff | N
RP | ARI | RP 500 | 1.5 | H | 2014-02-18 | 2023-02-18 | Y | 10 | (ooooo), ffffff | N
RP | ARI | RP 500 | 2 | H | 2014-02-18 | 2023-02-18 | Y | 10 | (ooooo), ffffff | N
RP | ARI | RP 501 | 0.5 | H | 2018-09-06 | 2024-09-06 | Y | 10 | (int) | N
RP | ARI | RP 501 | 0.75 | H | 2017-03-20 | 2023-03-20 | Y | 10 | (int) | N
RP | ARI | RP 501 | 1 | H | 2017-03-20 | 2023-03-20 | Y | 10 | (int) | N
RP | ARI | RP 501 | 1.25 | H | 2017-03-20 | 2023-03-20 | Y | 10 | (int) | N
RP | ARI | RP 501 | 1.5 | H | 2017-03-20 | 2023-03-20 | Y | 10 | (int) | N
RP | ARI | RP 501 | 2 | H | 2017-03-20 | 2023-03-20 | Y | 10 | (int) | N
RP | Backflow Direct | Deringer 40 | 2.5 | H | 2017-01-20 | 2023-01-20 | Y | 10 | (int) | N
RP | Backflow Direct | Deringer 40 | 3 | H | 2017-01-20 | 2023-01-20 | Y | 10 | (int) | N
RP | Backflow Direct | Deringer 40 | 4 | H | 2017-01-20 | 2023-01-20 | Y | 10 | (int) | N
RP | Backflow Direct | Deringer 40 | 6 | H | 2022-08-03 |  | Y | 10 | (int) | N
RP | Backflow Direct | Deringer 40 | 8 | H | 2017-06-27 | 2023-06-27 | Y | 10 | (int) | N
RP | Backflow Direct | Deringer 40G | 2.5 | H | 2018-10-24 | 2024-10-24 | Y | 10 | (ssssss), tttttt | N
RP | Backflow Direct | Deringer 40G | 3 | H | 2018-10-24 | 2024-10-24 | Y | 10 | (ssssss), tttttt | N
RP | Backflow Direct | Deringer 40G | 4 | H | 2018-10-24 | 2024-10-24 | Y | 10 | (ssssss), tttttt | N
RP | Backflow Direct | Deringer 40G | 6 | H | 2024-10-01 |  | Y | 10 | (ssssss), tttttt
RP | Backflow Direct | Deringer 40G | 8 | H | 2019-03-12 | 2022-03-12 | Y | 10 | (ssssss), tttttt | N
RP | Backflow Direct | Deringer 40GX | 4 | H | 2024-10-01 |  | Y | 10 | (ssssss), tttttt
RP | Backflow Direct | Deringer 40GX | 6 | H | 2019-03-12 | 2022-03-12 | Y | 10 | (ssssss), tttttt | N
RP | Backflow Direct | Deringer 40X | 4 | H | 2022-08-03 |  | Y | 10 | (int) | N
RP | Backflow Direct | Deringer 40X | 6 | H | 2017-06-27 | 2023-06-27 | Y | 10 | (int) | N
RP | Backflow Direct | Magnum 40 | 2.5 | H | 2018-03-15 | 2024-03-15 | Y | 10 | (int) | N
RP | Backflow Direct | Magnum 40 | 3 | H | 2018-03-15 | 2024-03-15 | Y | 10 | (int) | N
RP | Backflow Direct | Magnum 40 | 4 | H | 2018-03-15 | 2024-03-15 | Y | 10 | (int) | N
RP | Backflow Direct | Magnum 40 | 8 | H | 2018-03-15 | 2024-03-15 | Y | 10 | (int) | N
RP | Backflow Direct | Magnum 40G | 2.5 | H | 2018-10-24 | 2024-10-24 | Y | 10 | (qqqqqq), rrrrrr | N
RP | Backflow Direct | Magnum 40G | 3 | H | 2018-10-24 | 2024-10-24 | Y | 10 | (qqqqqq), rrrrrr | N
RP | Backflow Direct | Magnum 40G | 4 | H | 2018-10-24 | 2024-10-24 | Y | 10 | (qqqqqq), rrrrrr | N
RP | Backflow Direct | Magnum 40G | 8 | H | 2019-03-12 | 2022-03-12 | Y | 10 | (qqqqqq), rrrrrr | N
RP | Backflow Direct | Magnum 40GX | 6 | H | 2019-03-12 | 2022-03-12 | Y | 10 | (qqqqqq), rrrrrr | N
RP | Backflow Direct | Magnum 40X | 6 | H | 2018-03-15 | 2024-03-15 | Y | 10 | (int) | N
RP | BEECO | Barracuda 40 | 2.5 | H | 2018-12-18 | 2024-12-18 | Y | 10 | (qqqqqq), rrrrrr, vvvvvv, wwwwww | N
RP | BEECO | Barracuda 40 | 3 | H | 2018-12-18 | 2024-12-18 | Y | 10 | (qqqqqq), rrrrrr, vvvvvv, wwwwww | N
RP | BEECO | Barracuda 40 | 4 | H | 2018-12-18 | 2024-12-18 | Y | 10 | (qqqqqq), rrrrrr, vvvvvv, wwwwww | N
RP | BEECO | Barracuda 40 | 8 | H | 2019-03-12 | 2022-03-12 | Y | 10 | (qqqqqq), rrrrrr | N
RP | BEECO | Barracuda 40X | 6 | H | 2019-03-12 | 2022-03-12 | Y | 10 | (qqqqqq), rrrrrr, vvvvvv, wwwwww | N
RP | Cla-Val | RP4 | 8 | H | 1989-06-22 | 2022-06-22 | N | 8 | (gg),hh,qq,rr | Y
RP | Cla-Val | RP4 | 10 | H | 1989-06-22 | 2022-06-22 | N | 8 | (gg),hh,qq,rr | Y
RP | Conbraco | [5 empty] | N | [5 empty] | See Apollo/Conbraco
RP | Febco | 860 | 0.5 | H | 1998-04-09 | 2022-04-09 | N | 9 | (fff),ooo | N
RP | Febco | 860 | 0.75 | H | 1997-11-21 | 2024-11-21 | N | 9 | (fff),jjj,ooo | N
RP | Febco | 860 | 1 | H | 1997-11-21 | 2024-11-21 | N | 9 | (fff),jjj,ooo | N
RP | Febco | 860 | 1.25 | H | 1998-06-04 | 2022-06-04 | N | 9 | (fff),jjj,ooo | N
RP | Febco | 860 | 1.5 | H | 1998-04-09 | 2022-04-09 | N | 9 | (fff),jjj,ooo | N
RP | Febco | 860 | 2 | H | 1998-04-09 | 2022-04-09 | N | 9 | (fff),ooo | Y
RP | Febco | 860 | 2.5 | H | 1996-04-19 | 2023-04-19 | N | 8 | (ee),ff,ll,mm,oo,pp,tt,uu.zzz,cccc,ffff,gggg | Y
RP | Febco | 860 | 3 | H | 1996-04-19 | 2023-04-19 | N | 8 | (ee),ff,ll,mm,oo,pp,tt,uu.zzz,cccc,ffff,gggg | Y
RP | Febco | 860 | 4 | H | 1995-05-31 | 2022-05-31 | N | 8 | (ee),ff,ll,mm,oo,pp,tt,uu,nnn,zzz,cccc,ffff,gggg | Y
RP | Febco | 860 | 6 | H | 1995-08-07 | 2022-08-07 | N | 8 | (ee),ff,ll,mm,oo,pp,tt,uu,nnn,zzz,cccc,ffff,gggg | Y
RP | Febco | 860 | 8 | H | 1995-10-04 | 2022-10-04 | N | 8 | (ee),ff,ll,mm,oo,pp,tt,uu,nnn,zzz,cccc,ffff,gggg | Y
RP | Febco | 867 | 2.5 | H | 2006-08-01 | 2024-08-01 | N | 8 | (oo), gg, hh,ll, mm, pp, tt, uu, yy, fff | Y
RP | Febco | 867 | 3 | H | 2006-08-01 | 2024-08-01 | N | 8 | (oo), gg, hh,ll, mm, pp, tt, uu, yy, eee, fff | Y
RP | Febco | 880 | 2.5 | VUVD | 1995-05-24 | 2022-05-24 | N | 8 | ee,ff,ll,mm,oo,pp,tt,uu,zzz,ffff,gggg | Y
RP | Febco | 880 | 3 | VUVD | 1995-05-24 | 2022-05-24 | N | 8 | ee,ff,ll,mm,oo,pp,tt,uu,zzz,ffff,gggg | Y
RP | Febco | 880 | 4 | VUVD | 1995-03-10 | 2022-03-10 | N | 8 | ee,ff,ll,mm,oo,pp,tt,uu,zzz,ffff,gggg | Y
RP | Febco | 880 | 6 | VUVD | 1995-05-19 | 2022-05-19 | N | 8 | ee,ff,ll,mm,oo,pp,tt,uu,zzz,ffff,gggg | Y
RP | Febco | 880 | 8 | VUVD | 1995-05-19 | 2022-05-19 | N | 8 | ee,ff,ll,mm,oo,pp,tt,uu,zzz,ffff,gggg | Y
RP | Febco | 880 | 10 | VUVD | 1996-10-04 | 2023-10-04 | N | 8 | ee,ff,ll,mm,oo,pp,tt,uu,zzz,ffff,gggg | Y
RP | Febco | 825Y | 0.75 | H | 1982-03-19 | 2024-03-19 | N | 6 | (ii),fff,jjj,ooo | N |  |  | Replaceable check valve seats starting with serial No. J000001
RP | Febco | 825Y | 1 | H | 1982-03-19 | 2024-03-19 | N | 6 | (ii),fff,jjj,ooo | N |  |  | Replaceable check valve seats starting with serial No. J000001
RP | Febco | 825Y | 1.25 | H | 1982-06-03 | 2024-06-01 | N | 6 | ii,fff,jjj,ooo | Y
RP | Febco | 825Y | 1.5 | H | 1982-08-06 | 2024-08-06 | N | 6 | (ii),fff,jjj,ooo | N |  |  | Replaceable check valve seats starting with serial No. J000001
RP | Febco | 825Y | 2 | H | 1982-08-06 | 2024-08-06 | N | 6 | (ii),fff,ooo | N |  |  | Replaceable check valve seats starting with serial No. J000001
RP | Febco | 825YA | 0.75 | H | 1990-03-05 | 2023-03-05 | N | 8 | (ii),fff,jjj,ooo | N |  |  | Replaceable check valve seats starting with serial No. J000001
RP | Febco | 825YA | 0.75 | HVD | 1990-03-05 | 2023-03-05 | N | 8 | (ii),fff,jjj,ooo | N |  |  | Replaceable check valve seats starting with serial No. J000001
RP | Febco | 825YA | 0.75 | VUH | 1990-03-05 | 2023-03-05 | N | 8 | (ii),fff,jjj,ooo | N |  |  | Replaceable check valve seats starting with serial No. J000001
RP | Febco | 825YA | 0.75 | VUVD | 1990-03-05 | 2023-03-05 | N | 8 | (ii),fff,jjj,ooo | N |  |  | Replaceable check valve seats starting with serial No. J000001
RP | Febco | 825YA | 1 | H | 1990-03-05 | 2023-03-05 | N | 8 | (ii),fff,jjj,ooo | N |  |  | Replaceable check valve seats starting with serial No. J000001
RP | Febco | 825YA | 1 | HVD | 1990-03-05 | 2023-03-05 | N | 8 | (ii),fff,jjj,ooo | N |  |  | Replaceable check valve seats starting with serial No. J000001
RP | Febco | 825YA | 1 | VUH | 1990-03-05 | 2023-03-05 | N | 8 | (ii),fff,jjj,ooo | N |  |  | Replaceable check valve seats starting with serial No. J000001
RP | Febco | 825YA | 1 | VUVD | 1990-03-05 | 2023-03-05 | N | 8 | (ii),fff,jjj,ooo | N |  |  | Replaceable check valve seats starting with serial No. J000001
RP | Febco | 825YA | 1.5 | H | 1989-05-08 | 2022-05-08 | N | 8 | (ii),fff,jjj,ooo | N |  |  | Replaceable check valve seats starting with serial No. J000001
RP | Febco | 825YA | 1.5 | HVD | 1989-05-08 | 2022-05-08 | N | 8 | (ii),fff,jjj,ooo | N |  |  | Replaceable check valve seats starting with serial No. J000001
RP | Febco | 825YA | 1.5 | VUH | 1989-05-08 | 2022-05-08 | N | 8 | (ii),fff,jjj,ooo | N |  |  | Replaceable check valve seats starting with serial No. J000001
RP | Febco | 825YA | 1.5 | VUVD | 1989-05-08 | 2022-05-08 | N | 8 | (ii),fff,jjj,ooo | N |  |  | Replaceable check valve seats starting with serial No. J000001
RP | Febco | 825YA | 2 | H | 1989-05-08 | 2022-05-08 | N | 8 | (ii),fff,ooo | N |  |  | Replaceable check valve seats starting with serial No. J000001
RP | Febco | 825YA | 2 | HVD | 1989-05-08 | 2022-05-08 | N | 8 | (ii),fff,ooo | N |  |  | Replaceable check valve seats starting with serial No. J000001
RP | Febco | 825YA | 2 | VUH | 1989-05-08 | 2022-05-08 | N | 8 | (ii),fff,ooo | N |  |  | Replaceable check valve seats starting with serial No. J000001
RP | Febco | 825YA | 2 | VUVD | 1989-05-08 | 2022-05-08 | N | 8 | (ii),fff,ooo | N |  |  | Replaceable check valve seats starting with serial No. J000001
RP | Febco | 825YAR | 0.75 | H | 1993-01-22 | 2023-01-22 | N | 8 | ii,fff,jjj,ooo | Y
RP | Febco | 825YAR | 0.75 | HVD | 1993-01-22 | 2023-01-22 | N | 8 | ii,fff,jjj,ooo | Y
RP | Febco | 825YAR | 0.75 | VUH | 1993-01-22 | 2023-01-22 | N | 8 | ii,fff,jjj,ooo | Y
RP | Febco | 825YAR | 0.75 | VUVD | 1993-01-22 | 2023-01-22 | N | 8 | ii,fff,jjj,ooo | Y
RP | Febco | 825YAR | 1 | H | 1993-01-21 | 2023-01-21 | N | 8 | ii,fff,jjj,ooo | Y
RP | Febco | 825YAR | 1 | HVD | 1993-01-21 | 2023-01-21 | N | 8 | ii,fff,jjj,ooo | Y
RP | Febco | 825YAR | 1 | VUH | 1993-01-21 | 2023-01-21 | N | 8 | ii,fff,jjj,ooo | Y
RP | Febco | 825YAR | 1 | VUVD | 1993-01-21 | 2023-01-21 | N | 8 | ii,fff,jjj,ooo | Y
RP | Febco | 825YAR | 1.5 | H | 1993-08-19 | 2023-08-19 | N | 8 | ii,fff,jjj,ooo | Y
RP | Febco | 825YAR | 1.5 | HVD | 1993-08-19 | 2023-08-19 | N | 8 | ii,fff,jjj,ooo | Y
RP | Febco | 825YAR | 1.5 | VUH | 1993-08-19 | 2023-08-19 | N | 8 | ii,fff,jjj,ooo | Y
RP | Febco | 825YAR | 1.5 | VUVD | 1993-08-19 | 2023-08-19 | N | 8 | ii,fff,jjj,ooo | Y
RP | Febco | 825YAR | 2 | H | 1993-08-19 | 2023-08-19 | N | 8 | ii,fff,ooo | Y
RP | Febco | 825YAR | 2 | HVD | 1993-08-19 | 2023-08-19 | N | 8 | ii,fff,ooo | Y
RP | Febco | 825YAR | 2 | VUH | 1993-08-19 | 2023-08-19 | N | 8 | ii,fff,ooo | Y
RP | Febco | 825YAR | 2 | VUVD | 1993-08-19 | 2023-08-19 | N | 8 | ii,fff,ooo | Y
RP | Febco | 825YD | 2.5 | H | 1989-02-24 | 2022-02-24 | N | 7 | (ee),ff,ll,mm,oo,pp,tt,uu,zzz,ffff,gggg | Y
RP | Febco | 825YD | 3 | H | 1989-02-24 | 2022-02-24 | N | 7 | (ee),ff,ll,mm,oo,pp,tt,uu,zzz,ffff,gggg | Y
RP | Febco | 825YD | 4 | H | 1989-02-24 | 2022-02-24 | N | 7 | (ee),ff,ll,mm,oo,pp,tt,uu,zzz,ffff,gggg | Y
RP | Febco | 825YD | 6 | H | 1989-02-24 | 2022-02-24 | N | 7 | (ee),ff,ll,mm,oo,pp,tt,uu,zzz,ffff,gggg | Y
RP | Febco | 825YD | 8 | H | 1989-02-24 | 2022-02-24 | N | 7 | (ee),ff,ll,mm,oo,pp,tt,uu,zzz,ffff,gggg | Y
RP | Febco | 825YD | 10 | H | 1989-02-24 | 2022-02-24 | N | 7 | (ee),ff,ll,mm,oo,pp,tt,uu,zzz,ffff,gggg | Y
RP | Febco | 825YR | 0.75 | H | 1993-01-22 | 2023-01-22 | N | 8 | ii,fff,jjj | Y
RP | Febco | 825YR | 1 | H | 1993-01-22 | 2023-01-22 | N | 8 | ii,fff,jjj | Y
RP | Febco | 825YR | 1.5 | H | 1993-07-23 | 2023-07-23 | N | 8 | ii,fff,jjj | Y
RP | Febco | 825YR | 2 | H | 1993-07-23 | 2023-07-23 | N | 8 | ii,fff | Y
RP | Febco | 860U | 0.5 | H | 1998-10-12 | 2022-10-12 | N | 9 | (kkk) | N
RP | Febco | 860U | 0.75 | H | 1998-10-12 | 2022-10-12 | N | 9 | (kkk) | N
RP | Febco | 860U | 1 | H | 1998-10-12 | 2022-10-12 | N | 9 | (kkk) | N
RP | Febco | 860U | 1.25 | H | 1998-10-12 | 2022-10-12 | N | 9 | (kkk) | N
RP | Febco | 860U | 1.5 | H | 1998-10-12 | 2022-10-12 | N | 9 | (kkk) | N
RP | Febco | 860U | 2 | H | 1998-10-12 | 2022-10-12 | N | 9 | (kkk) | N
RP | Febco | 880V | 2.5 | VUVD | 1995-06-30 | 2022-06-30 | N | 8 | (ee),ff,ll,mm,oo,pp,tt,uu,nnn,zzz,cccc,ffff,gggg | Y
RP | Febco | 880V | 2.5 | VUVU | 1995-06-30 | 2022-06-30 | N | 8 | (ee),ff,ll,mm,oo,pp,tt,uu,nnn,zzz,cccc,ffff,gggg | Y
RP | Febco | 880V | 3 | VUVD | 1995-06-30 | 2022-06-30 | N | 8 | (ee),ff,ll,mm,oo,pp,tt,uu,nnn,zzz,cccc,ffff,gggg | Y
RP | Febco | 880V | 3 | VUVU | 1995-06-30 | 2022-06-30 | N | 8 | (ee),ff,ll,mm,oo,pp,tt,uu,nnn,zzz,cccc,ffff,gggg | Y
RP | Febco | 880V | 4 | VUVD | 1995-08-08 | 2022-08-08 | N | 8 | (ee),ff,ll,mm,oo,pp,tt,uu,nnn,zzz,cccc,ffff,gggg | Y
RP | Febco | 880V | 4 | VUVU | 1995-08-08 | 2022-08-08 | N | 8 | (ee),ff,ll,mm,oo,pp,tt,uu,nnn,zzz,cccc,ffff,gggg | Y
RP | Febco | 880V | 6 | VUVD | 1995-07-05 | 2022-07-05 | N | 8 | (ee),ff,ll,mm,oo,pp,tt,uu,nnn,zzz,cccc,ffff,gggg | Y
RP | Febco | 880V | 6 | VUVU | 1995-07-05 | 2022-07-05 | N | 8 | (ee),ff,ll,mm,oo,pp,tt,uu,nnn,zzz,cccc,ffff,gggg | Y
RP | Febco | 880V | 8 | VUVD | 1996-12-18 | 2023-12-18 | N | 8 | (ee),ff,ll,mm,oo,pp,tt,uu,nnn,zzz,cccc,ffff,gggg | Y
RP | Febco | 880V | 8 | VUVU | 1996-12-18 | 2023-12-18 | N | 8 | (ee),ff,ll,mm,oo,pp,tt,uu,nnn,zzz,cccc,ffff,gggg | Y
RP | Febco | 880V | 10 | VUVD | 1997-06-17 | 2024-06-17 | N | 8 | (ee),ff,ll,mm,oo,pp,tt,uu,nnn,zzz,cccc,ffff,gggg | Y
RP | Febco | 880V | 10 | VUVU | 1997-06-17 | 2024-06-17 | N | 8 | (ee),ff,ll,mm,oo,pp,tt,uu,nnn,zzz,cccc,ffff,gggg | Y
RP | Febco | LF825Y | 0.75 | H | 2010-02-18 | 2022-02-18 | Y | 8 | (qqqqq), hhhh | N
RP | Febco | LF825Y | 1 | H | 2010-02-18 | 2022-02-18 | Y | 8 | (qqqqq), hhhh | N
RP | Febco | LF825Y | 1.5 | H | 2010-03-25 | 2022-03-25 | Y | 8 | (qqqqq), hhhh | N
RP | Febco | LF825Y | 2 | H | 2010-03-25 | 2022-03-25 | Y | 8 | (qqqqq), hhhh | N
RP | Febco | LF825YA | 0.75 | H | 2010-02-18 | 2022-02-18 | Y | 8 | (qqqqq), hhhh | N
RP | Febco | LF825YA | 0.75 | HVD | 2010-02-18 | 2022-02-18 | Y | 8 | (qqqqq), hhhh | N
RP | Febco | LF825YA | 0.75 | VUH | 2010-02-18 | 2022-02-18 | Y | 8 | (qqqqq), hhhh | N
RP | Febco | LF825YA | 0.75 | VUVD | 2010-02-18 | 2022-02-18 | Y | 8 | (qqqqq), hhhh | N
RP | Febco | LF825YA | 1 | H | 2010-02-18 | 2022-02-18 | Y | 8 | (qqqqq), hhhh | N
RP | Febco | LF825YA | 1 | HVD | 2010-02-18 | 2022-02-18 | Y | 8 | (qqqqq), hhhh | N
RP | Febco | LF825YA | 1 | VUH | 2010-02-18 | 2022-02-18 | Y | 8 | (qqqqq), hhhh | N
RP | Febco | LF825YA | 1 | VUVD | 2010-02-18 | 2022-02-18 | Y | 8 | (qqqqq), hhhh | N
RP | Febco | LF825YA | 1.5 | H | 2010-03-25 | 2022-03-25 | Y | 8 | (qqqqq), hhhh | N
RP | Febco | LF825YA | 1.5 | HVD | 2010-03-25 | 2022-03-25 | Y | 8 | (qqqqq), hhhh | N
RP | Febco | LF825YA | 1.5 | VUH | 2010-03-25 | 2022-03-25 | Y | 8 | (qqqqq), hhhh | N
RP | Febco | LF825YA | 1.5 | VUVD | 2010-03-25 | 2022-03-25 | Y | 8 | (qqqqq), hhhh | N
RP | Febco | LF825YA | 2 | H | 2010-03-25 | 2022-03-25 | Y | 8 | (qqqqq), hhhh | N
RP | Febco | LF825YA | 2 | HVD | 2010-03-25 | 2022-03-25 | Y | 8 | (qqqqq), hhhh | N
RP | Febco | LF825YA | 2 | VUH | 2010-03-25 | 2022-03-25 | Y | 8 | (qqqqq), hhhh | N
RP | Febco | LF825YA | 2 | VUVD | 2010-03-25 | 2022-03-25 | Y | 8 | (qqqqq), hhhh | N
RP | Febco | LF860 | 0.5 | H | 2010-02-18 | 2022-02-18 | Y | 9 | (qqqqq), hhhh | N
RP | Febco | LF860 | 0.75 | H | 2010-02-18 | 2022-02-18 | Y | 9 | (qqqqq), hhhh | N
RP | Febco | LF860 | 1 | H | 2010-02-18 | 2022-02-18 | Y | 9 | (qqqqq), hhhh | N
RP | Febco | LF860 | 1.25 | H | 2010-02-18 | 2022-02-18 | Y | 9 | (qqqqq), hhhh | N
RP | Febco | LF860 | 1.5 | H | 2010-02-18 | 2022-02-18 | Y | 9 | (qqqqq), hhhh | N
RP | Febco | LF860 | 2 | H | 2010-02-18 | 2022-02-18 | Y | 9 | (qqqqq), hhhh | N
RP | Febco | LF860 | 2.5 | H | 2013-05-28 | 2022-05-28 | Y | 9 | (ll),mm,oo,pp,zzz,cccc,dddd,eeee,ffff,gggg,nnnnn,zzzzzz,aaaaaaa | N
RP | Febco | LF860 | 3 | H | 2013-05-28 | 2022-05-28 | Y | 9 | (ll),mm,oo,pp,zzz,cccc,dddd,eeee,ffff,gggg,nnnnn,zzzzzz,aaaaaaa | N
RP | Febco | LF860 | 4 | H | 2013-06-14 | 2022-06-14 | Y | 9 | (ll),mm,oo,pp,zzz,cccc,dddd,eeee,ffff,gggg,nnnnn,zzzzzz,aaaaaaa | N
RP | Febco | LF860 | 6 | H | 2013-06-14 | 2022-06-14 | Y | 9 | (ll),mm,oo,pp,zzz,cccc,dddd,eeee,ffff,gggg,nnnnn,zzzzzz,aaaaaaa | N
RP | Febco | LF860 | 8 | H | 2013-09-03 | 2022-09-03 | Y | 9 | (ll),mm,oo,pp,zzz,cccc,dddd,eeee,ffff,gggg,nnnnn,zzzzzz,aaaaaaa | N
RP | Febco | LF860 | 10 | H | 2013-09-25 | 2022-09-25 | Y | 9 | (ll),mm,oo,pp,zzz,cccc,dddd,eeee,ffff,gggg,nnnnn | N
RP | Febco | LF860U | 0.5 | H | 2013-09-03 | 2022-09-03 | Y | 9 | (ppppp), hhhh | N
RP | Febco | LF860U | 0.75 | H | 2013-09-03 | 2022-09-03 | Y | 9 | (ppppp), hhhh | N
RP | Febco | LF860U | 1 | H | 2013-09-03 | 2022-09-03 | Y | 9 | (ppppp), hhhh | N
RP | Febco | LF860U | 1.25 | H | 2013-09-03 | 2022-09-03 | Y | 9 | (ppppp), hhhh | N
RP | Febco | LF860U | 1.5 | H | 2013-09-03 | 2022-09-03 | Y | 9 | (ppppp), hhhh | N
RP | Febco | LF860U | 2 | H | 2013-09-03 | 2022-09-03 | Y | 9 | (ppppp), hhhh | N
RP | Febco | LF880V | 2.5 | VUVD | 2013-05-28 | 2022-05-28 | Y | 9 | (ll),mm,oo,pp,zzz,cccc,dddd,eeee,ffff,gggg,nnnnn,zzzzzz,aaaaaaa | N
RP | Febco | LF880V | 2.5 | VUVU | 2013-05-28 | 2022-05-28 | Y | 9 | (ll),mm,oo,pp,zzz,cccc,dddd,eeee,ffff,gggg,nnnnn,zzzzzz,aaaaaaa | N
RP | Febco | LF880V | 3 | VUVD | 2013-05-28 | 2022-05-28 | Y | 9 | (ll),mm,oo,pp,zzz,cccc,dddd,eeee,ffff,gggg,nnnnn,zzzzzz,aaaaaaa | N
RP | Febco | LF880V | 3 | VUVU | 2013-05-28 | 2022-05-28 | Y | 9 | (ll),mm,oo,pp,zzz,cccc,dddd,eeee,ffff,gggg,nnnnn,zzzzzz,aaaaaaa | N
RP | Febco | LF880V | 4 | VUVD | 2013-05-28 | 2022-05-28 | Y | 9 | (ll),mm,oo,pp,zzz,cccc,dddd,eeee,ffff,gggg,nnnnn,zzzzzz,aaaaaaa | N
RP | Febco | LF880V | 4 | VUVU | 2013-05-28 | 2022-05-28 | Y | 9 | (ll),mm,oo,pp,zzz,cccc,dddd,eeee,ffff,gggg,nnnnn,zzzzzz,aaaaaaa | N
RP | Febco | LF880V | 6 | VUVD | 2013-09-03 | 2022-09-03 | Y | 9 | (ll),mm,oo,pp,zzz,cccc,dddd,eeee,ffff,gggg,nnnnn,zzzzzz,aaaaaaa | N
RP | Febco | LF880V | 6 | VUVU | 2013-09-03 | 2022-09-03 | Y | 9 | (ll),mm,oo,pp,zzz,cccc,dddd,eeee,ffff,gggg,nnnnn,zzzzzz,aaaaaaa | N
RP | Febco | LF880V | 8 | VUVD | 2013-11-26 | 2022-11-26 | Y | 9 | (ll),mm,oo,pp,zzz,cccc,dddd,eeee,ffff,gggg,nnnnn,zzzzzz,aaaaaaa | N
RP | Febco | LF880V | 8 | VUVU | 2013-11-26 | 2022-11-26 | Y | 9 | (ll),mm,oo,pp,zzz,cccc,dddd,eeee,ffff,gggg,nnnnn,zzzzzz,aaaaaaa | N
RP | Febco | LF880V | 10 | VUVD | 2018-05-29 | 2024-05-29 | Y | 10 | (ll),mm,oo,pp,zzz,cccc,dddd,eeee,ffff,gggg,nnnnn | N
RP | Febco | LF880V | 10 | VUVU | 2018-05-29 | 2024-05-29 | Y | 10 | (ll),mm,oo,pp,zzz,cccc,dddd,eeee,ffff,gggg,nnnnn | N
RP | Febco | LF880W | 4 | VUVD | 2020-03-26 | 2023-03-26 | Y | 9 | (mm), ll,oo,pp,zzz,cccc,dddd,eeee,ffff,gggg,nnnnn,zzzzzz,aaaaaaa | N
RP | Febco | LF880W | 4 | VUVU | 2020-03-26 | 2023-03-26 | Y | 9 | (mm), ll,oo,pp,zzz,cccc,dddd,eeee,ffff,gggg,nnnnn,zzzzzz,aaaaaaa | N
RP | Febco | LF880W | 6 | VUVD | 2020-03-26 | 2023-03-26 | Y | 9 | (mm), ll,oo,pp,zzz,cccc,dddd,eeee,ffff,gggg,nnnnn,zzzzzz,aaaaaaa | N
RP | Febco | LF880W | 6 | VUVU | 2020-03-26 | 2023-03-26 | Y | 9 | (mm), ll,oo,pp,zzz,cccc,dddd,eeee,ffff,gggg,nnnnn,zzzzzz,aaaaaaa | N
RP | Febco | LF880W | 8 | VUVD | 2020-05-15 | 2023-05-15 | Y | 9 | (mm), ll,oo,pp,zzz,cccc,dddd,eeee,ffff,gggg,nnnnn,zzzzzz,aaaaaaa | N
RP | Febco | LF880W | 8 | VUVU | 2020-05-15 | 2023-05-15 | Y | 9 | (mm), ll,oo,pp,zzz,cccc,dddd,eeee,ffff,gggg,nnnnn,zzzzzz,aaaaaaa | N
RP | Febco | LF880W | 10 | VUVD | 2020-05-15 | 2023-05-15 | Y | 10 | (ll),mm,oo,pp,zzz,cccc,dddd,eeee,ffff,gggg,nnnnn | N
RP | Febco | LF880W | 10 | VUVU | 2020-05-15 | 2023-05-15 | Y | 10 | (ll),mm,oo,pp,zzz,cccc,dddd,eeee,ffff,gggg,nnnnn | N
RP | Febco | LF880WZ | 4 | VUVD | 2020-03-26 | 2023-03-26 | Y | 9 | (mm), ll,oo,pp,zzz,cccc,dddd,eeee,ffff,gggg,nnnnn,zzzzzz,aaaaaaa | N
RP | Febco | LF880WZ | 4 | VUVU | 2020-03-26 | 2023-03-26 | Y | 9 | (mm), ll,oo,pp,zzz,cccc,dddd,eeee,ffff,gggg,nnnnn,zzzzzz,aaaaaaa | N
RP | Febco | LF880WZ | 6 | VUVD | 2020-03-26 | 2023-03-26 | Y | 9 | (mm), ll,oo,pp,zzz,cccc,dddd,eeee,ffff,gggg,nnnnn,zzzzzz,aaaaaaa | N
RP | Febco | LF880WZ | 6 | VUVU | 2020-03-26 | 2023-03-26 | Y | 9 | (mm), ll,oo,pp,zzz,cccc,dddd,eeee,ffff,gggg,nnnnn,zzzzzz,aaaaaaa | N
RP | Febco | LF880WZ | 8 | VUVD | 2020-05-15 | 2023-05-15 | Y | 9 | (mm), ll,oo,pp,zzz,cccc,dddd,eeee,ffff,gggg,nnnnn,zzzzzz,aaaaaaa | N
RP | Febco | LF880WZ | 8 | VUVU | 2020-05-15 | 2023-05-15 | Y | 9 | (mm), ll,oo,pp,zzz,cccc,dddd,eeee,ffff,gggg,nnnnn,zzzzzz,aaaaaaa | N
RP | Febco | LF880WZ | 10 | VUVD | 2020-05-15 | 2023-05-15 | Y | 10 | (ll),mm,oo,pp,zzz,cccc,dddd,eeee,ffff,gggg,nnnnn | N
RP | Febco | LF880WZ | 10 | VUVU | 2020-05-15 | 2023-05-15 | Y | 10 | (ll),mm,oo,pp,zzz,cccc,dddd,eeee,ffff,gggg,nnnnn | N
RP | Neptune | [5 empty] | N | [5 empty] | See Wilkins
RP | Watts | 909 | 2.5 | H | 1986-06-12 | 2022-06-12 | N | 7 | (oo),gg,hh,ll,mm,pp,tt,uu,ww,yy,ffff,gggg | Y
RP | Watts | 909 | 3 | H | 1986-06-12 | 2022-06-12 | N | 7 | (oo),gg,hh,ll,mm,pp,tt,uu,ww,yy,eee,ffff,gggg | Y |  |  | formerly 909NRS/909OSY/909NRSRW/909OSYRW/909RW
RP | Watts | 909 | 4 | H | 1982-01-15 | 2024-01-15 | N | 6 | (oo),gg,hh,ll,mm,pp,tt,uu,ww,yy,eee,ffff,gggg | Y |  |  | formerly 909NRS/909OSY/909NRSRW/909OSYRW/909RW
RP | Watts | 909 | 6 | H | 1981-07-06 | 2023-07-06 | N | 6 | (oo),gg,hh,ll,mm,pp,tt,uu,ww,yy,eee,ffff,gggg | Y |  |  | formerly 909NRS/909OSY/909NRSRW/909OSYRW/909RW
RP | Watts | 909 | 8 | H | 1981-07-06 | 2023-07-06 | N | 6 |  | Y |  |  | formerly 909NRS/909OSY/909NRSRW/909OSYRW/909RW
RP | Watts | 909 | 10 | H | 1981-07-06 | 2023-07-06 | N | 6 |  | Y |  |  | formerly 909NRS/909OSY/909NRSRW/909OSYRW/909RW
RP | Watts | 957 | 2.5 | H | 2002-10-07 | 2023-10-07 | N | 9 | (ppp),qqq,aaaa,bbbb | N |  |  | Check valve discs may be black EPDM or orange Silicone
RP | Watts | 957 | 2.5 | H | 2002-10-07 | 2023-10-07 | Y | 9 | zzz,dddd,eeee,gggg,kkkk,llll,mmmm,nnnn,nnnnn | N |  |  | Check valve discs may be black EPDM or orange Silicone
RP | Watts | 957 | 3 | H | 2002-10-07 | 2023-10-07 | N | 9 | (ppp),qqq,aaaa,bbbb | N |  |  | Check valve discs may be black EPDM or orange Silicone
RP | Watts | 957 | 3 | H | 2002-10-07 | 2023-10-07 | Y | 9 | zzz,dddd,eeee,gggg,kkkk,llll,mmmm,nnnn,nnnnn | N |  |  | Check valve discs may be black EPDM or orange Silicone
RP | Watts | 957 | 4 | H | 2002-10-07 | 2023-10-07 | N | 9 | (ppp),qqq,aaaa,bbbb | N |  |  | Check valve discs may be black EPDM or orange Silicone
RP | Watts | 957 | 4 | H | 2002-10-07 | 2023-10-07 | Y | 9 | zzz,dddd,eeee,gggg,kkkk,llll,mmmm,nnnn,nnnnn | N |  |  | Check valve discs may be black EPDM or orange Silicone
RP | Watts | 957 | 6 | H | 2004-12-20 | 2022-12-20 | N | 9 | (ppp),qqq,aaaa,bbbb | N
RP | Watts | 957 | 6 | H | 2004-12-20 | 2022-12-20 | Y | 9 | zzz,dddd,eeee,gggg,kkkk,llll,mmmm,nnnn,nnnnn | N
RP | Watts | 957 | 8 | H | 2007-08-13 | 2022-08-13 | N | 9 | (ppp),qqq,aaaa,bbbb | N
RP | Watts | 957 | 8 | H | 2007-08-13 | 2022-08-13 | Y | 9 | zzz,cccc,dddd,eeee,gggg,kkkk,llll,mmmm,nnnn,nnnnn | N
RP | Watts | 957 | 10 | H | 2009-07-22 | 2024-07-22 | N | 9 | (ppp),qqq,aaaa,bbbb | N
RP | Watts | 957 | 10 | H | 2009-07-22 | 2024-07-22 | Y | 9 | zzz,cccc,dddd,eeee,gggg,kkkk,llll,mmmm,nnnn,nnnnn | N
RP | Watts | 967 | 2.5 | H | 2002-10-07 | 2023-10-07 | N | 9 | (ppp),qqq,zzz,aaaa,bbbb,dddd,eeee,ffff,gggg,kkkk,llll,mmmm,nnnn,nnnnn | N
RP | Watts | 967 | 3 | H | 2002-10-07 | 2023-10-07 | N | 9 | (ppp),qqq,zzz,aaaa,bbbb,dddd,eeee,ffff,gggg,kkkk,llll,mmmm,nnnn,nnnnn | N
RP | Watts | 967 | 4 | H | 2005-01-18 | 2023-01-18 | N | 9 | (ppp),qqq,aaaa,bbbb,gggg,kkkk,llll,mmmm,nnnn,nnnnn | N
RP | Watts | 967 | 6 | H | 2007-08-13 | 2022-08-13 | N | 9 | (ppp),qqq,sss, ttt, aaaa,bbbb,cccc,dddd,kkkk,llll,mmmm,nnnn,nnnnn | N
RP | Watts | 967 | 8 | H | 2009-07-22 | 2024-07-22 | N | 9 | (ppp),qqq,sss,ttt,zzz,aaaa,bbbb,cccc,dddd,eeee,gggg,kkkk,llll,mmmm,nnnn,nnnnn | N
RP | Watts | 967 | 10 | H | 2009-07-22 | 2024-07-22 | N | 9 | (ppp),qqq,sss,ttt,zzz,aaaa,bbbb,cccc,dddd,eeee,gggg,kkkk,llll,mmmm,nnnn | N
RP | Watts | 990 | 4 | H | 1992-11-01 | 2022-11-01 | N | 8 | oo,gg,hh,pp,tt,uu,yy | Y
RP | Watts | 990 | 8 | H | 1993-01-13 | 2023-01-13 | N | 8 | oo,gg,hh,pp,tt,uu,yy | Y
RP | Watts | 992 | 4 | H | 1992-11-01 | 2022-11-01 | N | 8 | oo | Y
RP | Watts | 992 | 10 | H | 1993-01-13 | 2023-01-13 | N | 8 | oo | Y
RP | Watts | 994 | 2.5 | H | 1994-04-15 | 2024-04-15 | N | 8 | (tt),ee,ff,gg,hh,pp,uu,ccc,ddd | N
RP | Watts | 994 | 2.5 | H | 1994-04-15 | 2024-04-15 | Y | 8 | ll,mm,oo,ffff,gggg | N
RP | Watts | 994 | 3 | H | 1994-04-15 | 2024-04-15 | N | 8 | (tt),ee,ff,gg,hh,pp,uu,ccc,ddd | N
RP | Watts | 994 | 3 | H | 1994-04-15 | 2024-04-15 | Y | 8 | ll,mm,oo,ffff,gggg | N
RP | Watts | 994 | 4 | H | 1994-04-15 | 2024-04-15 | N | 8 | (tt),ee,ff,gg,hh,pp,uu,ccc,ddd | N
RP | Watts | 994 | 4 | H | 1994-04-15 | 2024-04-15 | Y | 8 | ll,mm,oo,ffff,gggg | N
RP | Watts | 994 | 6 | H | 1997-09-22 | 2024-09-22 | N | 8 | (tt),ee,ff,gg,hh,pp,uu,ccc,ddd | N
RP | Watts | 994 | 6 | H | 1997-09-22 | 2024-09-22 | Y | 8 | ll,mm,oo,ffff,gggg | N
RP | Watts | 009 | 2.5 | H | 1990-08-31 | 2023-08-31 | N | 8 | (oo),gg,hh,ll,mm,pp,tt,uu,yy,ffff,gggg | Y
RP | Watts | 009 | 3 | H | 1990-08-31 | 2023-08-31 | N | 8 | (oo),gg,hh,ll,mm,pp,tt,uu,yy,eee,ffff,gggg | Y
RP | Watts | 009M1PCQT | 1.25 | H | 1994-09-27 | 2024-09-27 | N | 8 | vv,xx,ooo,hhhh,pppp,rrrrr | Y
RP | Watts | 009M1PCQT | 1.5 | H | 1994-09-27 | 2024-09-27 | N | 8 | vv,xx,ooo,hhhh,pppp,rrrrr | Y
RP | Watts | 009M1PCQT | 2 | H | 1994-09-27 | 2024-09-27 | N | 8 | vv,xx,ooo,hhhh,pppp,rrrrr | Y
RP | Watts | 009M1QT | 1.25 | H | 1992-06-30 | 2022-06-30 | N | 8 | vv,xx,ooo,hhhh,pppp,rrrrr | Y
RP | Watts | 009M1QT | 1.5 | H | 1992-06-30 | 2022-06-30 | N | 8 | vv,xx,ooo,hhhh,pppp,rrrrr | Y
RP | Watts | 009M1QT | 2 | H | 1991-12-19 | 2024-12-19 | N | 8 | vv,xx,ooo,hhhh,pppp,rrrrr | Y
RP | Watts | 009M2-FP | 1 | H | 2009-09-01 | 2024-09-01 | N | 9 | (eeeee) | N
RP | Watts | 009M2-FP | 1.25 | H | 2009-09-01 | 2024-09-01 | N | 9 | (eeeee) | N
RP | Watts | 009M2-FP | 1.5 | H | 2009-09-01 | 2024-09-01 | N | 9 | (eeeee) | N
RP | Watts | 009M2-FP | 2 | H | 2009-09-01 | 2024-09-01 | N | 9 | (eeeee) | N
RP | Watts | 009M2PCQT | 0.75 | H | 2002-10-07 | 2023-10-07 | N | 8 | (vv),xx,ooo,hhhh,pppp,rrrrr | N
RP | Watts | 009M2PCQT | 1 | H | 1999-01-15 | 2023-01-15 | N | 9 | (vv),xx,ooo,hhhh,pppp,rrrrr | N
RP | Watts | 009M2PCQT | 1.25 | H | 1994-09-12 | 2024-09-12 | N | 8 | (vv),xx,ooo,hhhh,pppp,rrrrr | N
RP | Watts | 009M2PCQT | 1.5 | H | 1994-09-12 | 2024-09-12 | N | 8 | (vv),xx,ooo,hhhh,pppp,rrrrr | N
RP | Watts | 009M2PCQT | 2 | H | 1997-08-26 | 2024-08-26 | N | 9 | (vv),xx,ooo,hhhh,pppp,rrrrr | N
RP | Watts | 009M2QT | 0.75 | H | 1992-10-31 | 2022-10-31 | N | 8 | (vv),xx,ooo,hhhh,pppp,rrrrr | N
RP | Watts | 009M2QT | 1 | H | 1998-05-18 | 2022-05-18 | N | 9 | (vv),xx,ooo,hhhh,pppp,rrrrr | N
RP | Watts | 009M2QT | 1.25 | H | 1993-08-24 | 2023-08-24 | N | 8 | (vv),xx,ooo,hhhh,pppp,rrrrr | N
RP | Watts | 009M2QT | 1.5 | H | 1993-08-24 | 2023-08-24 | N | 8 | (vv),xx,ooo,hhhh,pppp,rrrrr | N
RP | Watts | 009M2QT | 2 | H | 1996-09-10 | 2023-09-10 | N | 9 | (vv),xx,ooo,hhhh,pppp,rrrrr | N
RP | Watts | 009M3-FP | 0.75 | H | 2009-09-01 | 2024-09-01 | N | 9 | (eeeee) | N
RP | Watts | 009M3QT | 0.75 | H | 1999-10-18 | 2023-10-18 | N | 9 | (vv),xx,ooo,hhhh,pppp,rrrrr | N
RP | Watts | 009PCQT | 0.5 | H | 1995-02-17 | 2022-02-17 | N | 8 | (vv),xx,ooo,hhhh,pppp,rrrrr | Y
RP | Watts | 009PCQT | 0.75 | H | 1993-12-10 | 2023-12-10 | N | 8 | (vv),xx,ooo,hhhh,pppp,rrrrr | Y
RP | Watts | 009PCQT | 1 | H | 1993-12-10 | 2023-12-10 | N | 8 | vv,xx,ooo,hhhh,pppp,rrrrr | Y
RP | Watts | 009PCQT | 1.25 | H | 1994-09-27 | 2024-09-27 | N | 8 | vv,xx,ooo,hhhh,pppp,rrrrr | Y
RP | Watts | 009PCQT | 1.5 | H | 1994-09-27 | 2024-09-27 | N | 8 | vv,xx,ooo,hhhh,pppp,rrrrr | Y
RP | Watts | 009PCQT | 2 | H | 1994-09-27 | 2024-09-27 | N | 8 | vv,xx,ooo,hhhh,pppp,rrrrr | Y
RP | Watts | 009QT | 0.25 | H | 1995-08-07 | 2022-08-07 | N | 8 | (vv),xx,ooo,hhhh,pppp | N
RP | Watts | 009QT | 0.375 | H | 1995-08-07 | 2022-08-07 | N | 8 | (vv),xx,ooo,hhhh,pppp | N
RP | Watts | 009QT | 0.5 | H | 1996-09-10 | 2023-09-10 | N | 9 | (vv),xx,ooo,hhhh,pppp,rrrrr | N |  |  | Previously approved 8th Ed. 26 May 1993
RP | Watts | 009QT | 0.75 | H | 1988-01-11 | 2024-01-11 | N | 7 | (vv),xx,ooo,hhhh,pppp,rrrrr | Y
RP | Watts | 009QT | 1 | H | 1988-01-11 | 2024-01-11 | N | 7 | vv,xx,ooo,hhhh,pppp,rrrrr | Y
RP | Watts | 009QT | 1.25 | H | 1988-08-09 | 2024-08-09 | N | 7 | vv,xx,ooo,hhhh,pppp,rrrrr | Y
RP | Watts | 009QT | 1.5 | H | 1988-08-09 | 2024-08-09 | N | 7 | vv,xx,ooo,hhhh,pppp,rrrrr | Y
RP | Watts | 009QT | 2 | H | 1988-08-09 | 2024-08-09 | N | 7 | vv,xx,ooo,hhhh,pppp,rrrrr | Y
RP | Watts | 009SSM1PCQT | 2 | H | 1994-09-27 | 2024-09-27 | N | 8 | vv,xx,pppp | Y
RP | Watts | 009SSM1QT | 2 | H | 1991-12-19 | 2024-12-19 | N | 8 | vv,xx,pppp | Y
RP | Watts | 009SSPCQT | 0.75 | H | 1993-12-10 | 2023-12-10 | N | 8 | vv,xx,pppp | Y
RP | Watts | 009SSPCQT | 1 | H | 1993-12-10 | 2023-12-10 | N | 8 | vv,xx,pppp | Y
RP | Watts | 009SSPCQT | 1.25 | H | 1994-09-27 | 2024-09-27 | N | 8 | vv,xx,pppp | Y
RP | Watts | 009SSPCQT | 1.5 | H | 1994-09-27 | 2024-09-27 | N | 8 | vv,xx,pppp | Y
RP | Watts | 009SSPCQT | 2 | H | 1994-09-27 | 2024-09-27 | N | 8 | vv,xx,pppp | Y
RP | Watts | 009SSQT | 0.75 | H | 1988-01-11 | 2024-01-11 | N | 7 | vv,xx,pppp | Y
RP | Watts | 009SSQT | 1 | H | 1988-01-11 | 2024-01-11 | N | 7 | vv,xx,pppp | Y
RP | Watts | 009SSQT | 1.25 | H | 1988-08-09 | 2024-08-09 | N | 7 | vv,xx,pppp | Y
RP | Watts | 009SSQT | 1.5 | H | 1988-08-09 | 2024-08-09 | N | 7 | vv,xx,pppp | Y
RP | Watts | 009SSQT | 2 | H | 1988-08-09 | 2024-08-09 | N | 7 | vv,xx,pppp | Y
RP | Watts | 909BB | 2.5 | H | 1983-02-04 | 2022-02-04 | N | 6 | (oo),gg,hh,ll,mm,pp,tt,uu,yy,ffff,gggg | Y
RP | Watts | 909BB | 3 | H | 1983-02-04 | 2022-02-04 | N | 6 | (oo),gg,hh,ll,mm,pp,tt,uu,yy,ffff,gggg | Y
RP | Watts | 909HWQT | 0.75 | H | 1979-09-29 | 2024-09-29 | N | 5 | (vv),xx,ooo,hhhh,pppp,rrrrr | Y
RP | Watts | 909HWQT | 1 | H | 1979-09-29 | 2024-09-29 | N | 5 | (vv),xx,ooo,hhhh,pppp,rrrrr | Y
RP | Watts | 909HWQT | 1.25 | [9 empty] | model designation changed to 909M1HWQT
RP | Watts | 909HWQT | 1.5 | [9 empty] | model designation changed to 909M1HWQT
RP | Watts | 909HWQT | 2 | [9 empty] | model designation changed to 909M1HWQT
RP | Watts | 909M1 | 8 | H | 1989-05-01 | 2022-05-01 | N | 8 | (oo),gg,hh,ll,mm,pp,tt,uu,yy,ww,ffff,gggg | Y
RP | Watts | 909M1 | 10 | H | 1989-05-01 | 2022-05-01 | N | 8 | (oo),gg,hh,ll,mm,pp,tt,uu,ww,yy,ffff,gggg | Y
RP | Watts | 909M1HWQT | 1.25 | H | 1980-02-07 | 2022-02-07 | N | 5 | (vv),xx,ooo,hhhh,rrrrr | Y |  |  | formerly 909HWQT
RP | Watts | 909M1HWQT | 1.5 | H | 1980-02-07 | 2022-02-07 | N | 5 | (vv),xx,ooo,hhhh,rrrrr | Y |  |  | formerly 909HWQT
RP | Watts | 909M1HWQT | 2 | H | 1980-02-07 | 2022-02-07 | N | 5 | (vv),xx,ooo,hhhh,rrrrr | Y |  |  | formerly 909HWQT
RP | Watts | 909M1PCHWQT | 1.25 | H | 1995-02-02 | 2022-02-02 | N | 8 | (vv),xx,ooo,hhhh,rrrrr | Y
RP | Watts | 909M1PCHWQT | 1.5 | H | 1995-02-02 | 2022-02-02 | N | 8 | (vv),xx,ooo,hhhh,rrrrr | Y
RP | Watts | 909M1PCHWQT | 2 | H | 1995-02-02 | 2022-02-02 | N | 8 | (vv),xx,ooo,hhhh,rrrrr | Y
RP | Watts | 909M1QT | 1.25 | H | 1982-01-15 | 2024-01-15 | N | 6 | (vv),xx,ooo,hhhh,pppp,rrrrr | Y |  |  | formerly 909QT
RP | Watts | 909M1QT | 1.5 | H | 1982-01-15 | 2024-01-15 | N | 6 | (vv),xx,ooo,hhhh,pppp,rrrrr | Y |  |  | formerly 909QT
RP | Watts | 909M1QT | 2 | H | 1982-01-15 | 2024-01-15 | N | 6 | (vv),xx,ooo,hhhh,pppp,rrrrr | Y |  |  | formerly 909QT
RP | Watts | 909NRS | 3 | [9 empty] | model designation changed to 909
RP | Watts | 909NRS | 4 | [9 empty] | model designation changed to 909
RP | Watts | 909NRS | 6 | [9 empty] | model designation changed to 909
RP | Watts | 909NRS | 8 | [9 empty] | model designation changed to 909
RP | Watts | 909NRS | 10 | [9 empty] | model designation changed to 909
RP | Watts | 909NRSRW | 3 | [9 empty] | model designation changed to 909
RP | Watts | 909NRSRW | 4 | [9 empty] | model designation changed to 909
RP | Watts | 909NRSRW | 6 | [9 empty] | model designation changed to 909
RP | Watts | 909NRSRW | 8 | [9 empty] | model designation changed to 909
RP | Watts | 909NRSRW | 10 | [9 empty] | model designation changed to 909
RP | Watts | 909OSY | 3 | [9 empty] | model designation changed to 909
RP | Watts | 909OSY | 4 | [9 empty] | model designation changed to 909
RP | Watts | 909OSY | 6 | [9 empty] | model designation changed to 909
RP | Watts | 909OSY | 8 | [9 empty] | model designation changed to 909
RP | Watts | 909OSY | 10 | [9 empty] | model designation changed to 909
RP | Watts | 909OSYRW | 3 | [9 empty] | model designation changed to 909
RP | Watts | 909OSYRW | 4 | [9 empty] | model designation changed to 909
RP | Watts | 909OSYRW | 6 | [9 empty] | model designation changed to 909
RP | Watts | 909OSYRW | 8 | [9 empty] | model designation changed to 909
RP | Watts | 909OSYRW | 10 | [9 empty] | model designation changed to 909
RP | Watts | 909PCHWQT | 0.75 | H | 1995-02-02 | 2022-02-02 | N | 8 | (vv),xx,ooo,hhhh,pppp,rrrrr | Y
RP | Watts | 909PCHWQT | 1 | H | 1995-02-02 | 2022-02-02 | N | 8 | (vv),xx,ooo,hhhh,pppp,rrrrr | Y
RP | Watts | 909PCM1QT | 1.25 | H | 1995-02-02 | 2022-02-02 | N | 8 | (vv),xx,ooo,hhhh,pppp,rrrrr | Y
RP | Watts | 909PCM1QT | 1.5 | H | 1995-02-02 | 2022-02-02 | N | 8 | (vv),xx,ooo,hhhh,pppp,rrrrr | Y
RP | Watts | 909PCM1QT | 2 | H | 1995-02-02 | 2022-02-02 | N | 8 | (vv),xx,ooo,hhhh,pppp,rrrrr | Y
RP | Watts | 909PCQT | 0.75 | H | 1998-10-09 | 2022-10-09 | N | 9 | (vv),xx,ooo,hhhh,pppp,rrrrr | Y |  |  | Previously Approved 8th Ed (2 February 1995) 9th Ed. for Ser. Nos. 464100 and higher
RP | Watts | 909PCQT | 0.75 | VU | 1998-10-09 | 2022-10-09 | N | 9 | (vv),xx,ooo,hhhh,pppp,rrrrr | Y |  |  | Serial number 464100 and higher
RP | Watts | 909PCQT | 1 | H | 1998-10-09 | 2022-10-09 | N | 9 | (vv),xx,ooo,hhhh,pppp,rrrrr | Y |  |  | Previously Approved 8th Ed (2 February 1995) 9th Ed. for Ser. Nos. 464100 and higher
RP | Watts | 909PCQT | 1 | VU | 1998-10-09 | 2022-10-09 | N | 9 | (vv),xx,ooo,hhhh,pppp,rrrrr | Y |  |  | Previously Approved 8th Ed (2 February 1995) 9th Ed. for Ser. Nos. 464100 and higher
RP | Watts | 909QT | 0.75 | H | 1998-06-18 | 2022-06-18 | N | 9 | (vv),xx,ooo,hhhh,pppp,rrrrr | Y |  |  | Previously Approved 6th Ed. (15 Jan 1982) 9th Ed. For Ser. Nos. 461650 and higher
RP | Watts | 909QT | 0.75 | VU | 1998-06-18 | 2022-06-18 | N | 9 | (vv),xx,ooo,hhhh,pppp,rrrrr | Y |  |  | Serial number 461650 and higher
RP | Watts | 909QT | 1 | H | 1998-06-18 | 2022-06-18 | N | 9 | (vv),xx,ooo,hhhh,pppp,rrrrr | Y |  |  | Previously Approved 6th Ed. (15 Jan 1982) 9th Ed. For Ser. Nos. 461650 and higher
RP | Watts | 909QT | 1 | VU | 1998-06-18 | 2022-06-18 | N | 9 | (vv),xx,ooo,hhhh,pppp,rrrrr | Y |  |  | Serial number 461650 and higher
RP | Watts | 909QT | 1.25 | [9 empty] | model designation changed to 909M1QT
RP | Watts | 909QT | 1.5 | [9 empty] | model designation changed to 909M1QT
RP | Watts | 909QT | 2 | [9 empty] | model designation changed to 909M1QT
RP | Watts | 909RW | 3 | [9 empty] | model designation changed to 909
RP | Watts | 909RW | 4 | [9 empty] | model designation changed to 909
RP | Watts | 909RW | 6 | [9 empty] | model designation changed to 909
RP | Watts | 909RW | 8 | [9 empty] | model designation changed to 909
RP | Watts | 909RW | 10 | [9 empty] | model designation changed to 909
RP | Watts | 919AQT | 0.75 | VUVD | 2006-06-14 | 2024-06-14 | N | 9 | (vv),xx,ooo,hhhh,pppp,rrrrr | Y
RP | Watts | 919AQT | 1 | VUVD | 2006-06-01 | 2024-06-01 | N | 9 | (vv),xx,ooo,hhhh,pppp,rrrrr | N
RP | Watts | 919AQT | 1.25 | VUVD | 2006-09-05 | 2024-09-05 | N | 9 | (vv),xx,ooo,hhhh,pppp,rrrrr | N
RP | Watts | 919AQT | 1.5 | VUVD | 2006-06-01 | 2024-06-01 | N | 9 | (vv),xx,ooo,hhhh,pppp,rrrrr | N
RP | Watts | 919AQT | 2 | VUVD | 2006-06-01 | 2024-06-01 | N | 9 | (vv),xx,ooo,hhhh,pppp,rrrrr | N
RP | Watts | 919QT | 0.75 | H | 2006-06-14 | 2024-06-14 | N | 9 | (vv),xx,ooo,hhhh,pppp,rrrrr | N
RP | Watts | 919QT | 0.75 | VD | 2006-08-30 | 2024-08-30 | N | 9 | (vv),xx,ooo,hhhh,pppp,rrrrr | N
RP | Watts | 919QT | 1 | H | 2006-06-01 | 2024-06-01 | N | 9 | (vv),xx,ooo,hhhh,pppp,rrrrr | N
RP | Watts | 919QT | 1 | VD | 2006-08-30 | 2024-08-30 | N | 9 | (vv),xx,ooo,hhhh,pppp,rrrrr | N
RP | Watts | 919QT | 1.25 | H | 2006-06-01 | 2024-06-01 | N | 9 | (vv),xx,ooo,hhhh,pppp,rrrrr | N
RP | Watts | 919QT | 1.25 | VD | 2006-08-30 | 2024-08-30 | N | 9 | (vv),xx,ooo,hhhh,pppp,rrrrr | N
RP | Watts | 919QT | 1.5 | H | 2006-06-01 | 2024-06-01 | N | 9 | (vv),xx,ooo,hhhh,pppp,rrrrr | N
RP | Watts | 919QT | 1.5 | VD | 2006-08-30 | 2024-08-30 | N | 9 | (vv),xx,ooo,hhhh,pppp,rrrrr | N
RP | Watts | 919QT | 2 | H | 2006-06-01 | 2024-06-01 | N | 9 | (vv),xx,ooo,hhhh,pppp,rrrrr | N
RP | Watts | 919QT | 2 | VD | 2006-08-30 | 2024-08-30 | N | 9 | (vv),xx,ooo,hhhh,pppp,rrrrr | N
RP | Watts | 919ZQT | 0.75 | VUVU | 2006-06-14 | 2024-06-14 | N | 9 | (vv),xx,ooo,hhhh,pppp,rrrrr | Y
RP | Watts | 919ZQT | 1 | VUVU | 2006-06-01 | 2024-06-01 | N | 9 | (vv),xx,ooo,hhhh,pppp,rrrrr | N
RP | Watts | 919ZQT | 1.25 | VUVU | 2006-06-01 | 2024-06-01 | N | 9 | (vv),xx,ooo,hhhh,pppp,rrrrr | N
RP | Watts | 919ZQT | 1.5 | VUVU | 2006-06-01 | 2024-06-01 | N | 9 | (vv),xx,ooo,hhhh,pppp,rrrrr | N
RP | Watts | 919ZQT | 2 | VUVU | 2006-06-01 | 2024-06-01 | N | 9 | (vv),xx,ooo,hhhh,pppp,rrrrr | N
RP | Watts | 957 BF | 4 | H | 2008-01-17 | 2023-01-17 | Y | 9 | (yyy) | N |  |  | Check valve discs may be black EPDM or orange Silicone
RP | Watts | 957 BF | 6 | H | 2008-01-17 | 2023-01-17 | Y | 9 | (yyy) | N
RP | Watts | 957N | 2.5 | VUVD | 2003-04-14 | 2024-04-14 | N | 9 | (ppp),qqq,aaaa,bbbb,nnnnn | N |  |  | Check valve discs may be black EPDM or orange Silicone
RP | Watts | 957N | 2.5 | VUVD | 2003-04-14 | 2024-04-14 | Y | 9 | yyy,zzz,dddd,eeee,gggg,kkkk,llll,mmmm,nnnn | N |  |  | Check valve discs may be black EPDM or orange Silicone
RP | Watts | 957N | 2.5 | VUVU | 2021-07-26 | 2024-07-26 | N | 9 | (ppp),qqq,aaaa,bbbb,nnnnn | N |  |  | Check valve discs may be black EPDM or orange Silicone
RP | Watts | 957N | 2.5 | VUVU | 2021-07-26 | 2024-07-26 | Y | 9 | yyy,zzz,dddd,eeee,gggg,kkkk,llll,mmmm,nnnn | N |  |  | Check valve discs may be black EPDM or orange Silicone
RP | Watts | 957N | 3 | VUVD | 2003-04-14 | 2024-04-14 | N | 9 | (ppp),qqq,aaaa,bbbb,nnnnn | N |  |  | Check valve discs may be black EPDM or orange Silicone
RP | Watts | 957N | 3 | VUVD | 2003-04-14 | 2024-04-14 | Y | 9 | yyy,zzz,dddd,eeee,gggg,kkkk,llll,mmmm,nnnn | N |  |  | Check valve discs may be black EPDM or orange Silicone
RP | Watts | 957N | 3 | VUVU | 2021-07-26 | 2024-07-26 | N | 9 | (ppp),qqq,aaaa,bbbb,nnnnn | N |  |  | Check valve discs may be black EPDM or orange Silicone
RP | Watts | 957N | 3 | VUVU | 2021-07-26 | 2024-07-26 | Y | 9 | yyy,zzz,dddd,eeee,gggg,kkkk,llll,mmmm,nnnn | N |  |  | Check valve discs may be black EPDM or orange Silicone
RP | Watts | 957N | 4 | VUVD | 2003-04-14 | 2024-04-14 | N | 9 | (ppp),qqq,aaaa,bbbb,nnnnn | N |  |  | Check valve discs may be black EPDM or orange Silicone
RP | Watts | 957N | 4 | VUVD | 2003-04-14 | 2024-04-14 | Y | 9 | yyy,zzz,dddd,eeee,gggg,kkkk,llll,mmmm,nnnn | N |  |  | Check valve discs may be black EPDM or orange Silicone
RP | Watts | 957N | 4 | VUVU | 2021-07-26 | 2024-07-26 | N | 9 | (ppp),qqq,aaaa,bbbb,nnnnn | N |  |  | Check valve discs may be black EPDM or orange Silicone
RP | Watts | 957N | 4 | VUVU | 2021-07-26 | 2024-07-26 | Y | 9 | yyy,zzz,dddd,eeee,gggg,kkkk,llll,mmmm,nnnn | N |  |  | Check valve discs may be black EPDM or orange Silicone
RP | Watts | 957N | 6 | VUVD | 2010-11-15 | 2022-11-15 | N | 9 | ppp,qqq,aaaa,bbbb,nnnnn
RP | Watts | 957N | 6 | VUVD | 2010-11-15 | 2022-11-15 | Y | 9 | zzz,dddd,eeee,gggg,kkkk,llll,mmmm,nnnn
RP | Watts | 957N | 8 | VUVD | 2013-06-14 | 2022-06-14 | N | 9 | ppp, qqq, aaaa, bbbb,
RP | Watts | 957N | 8 | VUVD | 2013-06-14 | 2022-06-14 | Y | 9 | (yyy), zzz, dddd, eeee, gggg, kkkk, llll, mmmm, nnnn
RP | Watts | 957N | 8 | VUVU | 2021-07-26 | 2024-07-26 | N | 9 | ppp, qqq, aaaa, bbbb, | N
RP | Watts | 957N | 8 | VUVU | 2021-07-26 | 2024-07-26 | Y | 9 | (yyy), zzz, dddd, eeee, gggg, kkkk, llll, mmmm, nnnn | N
RP | Watts | 957NQT | 2.5 | VUVD | 2009-10-20 | 2024-10-20 | Y | 9 | (fffff) | N |  |  | Check valve discs may be black EPDM or orange Silicone
RP | Watts | 957NQT | 2.5 | VUVU | 2021-07-26 | 2024-07-26 | Y | 9 | (fffff) | N |  |  | Check valve discs may be black EPDM or orange Silicone
RP | Watts | 957NQT | 3 | VUVD | 2009-10-20 | 2024-10-20 | Y | 9 | (fffff) | N |  |  | Check valve discs may be black EPDM or orange Silicone
RP | Watts | 957NQT | 3 | VUVU | 2021-07-26 | 2024-07-26 | Y | 9 | (fffff) | N |  |  | Check valve discs may be black EPDM or orange Silicone
RP | Watts | 957NQT | 4 | VUVD | 2009-10-20 | 2024-10-20 | Y | 9 | (fffff) | N |  |  | Check valve discs may be black EPDM or orange Silicone
RP | Watts | 957NQT | 4 | VUVU | 2021-07-26 | 2024-07-26 | Y | 9 | (fffff) | N |  |  | Check valve discs may be black EPDM or orange Silicone
RP | Watts | 957QT | 2.5 | H | 2009-10-20 | 2024-10-20 | Y | 9 | (fffff) | N |  |  | Check valve discs may be black EPDM or orange Silicone
RP | Watts | 957QT | 3 | H | 2009-10-20 | 2024-10-20 | Y | 9 | (fffff) | N |  |  | Check valve discs may be black EPDM or orange Silicone
RP | Watts | 957QT | 4 | H | 2009-10-20 | 2024-10-20 | Y | 9 | (fffff) | N |  |  | Check valve discs may be black EPDM or orange Silicone
RP | Watts | 957Z | 2.5 | VUVD | 2021-07-26 | 2024-07-26 | N | 9 | (ppp),qqq,aaaa,bbbb,nnnnn | N |  |  | Check valve discs may be black EPDM or orange Silicone
RP | Watts | 957Z | 2.5 | VUVD | 2021-07-26 | 2024-07-26 | Y | 9 | yyy,zzz,dddd,eeee,gggg,kkkk,llll,mmmm,nnnn | N |  |  | Check valve discs may be black EPDM or orange Silicone
RP | Watts | 957Z | 2.5 | VUVU | 2003-04-14 | 2024-04-14 | N | 9 | (ppp),qqq,aaaa,bbbb,nnnnn | N |  |  | Check valve discs may be black EPDM or orange Silicone
RP | Watts | 957Z | 2.5 | VUVU | 2003-04-14 | 2024-04-14 | Y | 9 | yyy,zzz,dddd,eeee,gggg,kkkk,llll,mmmm,nnnn | N |  |  | Check valve discs may be black EPDM or orange Silicone
RP | Watts | 957Z | 3 | VUVD | 2021-07-26 | 2024-07-26 | N | 9 | (ppp),qqq,aaaa,bbbb,nnnnn | N |  |  | Check valve discs may be black EPDM or orange Silicone
RP | Watts | 957Z | 3 | VUVD | 2021-07-26 | 2024-07-26 | Y | 9 | yyy,zzz,dddd,eeee,gggg,kkkk,llll,mmmm,nnnn | N |  |  | Check valve discs may be black EPDM or orange Silicone
RP | Watts | 957Z | 3 | VUVU | 2003-04-14 | 2024-04-14 | N | 9 | (ppp),qqq,aaaa,bbbb,nnnnn | N |  |  | Check valve discs may be black EPDM or orange Silicone
RP | Watts | 957Z | 3 | VUVU | 2003-04-14 | 2024-04-14 | Y | 9 | yyy,zzz,dddd,eeee,gggg,kkkk,llll,mmmm,nnnn | N |  |  | Check valve discs may be black EPDM or orange Silicone
RP | Watts | 957Z | 4 | VUVD | 2021-07-26 | 2024-07-26 | N | 9 | (ppp),qqq,aaaa,bbbb,nnnnn | N |  |  | Check valve discs may be black EPDM or orange Silicone
RP | Watts | 957Z | 4 | VUVD | 2021-07-26 | 2024-07-26 | Y | 9 | yyy,zzz,dddd,eeee,gggg,kkkk,llll,mmmm,nnnn | N |  |  | Check valve discs may be black EPDM or orange Silicone
RP | Watts | 957Z | 4 | VUVU | 2003-04-14 | 2024-04-14 | N | 9 | (ppp),qqq,aaaa,bbbb,nnnnn | N |  |  | Check valve discs may be black EPDM or orange Silicone
RP | Watts | 957Z | 4 | VUVU | 2003-04-14 | 2024-04-14 | Y | 9 | yyy,zzz,dddd,eeee,gggg,kkkk,llll,mmmm,nnnn | N |  |  | Check valve discs may be black EPDM or orange Silicone
RP | Watts | 957Z | 8 | VUVD | 2021-07-26 | 2024-07-26 | N | 9 | ppp, qqq, aaaa, bbbb, | N
RP | Watts | 957Z | 8 | VUVD | 2021-07-26 | 2024-07-26 | Y | 9 | (yyy), zzz, dddd, eeee, gggg, kkkk, llll, mmmm, nnnn | N
RP | Watts | 957Z | 8 | VUVU | 2013-06-14 | 2022-06-14 | N | 9 | ppp, qqq, aaaa, bbbb,
RP | Watts | 957Z | 8 | VUVU | 2013-06-14 | 2022-06-14 | Y | 9 | (yyy), zzz, dddd, eeee, gggg, kkkk, llll, mmmm, nnnn
RP | Watts | 957ZQT | 2.5 | VUVD | 2021-07-26 | 2024-07-26 | Y | 9 | (fffff) | N |  |  | Check valve discs may be black EPDM or orange Silicone
RP | Watts | 957ZQT | 2.5 | VUVU | 2009-10-20 | 2024-10-20 | Y | 9 | (fffff) | N |  |  | Check valve discs may be black EPDM or orange Silicone
RP | Watts | 957ZQT | 3 | VUVD | 2021-07-26 | 2024-07-26 | Y | 9 | (fffff) | N |  |  | Check valve discs may be black EPDM or orange Silicone
RP | Watts | 957ZQT | 3 | VUVU | 2009-10-20 | 2024-10-20 | Y | 9 | (fffff) | N |  |  | Check valve discs may be black EPDM or orange Silicone
RP | Watts | 957ZQT | 4 | VUVD | 2021-07-26 | 2024-07-26 | Y | 9 | (fffff) | N |  |  | Check valve discs may be black EPDM or orange Silicone
RP | Watts | 957ZQT | 4 | VUVU | 2009-10-20 | 2024-10-20 | Y | 9 | (fffff) | N |  |  | Check valve discs may be black EPDM or orange Silicone
RP | Watts | 967N | 2.5 | VUVD | 2003-04-14 | 2024-04-14 | N | 9 | (ppp),qqq,yyy,zzz,aaaa,bbbb,dddd,eeee,gggg,kkkk,llll,mmmm,nnnn,nnnnn | N
RP | Watts | 967N | 2.5 | VUVU | 2021-07-26 | 2024-07-26 | N | 9 | (ppp),qqq,yyy,zzz,aaaa,bbbb,dddd,eeee,gggg,kkkk,llll,mmmm,nnnn,nnnnn | N
RP | Watts | 967N | 3 | VUVD | 2003-04-14 | 2024-04-14 | N | 9 | (ppp),qqq,zzz,aaaa,bbbb,dddd,eeee,ffff,gggg,kkkk,llll,mmmm,nnnn,nnnnn | N
RP | Watts | 967N | 3 | VUVU | 2021-07-26 | 2024-07-26 | N | 9 | (ppp),qqq,zzz,aaaa,bbbb,dddd,eeee,ffff,gggg,kkkk,llll,mmmm,nnnn,nnnnn | N
RP | Watts | 967N | 4 | VUVD | 2010-11-15 | 2022-11-15 | N | 9 | ppp,qqq,aaaa,bbbb,nnnnn
RP | Watts | 967N | 4 | VUVD | 2010-11-15 | 2022-11-15 | Y | 9 | yyy,zzz,dddd,eeee,gggg,kkkk,llll,mmmm,nnnn
RP | Watts | 967N | 4 | VUVU | 2021-07-26 | 2024-07-26 | N | 9 | ppp,qqq,aaaa,bbbb,nnnnn | N
RP | Watts | 967N | 4 | VUVU | 2021-07-26 | 2024-07-26 | Y | 9 | yyy,zzz,dddd,eeee,gggg,kkkk,llll,mmmm,nnnn | N
RP | Watts | 967N | 6 | VUVD | 2013-06-14 | 2022-06-14 | N | 9 | ppp, qqq, aaaa, bbbb,
RP | Watts | 967N | 6 | VUVD | 2013-06-14 | 2022-06-14 | Y | 9 | (yyy), zzz, dddd, eeee, gggg, kkkk, llll, mmmm, nnnn
RP | Watts | 967N | 6 | VUVU | 2021-07-26 | 2024-07-26 | N | 9 | ppp, qqq, aaaa, bbbb, | N
RP | Watts | 967N | 6 | VUVU | 2021-07-26 | 2024-07-26 | Y | 9 | (yyy), zzz, dddd, eeee, gggg, kkkk, llll, mmmm, nnnn | N
RP | Watts | 967Z | 2.5 | VUVD | 2021-07-26 | 2024-07-26 | N | 9 | (ppp),qqq,yyy,zzz,aaaa,bbbb,dddd,eeee,gggg,kkkk,llll,mmmm,nnnn,nnnnn | N
RP | Watts | 967Z | 2.5 | VUVU | 2003-04-14 | 2024-04-14 | N | 9 | (ppp),qqq,yyy,zzz,aaaa,bbbb,dddd,eeee,gggg,kkkk,llll,mmmm,nnnn,nnnnn | N
RP | Watts | 967Z | 3 | VUVD | 2021-07-26 | 2024-07-26 | N | 9 | (ppp),qqq,zzz,aaaa,bbbb,dddd,eeee,gggg,kkkk,llll,mmmm,nnnn,nnnnn | N
RP | Watts | 967Z | 3 | VUVU | 2003-04-14 | 2024-04-14 | N | 9 | (ppp),qqq,zzz,aaaa,bbbb,dddd,eeee,gggg,kkkk,llll,mmmm,nnnn,nnnnn | N
RP | Watts | 967Z | 6 | VUVD | 2021-07-26 | 2024-07-26 | N | 9 | ppp, qqq, aaaa, bbbb, | N
RP | Watts | 967Z | 6 | VUVD | 2021-07-26 | 2024-07-26 | Y | 9 | (yyy), zzz, dddd, eeee, gggg, kkkk, llll, mmmm, nnnn | N
RP | Watts | 967Z | 6 | VUVU | 2013-06-14 | 2022-06-14 | N | 9 | ppp, qqq, aaaa, bbbb,
RP | Watts | 967Z | 6 | VUVU | 2013-06-14 | 2022-06-14 | Y | 9 | (yyy), zzz, dddd, eeee, gggg, kkkk, llll, mmmm, nnnn
RP | Watts | 990QTFDA | 4 | H | 1993-01-13 | 2023-01-13 | N | 8 | ww | Y
RP | Watts | 990QTFDA | 8 | H | 1993-01-13 | 2023-01-13 | N | 8 | ww | Y
RP | Watts | 995QT | 0.5 | H | 2000-04-13 | 2024-04-13 | N | 9 | int | Y
RP | Watts | 995QT | 0.75 | H | 2000-04-13 | 2024-04-13 | N | 9 | int | Y
RP | Watts | 995QT | 1 | H | 1999-01-14 | 2023-01-14 | N | 9 | int | Y
RP | Watts | 995QT | 1.25 | H | 2002-03-28 | 2023-03-28 | N | 9 | int | Y
RP | Watts | 995QT | 1.5 | H | 2002-03-28 | 2023-03-28 | N | 9 | int | Y
RP | Watts | FAE909HWQT | 1.25 | H | 1980-02-07 | 2022-02-07 | N | 5 | (vv),xx,ooo,hhhh,pppp | Y
RP | Watts | FAE909HWQT | 1.5 | H | 1980-02-07 | 2022-02-07 | N | 5 | (vv),xx,ooo,hhhh,pppp | Y
RP | Watts | FAE909HWQT | 2 | H | 1980-02-07 | 2022-02-07 | N | 5 | (vv),xx,ooo,hhhh,pppp | Y
RP | Watts | FAE909QT | 1.25 | H | 1982-01-15 | 2024-01-15 | N | 6 | (vv),xx,ooo,hhhh,pppp | Y
RP | Watts | FAE909QT | 1.5 | H | 1982-01-15 | 2024-01-15 | N | 6 | (vv),xx,ooo,hhhh,pppp | Y
RP | Watts | FAE909QT | 2 | H | 1982-01-15 | 2024-01-15 | N | 6 | (vv),xx,ooo,hhhh,pppp | Y
RP | Watts | LF009 | 2.5 | H | 2010-01-12 | 2022-01-12 | Y | 9 | (oo),ll,mm | N
RP | Watts | LF009 | 3 | H | 2010-01-12 | 2022-01-12 | Y | 9 | (oo),ll,mm | N
RP | Watts | LF009IOTQT | 0.5 | H | 2021-02-25 | 2024-02-25 | Y | 9 | (hhhh),rrrrr | N
RP | Watts | LF009M2IOTQT | 1 | H | 2021-02-25 | 2024-02-25 | Y | 9 | (hhhh),rrrrr | N
RP | Watts | LF009M2IOTQT | 2 | H | 2021-02-25 | 2024-02-25 | Y | 9 | (hhhh),rrrrr | N
RP | Watts | LF009M2PCQT | 1 | H | 2015-03-13 | 2024-03-13 | Y | 9 | (hhhh),rrrrr | N
RP | Watts | LF009M2PCQT | 2 | H | 2015-03-13 | 2024-03-13 | Y | 9 | (hhhh),rrrrr | N
RP | Watts | LF009M2QT | 1 | H | 2008-01-11 | 2023-01-11 | Y | 9 | (hhhh),rrrrr | N
RP | Watts | LF009M2QT | 1.25 | H | 2008-01-11 | 2023-01-11 | Y | 8 | (hhhh),rrrrr | N
RP | Watts | LF009M2QT | 1.5 | H | 2008-01-11 | 2023-01-11 | Y | 8 | (hhhh),rrrrr | N
RP | Watts | LF009M2QT | 2 | H | 2008-01-11 | 2023-01-11 | Y | 9 | (hhhh),rrrrr | N
RP | Watts | LF009M3IOTQT | 0.75 | H | 2021-02-25 | 2024-02-25 | Y | 9 | (hhhh),rrrrr | N
RP | Watts | LF009M3PCQT | 0.75 | H | 2015-03-13 | 2024-03-13 | Y | 9 | (hhhh),rrrrr | N
RP | Watts | LF009M3QT | 0.75 | H | 2008-01-11 | 2023-01-11 | Y | 9 | (hhhh),rrrrr | N
RP | Watts | LF009PCQT | 0.5 | H | 2015-03-13 | 2024-03-13 | Y | 9 | (hhhh),rrrrr | N
RP | Watts | LF009QT | 0.5 | H | 2008-01-11 | 2023-01-11 | Y | 9 | (hhhh),rrrrr | N
RP | Watts | LF909 | 2.5 | H | 2010-01-12 | 2022-01-12 | Y | 9 | (ll),mm,oo,pp,zzz,cccc,dddd,eeee,ffff,gggg,nnnnn,zzzzzz,aaaaaaa | N
RP | Watts | LF909 | 3 | H | 2010-01-12 | 2022-01-12 | Y | 9 | (ll),mm,oo,pp,zzz,cccc,dddd,eeee,ffff,gggg,nnnnn,zzzzzz,aaaaaaa | N
RP | Watts | LF909 | 4 | H | 2012-07-27 | 2024-07-27 | Y | 9 | (ll),mm,oo,pp,zzz,cccc,dddd,eeee,ffff,gggg,nnnnn,zzzzzz,aaaaaaa | N
RP | Watts | LF909 | 6 | H | 2012-07-27 | 2024-07-27 | Y | 9 | (ll),mm,oo,pp,zzz,cccc,dddd,eeee,ffff,gggg,nnnnn,zzzzzz,aaaaaaa | N
RP | Watts | LF909M1 | 8 | H | 2010-07-01 | 2022-07-01 | Y | 9 | (ll),mm,oo,pp,zzz,cccc,dddd,eeee,ffff,gggg,nnnnn,zzzzzz,aaaaaaa | N
RP | Watts | LF909M1 | 10 | H | 2010-07-01 | 2022-07-01 | Y | 9 | (ll),mm,oo,pp,zzz,cccc,dddd,eeee,ffff,gggg,nnnnn | N
RP | Watts | LF909M1PCQT | 1.25 | H | 2015-03-13 | 2024-03-13 | N | 9 | (hhhh),rrrrr | N
RP | Watts | LF909M1PCQT | 1.5 | H | 2015-03-13 | 2024-03-13 | N | 9 | (hhhh),rrrrr | N
RP | Watts | LF909M1PCQT | 2 | H | 2015-03-13 | 2024-03-13 | N | 9 | (hhhh),rrrrr | N
RP | Watts | LF909M1QT | 1.25 | H | 2010-02-18 | 2022-02-18 | Y | 9 | (hhhh),rrrrr | N
RP | Watts | LF909M1QT | 1.5 | H | 2010-02-18 | 2022-02-18 | Y | 9 | (hhhh),rrrrr | N
RP | Watts | LF909M1QT | 2 | H | 2010-02-18 | 2022-02-18 | Y | 9 | (hhhh),rrrrr | N
RP | Watts | LF909PCQT | 0.75 | H | 2015-03-13 | 2024-03-13 | N | 9 | (hhhh),rrrrr | N
RP | Watts | LF909PCQT | 0.75 | VU | 2015-03-13 | 2024-03-13 | N | 9 | (hhhh),rrrrr | N
RP | Watts | LF909PCQT | 1 | H | 2015-03-13 | 2024-03-13 | N | 9 | (hhhh),rrrrr | N
RP | Watts | LF909PCQT | 1 | VU | 2015-03-13 | 2024-03-13 | N | 9 | (hhhh),rrrrr | N
RP | Watts | LF909QT | 0.75 | H | 2010-02-18 | 2022-02-18 | Y | 9 | (hhhh),rrrrr | N
RP | Watts | LF909QT | 0.75 | VU | 2010-11-15 | 2022-11-15 | Y | 9 | (hhhh),rrrrr
RP | Watts | LF909QT | 1 | H | 2010-02-18 | 2022-02-18 | Y | 9 | (hhhh),rrrrr | N
RP | Watts | LF909QT | 1 | VU | 2010-11-15 | 2022-11-15 | Y | 9 | (hhhh),rrrrr
RP | Watts | LF919AQT | 0.75 | VUVD | 2006-06-14 | 2024-06-14 | N | 9 | (vv),xx,ooo,pppp,rrrrr | Y
RP | Watts | LF919AQT | 0.75 | VUVD | 2006-06-14 | 2024-06-14 | Y | 9 | (hhhh),rrrrr | Y
RP | Watts | LF919AQT | 1 | VUVD | 2006-04-12 | 2024-04-12 | N | 9 | (vv),xx,ooo,pppp,rrrrr | N
RP | Watts | LF919AQT | 1 | VUVD | 2006-04-12 | 2024-04-12 | Y | 9 | (hhhh),rrrrr | N
RP | Watts | LF919AQT | 1.25 | VUVD | 2006-09-05 | 2024-09-05 | N | 9 | (vv),xx,ooo,pppp,rrrrr | N
RP | Watts | LF919AQT | 1.25 | VUVD | 2006-09-05 | 2024-09-05 | Y | 9 | (hhhh),rrrrr | N
RP | Watts | LF919AQT | 1.5 | VUVD | 2006-04-12 | 2024-04-12 | N | 9 | (vv),xx,ooo,pppp,rrrrr | N
RP | Watts | LF919AQT | 1.5 | VUVD | 2006-04-12 | 2024-04-12 | Y | 9 | (hhhh),rrrrr | N
RP | Watts | LF919AQT | 2 | VUVD | 2006-04-12 | 2024-04-12 | N | 9 | (vv),xx,ooo,pppp,rrrrr | N
RP | Watts | LF919AQT | 2 | VUVD | 2006-04-12 | 2024-04-12 | Y | 9 | (hhhh),rrrrr | N
RP | Watts | LF919QT | 0.75 | H | 2006-06-14 | 2024-06-14 | N | 9 | (vv),xx,ooo,pppp,rrrrr | N
RP | Watts | LF919QT | 0.75 | H | 2006-06-14 | 2024-06-14 | Y | 9 | (hhhh),rrrrr | N
RP | Watts | LF919QT | 0.75 | VD | 2006-08-30 | 2024-08-30 | N | 9 | (vv),xx,ooo,pppp,rrrrr | N
RP | Watts | LF919QT | 0.75 | VD | 2006-08-30 | 2024-08-30 | Y | 9 | (hhhh),rrrrr | N
RP | Watts | LF919QT | 1 | H | 2006-04-12 | 2024-04-12 | N | 9 | (vv),xx,ooo,pppp,rrrrr | N
RP | Watts | LF919QT | 1 | H | 2006-04-12 | 2024-04-12 | Y | 9 | (hhhh),rrrrr | N
RP | Watts | LF919QT | 1 | VD | 2006-08-30 | 2024-08-30 | N | 9 | (vv),xx,ooo,pppp,rrrrr | N
RP | Watts | LF919QT | 1 | VD | 2006-08-30 | 2024-08-30 | Y | 9 | (hhhh),rrrrr | N
RP | Watts | LF919QT | 1.25 | H | 2006-04-12 | 2024-04-12 | N | 9 | (vv),xx,ooo,pppp,rrrrr | N
RP | Watts | LF919QT | 1.25 | H | 2006-04-12 | 2024-04-12 | Y | 9 | (hhhh),rrrrr | N
RP | Watts | LF919QT | 1.25 | VD | 2006-08-30 | 2024-08-30 | N | 9 | (vv),xx,ooo,pppp,rrrrr | N
RP | Watts | LF919QT | 1.25 | VD | 2006-08-30 | 2024-08-30 | Y | 9 | (hhhh),rrrrr | N
RP | Watts | LF919QT | 1.5 | H | 2006-04-12 | 2024-04-12 | N | 9 | (vv),xx,ooo,pppp,rrrrr | N
RP | Watts | LF919QT | 1.5 | H | 2006-04-12 | 2024-04-12 | Y | 9 | (hhhh),rrrrr | N
RP | Watts | LF919QT | 1.5 | VD | 2006-08-30 | 2024-08-30 | N | 9 | (vv),xx,ooo,pppp,rrrrr | N
RP | Watts | LF919QT | 1.5 | VD | 2006-08-30 | 2024-08-30 | Y | 9 | (hhhh),rrrrr | N
RP | Watts | LF919QT | 2 | H | 2006-04-12 | 2024-04-12 | N | 9 | (vv),xx,ooo,pppp,rrrrr | N
RP | Watts | LF919QT | 2 | H | 2006-04-12 | 2024-04-12 | Y | 9 | (hhhh),rrrrr | N
RP | Watts | LF919QT | 2 | VD | 2006-08-30 | 2024-08-30 | N | 9 | (vv),xx,ooo,pppp,rrrrr | N
RP | Watts | LF919QT | 2 | VD | 2006-08-30 | 2024-08-30 | Y | 9 | (hhhh),rrrrr | N
RP | Watts | LF919ZQT | 0.75 | VUVU | 2006-06-14 | 2024-06-14 | N | 9 | (vv),xx,ooo,hhhh,pppp,rrrrr | Y
RP | Watts | LF919ZQT | 1 | VUVU | 2006-04-12 | 2024-04-12 | N | 9 | (vv),xx,ooo,hhhh,pppp,rrrrr | N
RP | Watts | LF919ZQT | 1.25 | VUVU | 2006-04-12 | 2024-04-12 | N | 9 | (vv),xx,ooo,hhhh,pppp,rrrrr | N
RP | Watts | LF919ZQT | 1.5 | VUVU | 2006-04-12 | 2024-04-12 | N | 9 | (vv),xx,ooo,hhhh,pppp,rrrrr | N
RP | Watts | LF919ZQT | 2 | VUVU | 2006-04-12 | 2024-04-12 | N | 9 | (vv),xx,ooo,hhhh,pppp,rrrrr | N
RP | Watts | LFU919AQT | 0.75 | VUVD | 2006-06-14 | 2024-06-14 | N | 9 | (vv),xx,ooo,pppp | Y
RP | Watts | LFU919AQT | 0.75 | VUVD | 2006-06-14 | 2024-06-14 | Y | 9 | hhhh | Y
RP | Watts | LFU919AQT | 1 | VUVD | 2006-04-12 | 2024-04-12 | N | 9 | (vv),xx,ooo,pppp | N
RP | Watts | LFU919AQT | 1 | VUVD | 2006-04-12 | 2024-04-12 | Y | 9 | hhhh | N
RP | Watts | LFU919AQT | 1.25 | VUVD | 2006-04-12 | 2024-04-12 | N | 9 | (vv),xx,ooo,pppp | N
RP | Watts | LFU919AQT | 1.25 | VUVD | 2006-04-12 | 2024-04-12 | Y | 9 | hhhh | N
RP | Watts | LFU919AQT | 1.5 | VUVD | 2006-04-12 | 2024-04-12 | N | 9 | (vv),xx,ooo,pppp | N
RP | Watts | LFU919AQT | 1.5 | VUVD | 2006-04-12 | 2024-04-12 | Y | 9 | hhhh | N
RP | Watts | LFU919AQT | 2 | VUVD | 2006-04-12 | 2024-04-12 | N | 9 | (vv),xx,ooo,pppp | N
RP | Watts | LFU919AQT | 2 | VUVD | 2006-04-12 | 2024-04-12 | Y | 9 | hhhh | N
RP | Watts | LFU919QT | 1 | H | 2006-04-12 | 2024-04-12 | N | 9 | (vv),xx,ooo,pppp | N
RP | Watts | LFU919QT | 1 | H | 2006-04-12 | 2024-04-12 | Y | 9 | hhhh | N
RP | Watts | LFU919QT | 1 | VD | 2006-08-30 | 2024-08-30 | N | 9 | (vv),xx,ooo,pppp | N
RP | Watts | LFU919QT | 1 | VD | 2006-08-30 | 2024-08-30 | Y | 9 | hhhh | N
RP | Watts | LFU919QT | 1.25 | H | 2006-04-12 | 2024-04-12 | N | 9 | (vv),xx,ooo,pppp | N
RP | Watts | LFU919QT | 1.25 | H | 2006-04-12 | 2024-04-12 | Y | 9 | hhhh | N
RP | Watts | LFU919QT | 1.25 | VD | 2006-08-30 | 2024-08-30 | N | 9 | (vv),xx,ooo,pppp | N
RP | Watts | LFU919QT | 1.25 | VD | 2006-08-30 | 2024-08-30 | Y | 9 | hhhh | N
RP | Watts | LFU919QT | 1.5 | H | 2006-04-12 | 2024-04-12 | N | 9 | (vv),xx,ooo,pppp | N
RP | Watts | LFU919QT | 1.5 | H | 2006-04-12 | 2024-04-12 | Y | 9 | hhhh | N
RP | Watts | LFU919QT | 1.5 | VD | 2006-08-30 | 2024-08-30 | N | 9 | (vv),xx,ooo,pppp | N
RP | Watts | LFU919QT | 1.5 | VD | 2006-08-30 | 2024-08-30 | Y | 9 | hhhh | N
RP | Watts | LFU919QT | 2 | H | 2006-04-12 | 2024-04-12 | N | 9 | (vv),xx,ooo,pppp | N
RP | Watts | LFU919QT | 2 | H | 2006-04-12 | 2024-04-12 | Y | 9 | hhhh | N
RP | Watts | LFU919QT | 2 | VD | 2006-08-30 | 2024-08-30 | N | 9 | (vv),xx,ooo,pppp | N
RP | Watts | LFU919QT | 2 | VD | 2006-08-30 | 2024-08-30 | Y | 9 | hhhh | N
RP | Watts | Magnum 40 | 2.5 | H | 2020-05-15 | 2023-05-15 | Y | 10 | (int) | N
RP | Watts | Magnum 40 | 3 | H | 2020-05-15 | 2023-05-15 | Y | 10 | (int) | N
RP | Watts | Magnum 40 | 4 | H | 2020-05-15 | 2023-05-15 | Y | 10 | (int) | N
RP | Watts | Magnum 40 | 8 | H | 2020-05-15 | 2023-05-15 | Y | 10 | (int) | N
RP | Watts | Magnum 40G | 2.5 | H | 2020-05-15 | 2023-05-15 | Y | 10 | (qqqqqq), rrrrrr | N
RP | Watts | Magnum 40G | 3 | H | 2020-05-15 | 2023-05-15 | Y | 10 | (qqqqqq), rrrrrr | N
RP | Watts | Magnum 40G | 4 | H | 2020-05-15 | 2023-05-15 | Y | 10 | (qqqqqq), rrrrrr | N
RP | Watts | Magnum 40G | 8 | H | 2020-05-15 | 2023-05-15 | Y | 10 | (qqqqqq), rrrrrr | N
RP | Watts | Magnum 40GX | 6 | H | 2020-05-15 | 2023-05-15 | Y | 10 | (qqqqqq), rrrrrr | N
RP | Watts | Magnum 40X | 6 | H | 2020-05-15 | 2023-05-15 | Y | 10 | (int) | N
RP | Watts | SS009M3QT | 0.25 | H | 2001-12-19 | 2022-12-19 | Y | 9 | (hhh) | N
RP | Watts | SS009M3QT | 0.375 | H | 2001-12-19 | 2022-12-19 | Y | 9 | (hhh) | N
RP | Watts | SS009M3QT | 0.5 | H | 2001-12-19 | 2022-12-19 | Y | 9 | (hhh) | N
RP | Watts | SS009M3QT | 0.75 | H | 2001-07-31 | 2022-07-31 | Y | 9 | (hhh) | N
RP | Watts | SS009QT | 1 | H | 1998-05-18 | 2022-05-18 | N | 9 | (hhh) | N
RP | Watts | U009APCQT | 0.75 | VDVD | 1993-12-10 | 2023-12-10 | N | 8 | (vv),xx,ooo,hhhh,pppp | N
RP | Watts | U009APCQT | 0.75 | VDVU | 1993-12-10 | 2023-12-10 | N | 8 | (vv),xx,ooo,hhhh,pppp | N
RP | Watts | U009APCQT | 0.75 | VUVD | 1993-12-10 | 2023-12-10 | N | 8 | (vv),xx,ooo,hhhh,pppp | N
RP | Watts | U009APCQT | 0.75 | VUVU | 1993-12-10 | 2023-12-10 | N | 8 | (vv),xx,ooo,hhhh,pppp | N
RP | Watts | U009APCQT | 1 | VDVD | 1993-12-10 | 2023-12-10 | N | 8 | vv,xx,ooo,hhhh,pppp | Y
RP | Watts | U009APCQT | 1 | VDVU | 1993-12-10 | 2023-12-10 | N | 8 | vv,xx,ooo,hhhh,pppp | Y
RP | Watts | U009APCQT | 1 | VUVD | 1993-12-10 | 2023-12-10 | N | 8 | vv,xx,ooo,hhhh,pppp | Y
RP | Watts | U009APCQT | 1 | VUVU | 1993-12-10 | 2023-12-10 | N | 8 | vv,xx,ooo,hhhh,pppp | Y
RP | Watts | U009AQT | 0.75 | VDVD | 1992-06-12 | 2022-06-12 | N | 8 | (vv),xx,ooo,hhhh,pppp | N
RP | Watts | U009AQT | 0.75 | VDVU | 1992-06-12 | 2022-06-12 | N | 8 | (vv),xx,ooo,hhhh,pppp | N
RP | Watts | U009AQT | 0.75 | VUVD | 1992-06-12 | 2022-06-12 | N | 8 | (vv),xx,ooo,hhhh,pppp | N
RP | Watts | U009AQT | 0.75 | VUVU | 1992-06-12 | 2022-06-12 | N | 8 | (vv),xx,ooo,hhhh,pppp | N
RP | Watts | U009AQT | 1 | VDVD | 1992-06-12 | 2022-06-12 | N | 8 | vv,xx,ooo,hhhh,pppp | Y
RP | Watts | U009AQT | 1 | VDVU | 1992-06-12 | 2022-06-12 | N | 8 | vv,xx,ooo,hhhh,pppp | Y
RP | Watts | U009AQT | 1 | VUVD | 1992-06-12 | 2022-06-12 | N | 8 | vv,xx,ooo,hhhh,pppp | Y
RP | Watts | U009AQT | 1 | VUVU | 1992-06-12 | 2022-06-12 | N | 8 | vv,xx,ooo,hhhh,pppp | Y
RP | Watts | U009M1APCQT | 1.5 | VDVD | 1994-09-27 | 2024-09-27 | N | 8 | vv,xx,ooo,hhhh,pppp | Y
RP | Watts | U009M1APCQT | 1.5 | VDVU | 1994-09-27 | 2024-09-27 | N | 8 | vv,xx,ooo,hhhh,pppp | Y
RP | Watts | U009M1APCQT | 1.5 | VUVD | 1994-09-27 | 2024-09-27 | N | 8 | vv,xx,ooo,hhhh,pppp | Y
RP | Watts | U009M1APCQT | 1.5 | VUVU | 1994-09-27 | 2024-09-27 | N | 8 | vv,xx,ooo,hhhh,pppp | Y
RP | Watts | U009M1APCQT | 2 | VDVD | 1994-09-27 | 2024-09-27 | N | 8 | vv,xx,ooo,hhhh,pppp | Y
RP | Watts | U009M1APCQT | 2 | VDVU | 1994-09-27 | 2024-09-27 | N | 8 | vv,xx,ooo,hhhh,pppp | Y
RP | Watts | U009M1APCQT | 2 | VUVD | 1994-09-27 | 2024-09-27 | N | 8 | vv,xx,ooo,hhhh,pppp | Y
RP | Watts | U009M1APCQT | 2 | VUVU | 1994-09-27 | 2024-09-27 | N | 8 | vv,xx,ooo,hhhh,pppp | Y
RP | Watts | U009M1AQT | 1.5 | VDVD | 1992-12-16 | 2022-12-16 | N | 8 | vv,xx,ooo,hhhh,pppp | Y
RP | Watts | U009M1AQT | 1.5 | VDVU | 1992-12-16 | 2022-12-16 | N | 8 | vv,xx,ooo,hhhh,pppp | Y
RP | Watts | U009M1AQT | 1.5 | VUVD | 1992-12-16 | 2022-12-16 | N | 8 | vv,xx,ooo,hhhh,pppp | Y
RP | Watts | U009M1AQT | 1.5 | VUVU | 1992-12-16 | 2022-12-16 | N | 8 | vv,xx,ooo,hhhh,pppp | Y
RP | Watts | U009M1AQT | 2 | VDVD | 1992-11-09 | 2022-11-09 | N | 8 | vv,xx,ooo,hhhh,pppp | Y
RP | Watts | U009M1AQT | 2 | VDVU | 1992-11-09 | 2022-11-09 | N | 8 | vv,xx,ooo,hhhh,pppp | Y
RP | Watts | U009M1AQT | 2 | VUVD | 1992-11-09 | 2022-11-09 | N | 8 | vv,xx,ooo,hhhh,pppp | Y
RP | Watts | U009M1AQT | 2 | VUVU | 1992-11-09 | 2022-11-09 | N | 8 | vv,xx,ooo,hhhh,pppp | Y
RP | Watts | U009M1PCQT | 1.25 | H | 1994-09-27 | 2024-09-27 | N | 8 | (vv),xx,ooo,hhhh,pppp | N
RP | Watts | U009M1PCQT | 1.5 | H | 1994-09-27 | 2024-09-27 | N | 8 | (vv),xx,ooo,hhhh,pppp | N
RP | Watts | U009M1PCQT | 2 | H | 1994-09-27 | 2024-09-27 | N | 8 | (vv),xx,ooo,hhhh,pppp | N
RP | Watts | U009M1QT | 1.25 | H | 1992-06-30 | 2022-06-30 | N | 8 | (vv),xx,ooo,hhhh,pppp | N
RP | Watts | U009M1QT | 1.5 | H | 1992-06-30 | 2022-06-30 | N | 8 | vv,xx,ooo,hhhh,pppp | Y
RP | Watts | U009M1QT | 2 | H | 1992-06-30 | 2022-06-30 | N | 8 | vv,xx,ooo,hhhh,pppp | Y
RP | Watts | U009M2APCQT | 1 | VDVD | 1999-01-15 | 2023-01-15 | N | 9 | (vv),xx,ooo,hhhh,pppp | N
RP | Watts | U009M2APCQT | 1 | VDVU | 1999-01-15 | 2023-01-15 | N | 9 | (vv),xx,ooo,hhhh,pppp | N
RP | Watts | U009M2APCQT | 1 | VUVD | 1999-01-15 | 2023-01-15 | N | 9 | (vv),xx,ooo,hhhh,pppp | N
RP | Watts | U009M2APCQT | 1 | VUVU | 1999-01-15 | 2023-01-15 | N | 9 | (vv),xx,ooo,hhhh,pppp | N
RP | Watts | U009M2APCQT | 1.5 | VDVD | 1994-09-12 | 2024-09-12 | N | 8 | (vv),xx,ooo,hhhh,pppp | N
RP | Watts | U009M2APCQT | 1.5 | VDVU | 1994-09-12 | 2024-09-12 | N | 8 | (vv),xx,ooo,hhhh,pppp | N
RP | Watts | U009M2APCQT | 1.5 | VUVD | 1994-09-12 | 2024-09-12 | N | 8 | (vv),xx,ooo,hhhh,pppp | N
RP | Watts | U009M2APCQT | 1.5 | VUVU | 1994-09-12 | 2024-09-12 | N | 8 | (vv),xx,ooo,hhhh,pppp | N
RP | Watts | U009M2APCQT | 2 | VDVD | 1997-08-26 | 2024-08-26 | N | 9 | (vv),xx,ooo,hhhh,pppp | N
RP | Watts | U009M2APCQT | 2 | VDVU | 1997-08-26 | 2024-08-26 | N | 9 | (vv),xx,ooo,hhhh,pppp | N
RP | Watts | U009M2APCQT | 2 | VUVD | 1997-08-26 | 2024-08-26 | N | 9 | (vv),xx,ooo,hhhh,pppp | N
RP | Watts | U009M2APCQT | 2 | VUVU | 1997-08-26 | 2024-08-26 | N | 9 | (vv),xx,ooo,hhhh,pppp | N
RP | Watts | U009M2AQT | 1 | VDVD | 1999-01-15 | 2023-01-15 | N | 9 | (vv),xx,ooo,hhhh,pppp | N
RP | Watts | U009M2AQT | 1 | VDVU | 1999-01-15 | 2023-01-15 | N | 9 | (vv),xx,ooo,hhhh,pppp | N
RP | Watts | U009M2AQT | 1 | VUVD | 1999-01-15 | 2023-01-15 | N | 9 | (vv),xx,ooo,hhhh,pppp | N
RP | Watts | U009M2AQT | 1 | VUVU | 1999-01-15 | 2023-01-15 | N | 9 | (vv),xx,ooo,hhhh,pppp | N
RP | Watts | U009M2AQT | 1.5 | VDVD | 1993-08-24 | 2023-08-24 | N | 8 | (vv),xx,ooo,hhhh,pppp | N
RP | Watts | U009M2AQT | 1.5 | VDVU | 1993-08-24 | 2023-08-24 | N | 8 | (vv),xx,ooo,hhhh,pppp | N
RP | Watts | U009M2AQT | 1.5 | VUVD | 1993-08-24 | 2023-08-24 | N | 8 | (vv),xx,ooo,hhhh,pppp | N
RP | Watts | U009M2AQT | 1.5 | VUVU | 1993-08-24 | 2023-08-24 | N | 8 | (vv),xx,ooo,hhhh,pppp | N
RP | Watts | U009M2AQT | 2 | VDVD | 1997-08-26 | 2024-08-26 | N | 9 | (vv),xx,ooo,hhhh,pppp | N
RP | Watts | U009M2AQT | 2 | VDVU | 1997-08-26 | 2024-08-26 | N | 9 | (vv),xx,ooo,hhhh,pppp | N
RP | Watts | U009M2AQT | 2 | VUVD | 1997-08-26 | 2024-08-26 | N | 9 | (vv),xx,ooo,hhhh,pppp | N
RP | Watts | U009M2AQT | 2 | VUVU | 1997-08-26 | 2024-08-26 | N | 9 | (vv),xx,ooo,hhhh,pppp | N
RP | Watts | U009M2PCQT | 1 | H | 1999-01-15 | 2023-01-15 | N | 9 | (vv),xx,ooo,hhhh,pppp | N
RP | Watts | U009M2PCQT | 1.5 | H | 1994-09-12 | 2024-09-12 | N | 8 | (vv),xx,ooo,hhhh,pppp | N
RP | Watts | U009M2PCQT | 2 | H | 1997-08-26 | 2024-08-26 | N | 9 | (vv),xx,ooo,hhhh,pppp | N
RP | Watts | U009M2QT | 0.75 | H | 1992-11-16 | 2022-11-16 | N | 8 | (vv),xx,ooo,hhhh,pppp | N
RP | Watts | U009M2QT | 1 | H | 1999-01-15 | 2023-01-15 | N | 9 | (vv),xx,ooo,hhhh,pppp | N
RP | Watts | U009M2QT | 1.5 | H | 1993-08-24 | 2023-08-24 | N | 8 | (vv),xx,ooo,hhhh,pppp | N
RP | Watts | U009M2QT | 2 | H | 1997-08-26 | 2024-08-26 | N | 9 | (vv),xx,ooo,hhhh,pppp | N
RP | Watts | U009PCQT | 0.5 | H | 1995-02-02 | 2022-02-02 | N | 8 | (vv),xx,ooo,hhhh,pppp | N
RP | Watts | U009PCQT | 0.75 | H | 1993-12-10 | 2023-12-10 | N | 8 | (vv),xx,ooo,hhhh,pppp | N
RP | Watts | U009PCQT | 1 | H | 1993-12-10 | 2023-12-10 | N | 8 | vv,xx,ooo,hhhh,pppp | Y
RP | Watts | U009PCQT | 1.25 | H | 1994-09-27 | 2024-09-27 | N | 8 | vv,xx,ooo,hhhh,pppp | Y
RP | Watts | U009PCQT | 1.5 | H | 1994-09-27 | 2024-09-27 | N | 8 | vv,xx,ooo,hhhh,pppp | Y
RP | Watts | U009PCQT | 2 | H | 1994-09-27 | 2024-09-27 | N | 8 | vv,xx,ooo,hhhh,pppp | Y
RP | Watts | U009QT | 0.5 | H | 1995-02-02 | 2022-02-02 | N | 8 | (vv),xx,ooo,hhhh,pppp | N
RP | Watts | U009QT | 0.75 | H | 1988-01-11 | 2024-01-11 | N | 7 | vv,xx,ooo,hhhh,pppp | Y
RP | Watts | U009QT | 1 | H | 1988-01-11 | 2024-01-11 | N | 7 | vv,xx,ooo,hhhh,pppp | Y
RP | Watts | U009QT | 1.25 | H | 1988-08-09 | 2024-08-09 | N | 7 | vv,xx,ooo,hhhh,pppp | Y
RP | Watts | U009QT | 1.5 | H | 1988-08-09 | 2024-08-09 | N | 7 | vv,xx,ooo,hhhh,pppp | Y
RP | Watts | U009QT | 2 | H | 1988-08-09 | 2024-08-09 | N | 7 | vv,xx,ooo,hhhh,pppp | Y
RP | Watts | U009SSPCQT | 0.75 | H | 1993-12-10 | 2023-12-10 | N | 8 | vv,xx,pppp | Y
RP | Watts | U009SSPCQT | 1 | H | 1993-12-10 | 2023-12-10 | N | 8 | vv,xx,pppp | Y
RP | Watts | U009SSPCQT | 1.25 | H | 1994-09-27 | 2024-09-27 | N | 8 | vv,xx,pppp | Y
RP | Watts | U009SSPCQT | 1.5 | H | 1994-09-27 | 2024-09-27 | N | 8 | vv,xx,pppp | Y
RP | Watts | U009SSPCQT | 2 | H | 1994-09-27 | 2024-09-27 | N | 8 | vv,xx,pppp | Y
RP | Watts | U009SSQT | 0.75 | H | 1988-01-11 | 2024-01-11 | N | 7 | vv,xx,pppp | Y
RP | Watts | U009SSQT | 1 | H | 1988-01-11 | 2024-01-11 | N | 7 | vv,xx,pppp | Y
RP | Watts | U009SSQT | 1.25 | H | 1988-08-09 | 2024-08-09 | N | 7 | vv,xx,pppp | Y
RP | Watts | U009SSQT | 1.5 | H | 1988-08-09 | 2024-08-09 | N | 7 | vv,xx,pppp | Y
RP | Watts | U009SSQT | 2 | H | 1988-08-09 | 2024-08-09 | N | 7 | vv,xx,pppp | Y
RP | Watts | U909HWQT | 0.75 | H | 1979-09-29 | 2024-09-29 | N | 5 | (vv),xx,ooo,hhhh,pppp | Y
RP | Watts | U909HWQT | 1 | H | 1979-09-29 | 2024-09-29 | N | 5 | (vv),xx,ooo,hhhh,pppp | Y
RP | Watts | U909QT | 0.75 | H | 1998-10-09 | 2022-10-09 | N | 9 | (vv),xx,ooo,hhhh,pppp | Y |  |  | Approved 6th Ed. (15 Jan 1982), 9th Ed. Approval for S/N 464100 and higher
RP | Watts | U909QT | 0.75 | VU | 1998-10-09 | 2022-10-09 | N | 9 | (vv),xx,ooo,hhhh,pppp | Y |  |  | S/N 464100 and greater
RP | Watts | U909QT | 1 | H | 1998-10-09 | 2022-10-09 | N | 9 | (vv),xx,ooo,hhhh,pppp | Y |  |  | Approved 6th Ed. (15 Jan 1982), 9th Ed. Approval for S/N 464100 and higher
RP | Watts | U909QT | 1 | VU | 1998-10-09 | 2022-10-09 | N | 9 | (vv),xx,ooo,hhhh,pppp | Y |  |  | S/N 464100 and greater
RP | Watts | U919AQT | 0.75 | VUVD | 2006-06-14 | 2024-06-14 | N | 9 | (vv),xx,ooo,hhhh,pppp | N
RP | Watts | U919AQT | 1 | VUVD | 2006-06-01 | 2024-06-01 | N | 9 | (vv),xx,ooo,hhhh,pppp | N
RP | Watts | U919AQT | 1.25 | VUVD | 2006-06-01 | 2024-06-01 | N | 9 | (vv),xx,ooo,hhhh,pppp | N
RP | Watts | U919AQT | 1.5 | VUVD | 2006-06-01 | 2024-06-01 | N | 9 | (vv),xx,ooo,hhhh,pppp | N
RP | Watts | U919AQT | 2 | VUVD | 2006-06-01 | 2024-06-01 | N | 9 | (vv),xx,ooo,hhhh,pppp | N
RP | Watts | U919QT | 1 | H | 2006-06-01 | 2024-06-01 | N | 9 | (vv),xx,ooo,hhhh,pppp | N
RP | Watts | U919QT | 1 | VD | 2006-08-30 | 2024-08-30 | N | 9 | (vv),xx,ooo,hhhh,pppp | N
RP | Watts | U919QT | 1.25 | H | 2006-06-01 | 2024-06-01 | N | 9 | (vv),xx,ooo,hhhh,pppp | N
RP | Watts | U919QT | 1.25 | VD | 2006-08-30 | 2024-08-30 | N | 9 | (vv),xx,ooo,hhhh,pppp | N
RP | Watts | U919QT | 1.5 | H | 2006-06-01 | 2024-06-01 | N | 9 | (vv),xx,ooo,hhhh,pppp | N
RP | Watts | U919QT | 1.5 | VD | 2006-08-30 | 2024-08-30 | N | 9 | (vv),xx,ooo,hhhh,pppp | N
RP | Watts | U919QT | 2 | H | 2006-06-01 | 2024-06-01 | N | 9 | (vv),xx,ooo,hhhh,pppp | N
RP | Watts | U919QT | 2 | VD | 2006-08-30 | 2024-08-30 | N | 9 | (vv),xx,ooo,hhhh,pppp | N
RP | Wilkins | 375 | 0.5 | H | 2011-04-06 | 2023-04-06 | N | 9 | (int) | N |  |  | Testcocks: Female Threaded End or 45 degree male SAE flare
RP | Wilkins | 375 | 0.75 | H | 2007-03-09 | 2022-03-09 | N | 9 | (int) | N |  |  | Testcocks: Female Threaded End or 45 degree male SAE flare
RP | Wilkins | 375 | 1 | H | 2007-03-09 | 2022-03-09 | N | 9 | (int) | N |  |  | Testcocks: Female Threaded End or 45 degree male SAE flare
RP | Wilkins | 375 | 1.25 | H | 2010-04-20 | 2022-04-20 | N | 9 | (int) | N
RP | Wilkins | 375 | 1.5 | H | 2010-04-20 | 2022-04-20 | N | 9 | (int) | N
RP | Wilkins | 375 | 2 | H | 2010-04-20 | 2022-04-20 | N | 9 | (int) | N
RP | Wilkins | 375 | 2.5 | H | 2001-09-28 | 2022-09-28 | N | 9 | (gg),ee,ff,hh,ll,mm,tt,uu,yy,zz,ppp,qqq,zzz,dddd,ssss,tttt,vvvv,wwww,yyyy,zzzz,kkkkk,gggggg,hhhhhh,jjjjjj,kkkkkk,mmmmmm,nnnnnn | N |  |  | Up to serial number L61205
RP | Wilkins | 375 | 2.5 | H | 2010-09-09 | 2022-09-09 | Y | 9 | (gg),hh,ppp,qqq,ssss,tttt,vvvv,wwww,yyyy,zzzz,kkkkk,gggggg,hhhhhh,jjjjjj,kkkkkk,mmmmmm,nnnnnn | N |  |  | Serial number L61205 and higher
RP | Wilkins | 375 | 3 | H | 2001-09-28 | 2022-09-28 | N | 9 | (gg),ee,ff,hh,ll,mm,tt,uu,yy,zz,ppp,qqq,zzz,dddd,ssss,tttt,vvvv,wwww,yyyy,zzzz,kkkkk,gggggg,hhhhhh,jjjjjj,kkkkkk,mmmmmm,nnnnnn | N |  |  | Up to serial number L61205
RP | Wilkins | 375 | 3 | H | 2010-09-09 | 2022-09-09 | Y | 9 | (gg),hh,ppp,qqq,ssss,tttt,vvvv,wwww,yyyy,zzzz,kkkkk,gggggg,hhhhhh,jjjjjj,kkkkkk,mmmmmm,nnnnnn | N |  |  | Serial number L61205 and higher
RP | Wilkins | 375 | 4 | H | 2000-03-27 | 2023-03-27 | N | 9 | (gg),ee,ff,hh,ll,mm,tt,uu,yy,zz,ppp,qqq,vvv,www,zzz,dddd,eeee,ssss,tttt,vvvv,wwww,yyyy,zzzz,kkkkk,gggggg,hhhhhh,jjjjjj,kkkkkk,mmmmmm,nnnnnn | N |  |  | Up to serial number L61205
RP | Wilkins | 375 | 4 | H | 2010-09-09 | 2022-09-09 | Y | 9 | (gg),hh,ppp,qqq,vvv,www,ssss,tttt,vvvv,wwww,yyyy,zzzz,kkkkk,gggggg,hhhhhh,jjjjjj,kkkkkk,mmmmmm,nnnnnn | N |  |  | Serial number L61205 and higher
RP | Wilkins | 375 | 6 | H | 2000-07-27 | 2024-07-27 | N | 9 | (gg),ee,ff,hh,ll,mm,tt,uu,yy,zz,ppp,qqq,vvv,www,zzz,dddd,eeee,ssss,tttt,vvvv,wwww,yyyy,zzzz,kkkkk,gggggg,hhhhhh,jjjjjj,kkkkkk,mmmmmm,nnnnnn | N |  |  | Up to serial number L61205
RP | Wilkins | 375 | 6 | H | 2010-09-09 | 2022-09-09 | Y | 9 | (gg),hh,ppp,qqq,vvv,www,ssss,tttt,vvvv,wwww,yyyy,zzzz,kkkkk,gggggg,hhhhhh,jjjjjj,kkkkkk,mmmmmm,nnnnnn | N |  |  | Serial number L61205 and higher
RP | Wilkins | 375 | 8 | H | 2002-11-11 | 2023-11-11 | N | 9 | (gg),ee,ff,hh,ll,mm,tt,uu,yy,zz,ppp,qqq,vvv,www,zzz,dddd,eeee,ssss,tttt,vvvv,wwww,yyyy,zzzz,kkkkk,gggggg,hhhhhh,jjjjjj,kkkkkk,mmmmmm,nnnnnn | N |  |  | Up to serial number L61205
RP | Wilkins | 375 | 8 | H | 2010-09-09 | 2022-09-09 | Y | 9 | (gg),hh,ppp,qqq,vvv,www,ssss,tttt,vvvv,wwww,yyyy,zzzz,kkkkk,gggggg,hhhhhh,jjjjjj,kkkkkk,mmmmmm,nnnnnn | N |  |  | Serial number L61205 and higher
RP | Wilkins | 375 | 10 | H | 2004-11-22 | 2022-11-22 | N | 9 | (gg),ee,ff,hh,ll,mm,tt,uu,yy,zz,ppp,qqq,vvv,www,zzz,dddd,eeee,ssss,tttt,vvvv,wwww,yyyy,zzzz,kkkkk,gggggg,hhhhhh,jjjjjj,kkkkkk,mmmmmm,nnnnnn | N |  |  | Up to serial number L61205
RP | Wilkins | 375 | 10 | H | 2010-09-09 | 2022-09-09 | Y | 9 | (gg),hh,ppp,qqq,vvv,www,ssss,tttt,vvvv,wwww,yyyy,zzzz,kkkkk,gggggg,hhhhhh,jjjjjj,kkkkkk,mmmmmm,nnnnnn | N |  |  | Serial number L61205 and higher
RP | Wilkins | 475 | 2.5 | VUVD | 2002-01-24 | 2023-01-24 | N | 9 | (gg),ee,ff,hh,ll,mm,tt,uu,yy,zz,ppp,qqq,zzz,dddd,ssss,tttt,vvvv,wwww,yyyy,zzzz,kkkkk,gggggg,hhhhhh,jjjjjj,kkkkkk,mmmmmm,nnnnnn | N |  |  | Up to serial number Q05664
RP | Wilkins | 475 | 2.5 | VUVD | 2010-09-09 | 2022-09-09 | Y | 9 | (gg),hh,ppp,qqq,ssss,tttt,vvvv,wwww,yyyy,zzzz,kkkkk,gggggg,hhhhhh,jjjjjj,kkkkkk,mmmmmm,nnnnnn | N |  |  | Serial number Q05664 and higher
RP | Wilkins | 475 | 3 | VUVD | 2002-01-24 | 2023-01-24 | N | 9 | (gg),ee,ff,hh,ll,mm,tt,uu,yy,zz,ppp,qqq,zzz,dddd,ssss,tttt,vvvv,wwww,yyyy,zzzz,kkkkk,gggggg,hhhhhh,jjjjjj,kkkkkk,mmmmmm,nnnnnn | N |  |  | Up to serial number Q05664
RP | Wilkins | 475 | 3 | VUVD | 2010-09-09 | 2022-09-09 | Y | 9 | (gg),hh,ppp,qqq,ssss,tttt,vvvv,wwww,yyyy,zzzz,kkkkk,gggggg,hhhhhh,jjjjjj,kkkkkk,mmmmmm,nnnnnn | N |  |  | Serial number Q05664 and higher
RP | Wilkins | 475 | 4 | VUVD | 2000-07-27 | 2024-07-27 | N | 9 | (ppp),qqq,sss,ttt,www,yyy,zzz,dddd,eeee,ssss,uuuu,vvvv,xxxx,yyyy,aaaaa,kkkkk,lllll,gggggg,iiiiii,jjjjjj,llllll,mmmmmm,oooooo | N |  |  | Up to serial number Q05664
RP | Wilkins | 475 | 4 | VUVD | 2010-09-09 | 2022-09-09 | Y | 9 | (ppp),qqq,sss,ttt,www,yyy,ssss,uuuu,vvvv,xxxx,yyyy,aaaaa,kkkkk,lllll,gggggg,iiiiii,jjjjjj,llllll,mmmmmm,oooooo | N |  |  | Serial number Q05664 and higher
RP | Wilkins | 475 | 6 | VUVD | 2000-07-27 | 2024-07-27 | N | 9 | (ppp),qqq,sss,ttt,www,yyy,zzz,dddd,eeee,ssss,uuuu,vvvv,xxxx,yyyy,aaaaa,kkkkk,lllll,gggggg,iiiiii,jjjjjj,llllll,mmmmmm,oooooo | N |  |  | Up to serial number Q05664
RP | Wilkins | 475 | 6 | VUVD | 2010-09-09 | 2022-09-09 | Y | 9 | (ppp),qqq,sss,ttt,www,yyy,ssss,uuuu,vvvv,xxxx,yyyy,aaaaa,kkkkk,lllll,gggggg,iiiiii,jjjjjj,llllll,mmmmmm,oooooo | N |  |  | Serial number Q05664 and higher
RP | Wilkins | 475 | 8 | VUVD | 2003-07-03 | 2024-07-03 | N | 9 | (ppp),qqq,sss,ttt,www,yyy,zzz,dddd,eeee,ssss,uuuu,vvvv,xxxx,yyyy,aaaaa,kkkkk,lllll,gggggg,iiiiii,jjjjjj,llllll,mmmmmm,oooooo | N |  |  | Up to serial number Q05664
RP | Wilkins | 475 | 8 | VUVD | 2010-09-09 | 2022-09-09 | Y | 9 | (ppp),qqq,sss,ttt,www,yyy,ssss,uuuu,vvvv,xxxx,yyyy,aaaaa,kkkkk,lllll,gggggg,iiiiii,jjjjjj,llllll,mmmmmm,oooooo | N |  |  | Serial number Q05664 and higher
RP | Wilkins | 475 | 10 | VUVD | 2004-11-22 | 2022-11-22 | N | 9 | (ppp),qqq,sss,ttt,www,zzz,dddd,eeee,ssss,uuuu,vvvv,xxxx,yyyy,aaaaa,kkkkk,lllll,gggggg,iiiiii,jjjjjj,llllll,mmmmmm,oooooo | N |  |  | Up to serial number Q05664
RP | Wilkins | 475 | 10 | VUVD | 2010-09-09 | 2022-09-09 | Y | 9 | (ppp),qqq,sss,ttt,www,ssss,uuuu,vvvv,xxxx,yyyy,aaaaa,kkkkk,lllll,gggggg,iiiiii,jjjjjj,llllll,mmmmmm,oooooo | N |  |  | Serial number Q05664 and higher
RP | Wilkins | 575 | 0.75 | H | 1976-04-28 | 2024-04-28 | N | 5 |  | Y
RP | Wilkins | 575 | 1 | H | 1976-04-28 | 2024-04-28 | N | 5 |  | Y
RP | Wilkins | 575 | 3 | H | 1979-08-20 | 2024-08-20 | N | 5 | gg,ee,tt,yy | Y
RP | Wilkins | 575 | 4 | H | 1980-06-08 | 2022-06-08 | N | 5 | gg,ee,tt,yy | Y
RP | Wilkins | 575 | 6 | H | 1981-07-06 | 2023-07-06 | N | 6 | gg,ee,tt,yy | Y
RP | Wilkins | 975 | 8 | H | 1995-02-06 | 2022-02-06 | N | 8 | (ppp),qqq,sss,ttt,www,yyy,zzz,dddd,eeee,ssss,uuuu,vvvv,xxxx,yyyy,aaaaa,kkkkk,lllll,gggggg,iiiiii,jjjjjj,llllll,mmmmmm,oooooo | Y
RP | Wilkins | 975 | 10 | H | 1995-02-06 | 2022-02-06 | N | 8 | (gg),ee,ff,hh,tt,uu,yy,zz,ppp,ssss,tttt,vvvv,wwww,yyyy,zzzz | Y
RP | Wilkins | 375A | 2.5 | H | 2008-10-20 | 2023-10-20 | N | 9 | (ppp),qqq,sss,ttt,yyy,zzz,dddd,ssss,uuuu,vvvv,xxxx,yyyy,aaaaa,kkkkk,lllll,gggggg,iiiiii,jjjjjj,llllll,mmmmmm,oooooo | N |  |  | Up to serial number X18805
RP | Wilkins | 375A | 2.5 | H | 2010-09-09 | 2022-09-09 | Y | 9 | (ppp),qqq,sss,ttt,yyy,ssss,uuuu,vvvv,xxxx,yyyy,aaaaa,kkkkk,lllll,gggggg,iiiiii,jjjjjj,llllll,mmmmmm,oooooo | N |  |  | Serial number X18805 and higher
RP | Wilkins | 375A | 3 | H | 2008-10-20 | 2023-10-20 | N | 9 | (ppp),qqq,sss,ttt,yyy,zzz,dddd,ssss,uuuu,vvvv,xxxx,yyyy,aaaaa,kkkkk,lllll,gggggg,iiiiii,jjjjjj,llllll,mmmmmm,oooooo | N |  |  | Up to serial number X18805
RP | Wilkins | 375A | 3 | H | 2010-09-09 | 2022-09-09 | Y | 9 | (ppp),qqq,sss,ttt,yyy,ssss,uuuu,vvvv,xxxx,yyyy,aaaaa,kkkkk,lllll,gggggg,iiiiii,jjjjjj,llllll,mmmmmm,oooooo | N |  |  | Serial number X18805 and higher
RP | Wilkins | 375A | 4 | H | 2004-06-02 | 2022-06-02 | N | 9 | (ppp),qqq,sss,ttt,www,yyy,zzz,dddd,eeee,ssss,uuuu,vvvv,xxxx,yyyy,aaaaa,kkkkk,lllll,gggggg,iiiiii,jjjjjj,llllll,mmmmmm,oooooo | N |  |  | Up to serial number X18805
RP | Wilkins | 375A | 4 | H | 2010-09-09 | 2022-09-09 | Y | 9 | (ppp),qqq,sss,ttt,www,yyy,zzz,ssss,uuuu,vvvv,xxxx,yyyy,aaaaa,kkkkk,lllll,gggggg,iiiiii,jjjjjj,llllll,mmmmmm,oooooo | N |  |  | Serial number X18805 and higher
RP | Wilkins | 375A | 6 | H | 2003-11-25 | 2024-11-25 | N | 9 | (ppp),qqq,sss,ttt,www,yyy,zzz,dddd,eeee,ssss,uuuu,vvvv,xxxx,yyyy,aaaaa,kkkkk,lllll,gggggg,iiiiii,jjjjjj,llllll,mmmmmm,oooooo | N |  |  | Up to serial number X18805
RP | Wilkins | 375A | 6 | H | 2010-09-09 | 2022-09-09 | Y | 9 | (ppp),qqq,sss,ttt,www,yyy,zzz,ssss,uuuu,vvvv,xxxx,yyyy,aaaaa,kkkkk,lllll,gggggg,iiiiii,jjjjjj,llllll,mmmmmm,oooooo | N |  |  | Serial number X18805 and higher
RP | Wilkins | 375A | 8 | H | 2004-06-15 | 2022-06-15 | N | 9 | (ppp),qqq,sss,ttt,www,yyy,zzz,ssss,uuuu,vvvv,xxxx,yyyy,aaaaa,kkkkk,lllll,gggggg,iiiiii,jjjjjj,llllll,mmmmmm,oooooo | N |  |  | Up to serial number X18805
RP | Wilkins | 375A | 8 | H | 2010-09-09 | 2022-09-09 | Y | 9 | (ppp),qqq,sss,ttt,www,yyy,ssss,uuuu,vvvv,xxxx,yyyy,aaaaa,kkkkk,lllll,gggggg,iiiiii,jjjjjj,llllll,mmmmmm,oooooo | N |  |  | Serial number X18805 and higher
RP | Wilkins | 375A | 10 | H | 2007-03-02 | 2022-03-02 | N | 9 | (ppp),qqq,sss,ttt,www,yyy,zzz,dddd,eeee,ssss,uuuu,vvvv,xxxx,yyyy,aaaaa,kkkkk,lllll,gggggg,iiiiii,jjjjjj,llllll,mmmmmm,oooooo | N |  |  | Up to serial number X18805
RP | Wilkins | 375A | 10 | H | 2010-09-09 | 2022-09-09 | Y | 9 | (ppp),qqq,sss,ttt,www,yyy,ssss,uuuu,vvvv,xxxx,yyyy,aaaaa,kkkkk,lllll,gggggg,iiiiii,jjjjjj,llllll,mmmmmm,oooooo | N |  |  | Serial number X18805 and higher
RP | Wilkins | 375AMS | 2.5 | H | 2014-11-05 | 2023-11-05 | Y | 9 | (ppp),qqq,sss,ttt,www,yyy,zzz,ssss,uuuu,vvvv,xxxx,yyyy,aaaaa,kkkkk,lllll | N
RP | Wilkins | 375AMS | 3 | H | 2014-11-05 | 2023-11-05 | Y | 9 | (ppp),qqq,sss,ttt,www,yyy,zzz,ssss,uuuu,vvvv,xxxx,yyyy,aaaaa,kkkkk,lllll | N
RP | Wilkins | 375AMS | 4 | H | 2014-11-05 | 2023-11-05 | Y | 9 | (ppp),qqq,sss,ttt,www,yyy,zzz,ssss,uuuu,vvvv,xxxx,yyyy,aaaaa,kkkkk,lllll | N
RP | Wilkins | 375AMS | 6 | H | 2014-11-05 | 2023-11-05 | Y | 9 | (ppp),qqq,sss,ttt,www,yyy,zzz,ssss,uuuu,vvvv,xxxx,yyyy,aaaaa,kkkkk,lllll | N
RP | Wilkins | 375AMS | 8 | H | 2014-11-05 | 2023-11-05 | Y | 9 | (ppp),qqq,sss,ttt,www,yyy,ssss,uuuu,vvvv,xxxx,yyyy,aaaaa,kkkkk,lllll | N
RP | Wilkins | 375AMS | 10 | H | 2014-11-05 | 2023-11-05 | Y | 9 | (ppp),qqq,sss,ttt,www,yyy,zzz,ssss,uuuu,vvvv,xxxx,yyyy,aaaaa,kkkkk,lllll | N
RP | Wilkins | 375AR | 2.5 | H | 2010-06-16 | 2022-06-16 | N | 9 | (ppp),qqq,sss,ttt,yyy,zzz,dddd,ssss,uuuu,vvvv,xxxx,yyyy,aaaaa,kkkkk,lllll,gggggg,iiiiii,jjjjjj,llllll,mmmmmm,oooooo | N |  |  | Integral grooved spool between the #2 ck and #2 SOV - assembly length: min. 34 1/4" and max. 47 1/8" Up to serial number X18805
RP | Wilkins | 375AR | 2.5 | H | 2010-09-09 | 2022-09-09 | Y | 9 | (ppp),qqq,sss,ttt,yyy,ssss,uuuu,vvvv,xxxx,yyyy,aaaaa,kkkkk,lllll,gggggg,iiiiii,jjjjjj,llllll,mmmmmm,oooooo | N |  |  | Only Serial No G00110 and higher approved. These have an Integral grooved spool between the #2 ck and #2 SOV with length: min. 34 1/4" and max. 47 1/8"
RP | Wilkins | 375AR | 3 | H | 2010-06-16 | 2022-06-16 | N | 9 | (ppp),qqq,sss,ttt,yyy,zzz,dddd,ssss,uuuu,vvvv,xxxx,yyyy,aaaaa,kkkkk,lllll,gggggg,iiiiii,jjjjjj,llllll,mmmmmm,oooooo | N |  |  | Only Serial No G00110 and higher approved. These have an Integral grooved spool between the #2 ck and #2 SOV with length: min. 34 1/4" and max. 47 1/8"
RP | Wilkins | 375AR | 3 | H | 2010-09-09 | 2022-09-09 | Y | 9 | (ppp),qqq,sss,ttt,yyy,ssss,uuuu,vvvv,xxxx,yyyy,aaaaa,kkkkk,lllll,gggggg,iiiiii,jjjjjj,llllll,mmmmmm,oooooo | N |  |  | Only Serial No G00110 and higher approved. These have an Integral grooved spool between the #2 ck and #2 SOV with length: min. 34 1/4" and max. 47 1/8"
RP | Wilkins | 375AR | 4 | H | 2010-03-25 | 2022-03-25 | N | 9 | (ppp),qqq,sss,ttt,www,yyy,zzz,dddd,eeee,ssss,uuuu,vvvv,xxxx,yyyy,aaaaa,kkkkk,lllll,gggggg,iiiiii,jjjjjj,llllll,mmmmmm,oooooo | N |  |  | Only Serial No G00110 and higher approved. These have an Integral grooved spool between the #2 ck and #2 SOV with length: min. 34 1/4" and max. 47 1/8"
RP | Wilkins | 375AR | 4 | H | 2010-09-09 | 2022-09-09 | Y | 9 | (ppp),qqq,sss,ttt,www,yyy,zzz,dddd,eeee,ssss,uuuu,vvvv,xxxx,yyyy,aaaaa,kkkkk,lllll,gggggg,iiiiii,jjjjjj,llllll,mmmmmm,oooooo | N |  |  | Only Serial No G00110 and higher approved. These have an Integral grooved spool between the #2 ck and #2 SOV with length: min. 35 3/4" and max. 62 1/4"
RP | Wilkins | 375AR | 6 | H | 2010-03-25 | 2022-03-25 | N | 9 | (ppp),qqq,sss,ttt,www,yyy,zzz,dddd,eeee,ssss,uuuu,vvvv,xxxx,yyyy,aaaaa,kkkkk,lllll,gggggg,iiiiii,jjjjjj,llllll,mmmmmm,oooooo | N |  |  | Only Serial No G00110 and higher approved. These have an Integral grooved spool between the #2 ck and #2 SOV with length: min. 34 1/4" and max. 47 1/8"
RP | Wilkins | 375AR | 6 | H | 2010-09-09 | 2022-09-09 | Y | 9 | (ppp),qqq,sss,ttt,www,yyy,zzz,dddd,eeee,ssss,uuuu,vvvv,xxxx,yyyy,aaaaa,kkkkk,lllll,gggggg,iiiiii,jjjjjj,llllll,mmmmmm,oooooo | N |  |  | Only Serial No G00110 and higher approved. These have an Integral grooved spool between the #2 ck and #2 SOV with length: min. 42 1/2" and max. 71 1/4"
RP | Wilkins | 375AR | 8 | H | 2010-03-25 | 2022-03-25 | N | 9 | (ppp),qqq,sss,ttt,www,yyy,zzz,dddd,eeee,ssss,uuuu,vvvv,xxxx,yyyy,aaaaa,kkkkk,lllll,gggggg,iiiiii,jjjjjj,llllll,mmmmmm,oooooo | N |  |  | Only Serial No G00110 and higher approved. These have an Integral grooved spool between the #2 ck and #2 SOV with length: min. 34 1/4" and max. 47 1/8"
RP | Wilkins | 375AR | 8 | H | 2010-09-09 | 2022-09-09 | Y | 9 | (ppp),qqq,sss,ttt,www,yyy,zzz,dddd,eeee,ssss,uuuu,vvvv,xxxx,yyyy,aaaaa,kkkkk,lllll,gggggg,iiiiii,jjjjjj,llllll,mmmmmm,oooooo | N |  |  | Only Serial No G00110 and higher approved. These have an Integral grooved spool between the #2 ck and #2 SOV with length: min. 57 7/8" and max. 86"
RP | Wilkins | 375AR | 10 | H | 2010-03-25 | 2022-03-25 | N | 9 | (ppp),qqq,sss,ttt,www,yyy,zzz,dddd,eeee,ssss,uuuu,vvvv,xxxx,yyyy,aaaaa,kkkkk,lllll,gggggg,iiiiii,jjjjjj,llllll,mmmmmm,oooooo | N |  |  | Only Serial No G00110 and higher approved. These have an Integral grooved spool between the #2 ck and #2 SOV with length: min. 34 1/4" and max. 47 1/8"
RP | Wilkins | 375AR | 10 | H | 2010-09-09 | 2022-09-09 | Y | 9 | (ppp),qqq,sss,ttt,www,yyy,zzz,dddd,eeee,ssss,uuuu,vvvv,xxxx,yyyy,aaaaa,kkkkk,lllll,gggggg,iiiiii,jjjjjj,llllll,mmmmmm,oooooo | N |  |  | Only Serial No G00110 and higher approved. These have an Integral grooved spool between the #2 ck and #2 SOV with length: min. 61 3/8" and max. 100 5/8"
RP | Wilkins | 375ARMS | 2.5 | H | 2014-11-05 | 2023-11-05 | Y | 9 | (ppp),qqq,sss,ttt,yyy,ssss,uuuu,vvvv,xxxx,yyyy,aaaaa,kkkkk,lllll | N |  |  | These have an Integral grooved spool between the #2 ck and #2 SOV with length: min. 34 1/4" and max. 47 1/8"
RP | Wilkins | 375ARMS | 3 | H | 2014-11-05 | 2023-11-05 | Y | 9 | (ppp),qqq,sss,ttt,yyy,ssss,uuuu,vvvv,xxxx,yyyy,aaaaa,kkkkk,lllll | N |  |  | These have an Integral grooved spool between the #2 ck and #2 SOV with length: min. 34 1/4" and max. 48 1/8"
RP | Wilkins | 375ARMS | 4 | H | 2014-11-05 | 2023-11-05 | Y | 9 | (ppp),qqq,sss,ttt,www,yyy,zzz,dddd,eeee,ssss,uuuu,vvvv,xxxx,yyyy,aaaaa,kkkkk,lllll | N |  |  | These have an Integral grooved spool between the #2 ck and #2 SOV with length: min. 35 3/4" and max. 62 1/4"
RP | Wilkins | 375ARMS | 6 | H | 2014-11-05 | 2023-11-05 | Y | 9 | (ppp),qqq,sss,ttt,www,yyy,zzz,dddd,eeee,ssss,uuuu,vvvv,xxxx,yyyy,aaaaa,kkkkk,lllll | N |  |  | These have an Integral grooved spool between the #2 ck and #2 SOV with length: min. 42 1/2" and max. 71 1/4"
RP | Wilkins | 375ARMS | 8 | H | 2014-11-05 | 2023-11-05 | Y | 9 | (ppp),qqq,sss,ttt,www,yyy,zzz,dddd,eeee,ssss,uuuu,vvvv,xxxx,yyyy,aaaaa,kkkkk,lllll | N |  |  | These have an Integral grooved spool between the #2 ck and #2 SOV with length: min. 57 7/8" and max. 86"
RP | Wilkins | 375ARMS | 10 | H | 2014-11-05 | 2023-11-05 | Y | 9 | (ppp),qqq,sss,ttt,www,yyy,zzz,dddd,eeee,ssss,uuuu,vvvv,xxxx,yyyy,aaaaa,kkkkk,lllll | N |  |  | These have an Integral grooved spool between the #2 ck and #2 SOV with length: min. 61 3/8" and max. 100 5/8"
RP | Wilkins | 375ARW1 | 2.5 | H | 2019-03-12 | 2022-03-12 | Y | 9 | (ppp),qqq,sss,ttt,www,yyy,zzz,dddd,eeee,ssss,uuuu,vvvv,xxxx,yyyy,aaaaa,kkkkk,lllll,gggggg,iiiiii,jjjjjj,llllll,mmmmmm,oooooo | N |  |  | These have an Integral grooved spool between the #2 ck and #2 SOV with length: min. 34 1/4" and max. 47 1/8"
RP | Wilkins | 375ARW1 | 3 | H | 2019-03-12 | 2022-03-12 | Y | 9 | (ppp),qqq,sss,ttt,www,yyy,zzz,dddd,eeee,ssss,uuuu,vvvv,xxxx,yyyy,aaaaa,kkkkk,lllll,gggggg,iiiiii,jjjjjj,llllll,mmmmmm,oooooo | N |  |  | These have an Integral grooved spool between the #2 ck and #2 SOV with length: min. 34 3/4" and max. 48 1/8"
RP | Wilkins | 375ARW1 | 4 | H | 2019-03-12 | 2022-03-12 | Y | 9 | (ppp),qqq,sss,ttt,www,yyy,zzz,dddd,eeee,ssss,uuuu,vvvv,xxxx,yyyy,aaaaa,kkkkk,lllll,gggggg,iiiiii,jjjjjj,llllll,mmmmmm,oooooo | N |  |  | These have an Integral grooved spool between the #2 ck and #2 SOV with length: min. 35 3/4" and max. 62 1/4"
RP | Wilkins | 375ARW1 | 6 | H | 2019-03-12 | 2022-03-12 | Y | 9 | (ppp),qqq,sss,ttt,www,yyy,zzz,dddd,eeee,ssss,uuuu,vvvv,xxxx,yyyy,aaaaa,kkkkk,lllll,gggggg,iiiiii,jjjjjj,llllll,mmmmmm,oooooo | N |  |  | These have an Integral grooved spool between the #2 ck and #2 SOV with length: min. 42 1/2" and max. 71 1/4"
RP | Wilkins | 375ARW1 | 8 | H | 2019-04-25 | 2022-04-25 | Y | 9 | (ppp),qqq,sss,ttt,www,yyy,zzz,dddd,eeee,ssss,uuuu,vvvv,xxxx,yyyy,aaaaa,kkkkk,lllll,gggggg,iiiiii,jjjjjj,llllll,mmmmmm,oooooo | N |  |  | These have an Integral grooved spool between the #2 ck and #2 SOV with length: min. 57 7/8" and max. 86"
RP | Wilkins | 375ARW1 | 10 | H | 2019-04-25 | 2022-04-25 | Y | 9 | (ppp),qqq,sss,ttt,www,yyy,zzz,dddd,eeee,ssss,uuuu,vvvv,xxxx,yyyy,aaaaa,kkkkk,lllll,gggggg,iiiiii,jjjjjj,llllll,mmmmmm,oooooo | N |  |  | These have an Integral grooved spool between the #2 ck and #2 SOV with length: min. 61 3/8" and max. 100 5/8"
RP | Wilkins | 375AST | 2.5 | H | 2015-06-12 | 2024-06-12 | Y | 10 | (yyy),ssss,uuuu,vvvv,xxxx,yyyy,aaaaa,kkkkk,lllll,gggggg,iiiiii,jjjjjj,llllll,mmmmmm,oooooo | N
RP | Wilkins | 375AST | 3 | H | 2015-06-12 | 2024-06-12 | Y | 10 | (yyy),ssss,uuuu,vvvv,xxxx,yyyy,aaaaa,kkkkk,lllll,gggggg,iiiiii,jjjjjj,llllll,mmmmmm,oooooo | N
RP | Wilkins | 375AST | 4 | H | 2012-05-31 | 2024-05-31 | Y | 10 | (yyy),ssss,uuuu,vvvv,xxxx,yyyy,aaaaa,kkkkk,lllll,gggggg,iiiiii,jjjjjj,llllll,mmmmmm,oooooo | N
RP | Wilkins | 375AST | 6 | H | 2013-06-24 | 2022-06-24 | Y | 10 | (yyy),ssss,uuuu,vvvv,xxxx,yyyy,aaaaa,kkkkk,lllll,gggggg,iiiiii,jjjjjj,llllll,mmmmmm,oooooo | N
RP | Wilkins | 375AST | 8 | H | 2013-11-26 | 2022-11-26 | Y | 10 | (yyy),ssss,uuuu,vvvv,xxxx,yyyy,aaaaa,kkkkk,lllll,gggggg,iiiiii,jjjjjj,llllll,mmmmmm,oooooo | N
RP | Wilkins | 375AST | 10 | H | 2013-11-26 | 2022-11-26 | Y | 10 | (yyy),ssss,uuuu,vvvv,xxxx,yyyy,aaaaa,kkkkk,lllll,gggggg,iiiiii,jjjjjj,llllll,mmmmmm,oooooo | N
RP | Wilkins | 375ASTMS | 2.5 | H | 2014-11-05 | 2023-11-05 | Y | 10 | (yyy),ssss,uuuu,vvvv,xxxx,yyyy,aaaaa,kkkkk,lllll | N
RP | Wilkins | 375ASTMS | 3 | H | 2014-11-05 | 2023-11-05 | Y | 10 | (yyy),ssss,uuuu,vvvv,xxxx,yyyy,aaaaa,kkkkk,lllll | N
RP | Wilkins | 375ASTMS | 4 | H | 2014-11-05 | 2023-11-05 | Y | 10 | (yyy),ssss,uuuu,vvvv,xxxx,yyyy,aaaaa,kkkkk,lllll | N
RP | Wilkins | 375ASTMS | 6 | H | 2014-11-05 | 2023-11-05 | Y | 10 | (yyy),ssss,uuuu,vvvv,xxxx,yyyy,aaaaa,kkkkk,lllll | N
RP | Wilkins | 375ASTMS | 8 | H | 2014-11-05 | 2023-11-05 | Y | 10 | (yyy),ssss,uuuu,vvvv,xxxx,yyyy,aaaaa,kkkkk,lllll | N
RP | Wilkins | 375ASTMS | 10 | H | 2014-11-05 | 2023-11-05 | Y | 10 | (yyy),ssss,uuuu,vvvv,xxxx,yyyy,aaaaa,kkkkk,lllll | N
RP | Wilkins | 375ASTR | 2.5 | H | 2015-06-12 | 2024-06-12 | Y | 10 | (yyy),ssss,uuuu,vvvv,xxxx,yyyy,aaaaa,kkkkk,lllll,gggggg,iiiiii,jjjjjj,llllll,mmmmmm,oooooo | N |  |  | Integral Stainless Steel grooved spool between the #2 ck and #2 SOV - assembly length: min. 31" and max. 47 1/8"
RP | Wilkins | 375ASTR | 3 | H | 2015-06-12 | 2024-06-12 | Y | 10 | (yyy),ssss,uuuu,vvvv,xxxx,yyyy,aaaaa,kkkkk,lllll,gggggg,iiiiii,jjjjjj,llllll,mmmmmm,oooooo | N |  |  | Integral Stainless Steel grooved spool between the #2 ck and #2 SOV - assembly length: min. 31 1/2" and max. 48 1/8"
RP | Wilkins | 375ASTR | 4 | H | 2012-05-31 | 2024-05-31 | Y | 10 | (yyy),ssss,uuuu,vvvv,xxxx,yyyy,aaaaa,kkkkk,lllll,gggggg,iiiiii,jjjjjj,llllll,mmmmmm,oooooo | N |  |  | Integral Stainless Steel grooved spool between the #2 ck and #2 SOV - assembly length: min. 32 5/8" and max. 62 1/4"
RP | Wilkins | 375ASTR | 6 | H | 2013-11-05 | 2022-11-05 | Y | 10 | (yyy),ssss,uuuu,vvvv,xxxx,yyyy,aaaaa,kkkkk,lllll,gggggg,iiiiii,jjjjjj,llllll,mmmmmm,oooooo | N |  |  | Integral Stainless Steel grooved spool between the #2 ck and #2 SOV - assembly length: min. 39" and max. 71 1/4"
RP | Wilkins | 375ASTR | 8 | H | 2014-01-23 | 2023-01-23 | Y | 10 | (yyy),ssss,uuuu,vvvv,xxxx,yyyy,aaaaa,kkkkk,lllll,gggggg,iiiiii,jjjjjj,llllll,mmmmmm,oooooo | N |  |  | Integral Stainless Steel grooved spool between the #2 ck and #2 SOV - assembly length: min. 48 3/4" and max. 86"
RP | Wilkins | 375ASTR | 10 | H | 2014-01-23 | 2023-01-23 | Y | 10 | (yyy),ssss,uuuu,vvvv,xxxx,yyyy,aaaaa,kkkkk,lllll,gggggg,iiiiii,jjjjjj,llllll,mmmmmm,oooooo | N |  |  | Integral Stainless Steel grooved spool between the #2 ck and #2 SOV - assembly length: min. 52 5/8" and max. 100 5/8"
RP | Wilkins | 375ASTRMS | 2.5 | H | 2014-11-05 | 2023-11-05 | Y | 10 | (yyy),ssss,uuuu,vvvv,xxxx,yyyy,aaaaa,kkkkk,lllll | N |  |  | Integral Stainless Steel grooved spool between the #2 ck and #2 SOV - assembly length: min. 31" and max. 47 1/8"
RP | Wilkins | 375ASTRMS | 3 | H | 2014-11-05 | 2023-11-05 | Y | 10 | (yyy),ssss,uuuu,vvvv,xxxx,yyyy,aaaaa,kkkkk,lllll | N |  |  | Integral Stainless Steel grooved spool between the #2 ck and #2 SOV - assembly length: min. 31 1/2" and max. 48 1/8"
RP | Wilkins | 375ASTRMS | 4 | H | 2014-11-05 | 2023-11-05 | Y | 10 | (yyy),ssss,uuuu,vvvv,xxxx,yyyy,aaaaa,kkkkk,lllll | N |  |  | Integral Stainless Steel grooved spool between the #2 ck and #2 SOV - assembly length: min. 32 5/8" and max. 62 1/4"
RP | Wilkins | 375ASTRMS | 6 | H | 2014-11-05 | 2023-11-05 | Y | 10 | (yyy),ssss,uuuu,vvvv,xxxx,yyyy,aaaaa,kkkkk,lllll | N |  |  | Integral Stainless Steel grooved spool between the #2 ck and #2 SOV - assembly length: min. 39" and max. 71 1/4"
RP | Wilkins | 375ASTRMS | 8 | H | 2014-11-05 | 2023-11-05 | Y | 10 | (yyy),ssss,uuuu,vvvv,xxxx,yyyy,aaaaa,kkkkk,lllll | N |  |  | Integral Stainless Steel grooved spool between the #2 ck and #2 SOV - assembly length: min. 48 3/4" and max. 86"
RP | Wilkins | 375ASTRMS | 10 | H | 2014-11-05 | 2023-11-05 | Y | 10 | (yyy),ssss,uuuu,vvvv,xxxx,yyyy,aaaaa,kkkkk,lllll | N |  |  | Integral Stainless Steel grooved spool between the #2 ck and #2 SOV - assembly length: min. 52 5/8" and max. 100 5/8"
RP | Wilkins | 375ASTRW1 | 2.5 | H | 2019-01-16 | 2022-01-16 | Y | 10 | (yyy),ssss,uuuu,vvvv,xxxx,yyyy,aaaaa,kkkkk,lllll,gggggg,iiiiii,jjjjjj,llllll,mmmmmm,oooooo | N |  |  | Integral Stainless Steel grooved spool between the #2 ck and #2 SOV - assembly length: min. 31" and max. 47 1/8"
RP | Wilkins | 375ASTRW1 | 3 | H | 2019-01-16 | 2022-01-16 | Y | 10 | (yyy),ssss,uuuu,vvvv,xxxx,yyyy,aaaaa,kkkkk,lllll,gggggg,iiiiii,jjjjjj,llllll,mmmmmm,oooooo | N |  |  | Integral Stainless Steel grooved spool between the #2 ck and #2 SOV - assembly length: min. 31 1/2" and max. 48 1/8"
RP | Wilkins | 375ASTRW1 | 4 | H | 2019-01-16 | 2022-01-16 | Y | 10 | (yyy),ssss,uuuu,vvvv,xxxx,yyyy,aaaaa,kkkkk,lllll,gggggg,iiiiii,jjjjjj,llllll,mmmmmm,oooooo | N |  |  | Integral Stainless Steel grooved spool between the #2 ck and #2 SOV - assembly length: min. 32 5/8" and max. 62 1/4"
RP | Wilkins | 375ASTRW1 | 6 | H | 2019-01-16 | 2022-01-16 | Y | 10 | (yyy),ssss,uuuu,vvvv,xxxx,yyyy,aaaaa,kkkkk,lllll,gggggg,iiiiii,jjjjjj,llllll,mmmmmm,oooooo | N |  |  | Integral Stainless Steel grooved spool between the #2 ck and #2 SOV - assembly length: min. 39" and max. 71 1/4"
RP | Wilkins | 375ASTRW1 | 8 | H | 2019-04-25 | 2022-04-25 | Y | 10 | (yyy),ssss,uuuu,vvvv,xxxx,yyyy,aaaaa,kkkkk,lllll,gggggg,iiiiii,jjjjjj,llllll,mmmmmm,oooooo | N |  |  | Integral Stainless Steel grooved spool between the #2 ck and #2 SOV - assembly length: min. 48 3/4" and max. 86"
RP | Wilkins | 375ASTRW1 | 10 | H | 2019-04-25 | 2022-04-25 | Y | 10 | (yyy),ssss,uuuu,vvvv,xxxx,yyyy,aaaaa,kkkkk,lllll,gggggg,iiiiii,jjjjjj,llllll,mmmmmm,oooooo | N |  |  | Integral Stainless Steel grooved spool between the #2 ck and #2 SOV - assembly length: min. 52 5/8" and max. 100 5/8"
RP | Wilkins | 375ASTW1 | 2.5 | H | 2019-01-16 | 2022-01-16 | Y | 10 | (yyy),ssss,uuuu,vvvv,xxxx,yyyy,aaaaa,kkkkk,lllll,gggggg,iiiiii,jjjjjj,llllll,mmmmmm,oooooo | N
RP | Wilkins | 375ASTW1 | 3 | H | 2019-01-16 | 2022-01-16 | Y | 10 | (yyy),ssss,uuuu,vvvv,xxxx,yyyy,aaaaa,kkkkk,lllll,gggggg,iiiiii,jjjjjj,llllll,mmmmmm,oooooo | N
RP | Wilkins | 375ASTW1 | 4 | H | 2019-01-16 | 2022-01-16 | Y | 10 | (yyy),ssss,uuuu,vvvv,xxxx,yyyy,aaaaa,kkkkk,lllll,gggggg,iiiiii,jjjjjj,llllll,mmmmmm,oooooo | N
RP | Wilkins | 375ASTW1 | 6 | H | 2019-01-16 | 2022-01-16 | Y | 10 | (yyy),ssss,uuuu,vvvv,xxxx,yyyy,aaaaa,kkkkk,lllll,gggggg,iiiiii,jjjjjj,llllll,mmmmmm,oooooo | N
RP | Wilkins | 375ASTW1 | 8 | H | 2019-04-25 | 2022-04-25 | Y | 10 | (yyy),ssss,uuuu,vvvv,xxxx,yyyy,aaaaa,kkkkk,lllll,gggggg,iiiiii,jjjjjj,llllll,mmmmmm,oooooo | N
RP | Wilkins | 375ASTW1 | 10 | H | 2019-04-25 | 2022-04-25 | Y | 10 | (yyy),ssss,uuuu,vvvv,xxxx,yyyy,aaaaa,kkkkk,lllll,gggggg,iiiiii,jjjjjj,llllll,mmmmmm,oooooo | N
RP | Wilkins | 375AW1 | 2.5 | H | 2019-03-12 | 2022-03-12 | Y | 9 | (ppp),qqq,sss,ttt,www,yyy,zzz,dddd,eeee,ssss,uuuu,vvvv,xxxx,yyyy,aaaaa,kkkkk,lllll,gggggg,iiiiii,jjjjjj,llllll,mmmmmm,oooooo | N
RP | Wilkins | 375AW1 | 3 | H | 2019-03-12 | 2022-03-12 | Y | 9 | (ppp),qqq,sss,ttt,www,yyy,zzz,dddd,eeee,ssss,uuuu,vvvv,xxxx,yyyy,aaaaa,kkkkk,lllll,gggggg,iiiiii,jjjjjj,llllll,mmmmmm,oooooo | N
RP | Wilkins | 375AW1 | 4 | H | 2019-03-12 | 2022-03-12 | Y | 9 | (ppp),qqq,sss,ttt,www,yyy,zzz,dddd,eeee,ssss,uuuu,vvvv,xxxx,yyyy,aaaaa,kkkkk,lllll,gggggg,iiiiii,jjjjjj,llllll,mmmmmm,oooooo | N
RP | Wilkins | 375AW1 | 6 | H | 2019-03-12 | 2022-03-12 | Y | 9 | (ppp),qqq,sss,ttt,www,yyy,zzz,dddd,eeee,ssss,uuuu,vvvv,xxxx,yyyy,aaaaa,kkkkk,lllll,gggggg,iiiiii,jjjjjj,llllll,mmmmmm,oooooo | N
RP | Wilkins | 375AW1 | 8 | H | 2019-04-25 | 2022-04-25 | Y | 9 | (ppp),qqq,sss,ttt,www,yyy,ssss,uuuu,vvvv,xxxx,yyyy,aaaaa,kkkkk,lllll,gggggg,iiiiii,jjjjjj,llllll,mmmmmm,oooooo | N
RP | Wilkins | 375AW1 | 10 | H | 2019-04-25 | 2022-04-25 | Y | 9 | (ppp),qqq,sss,ttt,www,yyy,ssss,uuuu,vvvv,xxxx,yyyy,aaaaa,kkkkk,lllll,gggggg,iiiiii,jjjjjj,llllll,mmmmmm,oooooo | N
RP | Wilkins | 375B | 0.5 | H | 2012-11-08 | 2024-11-08 | N | 9 | (int) | N |  |  | Testcocks: Female Threaded End or 45 degree male SAE flare
RP | Wilkins | 375B | 0.75 | H | 2012-11-08 | 2024-11-08 | N | 9 | (int) | N |  |  | Testcocks: Female Threaded End or 45 degree male SAE flare
RP | Wilkins | 375B | 1 | H | 2012-11-08 | 2024-11-08 | N | 9 | (int) | N |  |  | Testcocks: Female Threaded End or 45 degree male SAE flare
RP | Wilkins | 375B | 1.25 | H | 2012-11-08 | 2024-11-08 | N | 9 | (int) | N
RP | Wilkins | 375B | 1.5 | H | 2012-11-08 | 2024-11-08 | N | 9 | (int) | N
RP | Wilkins | 375B | 2 | H | 2012-11-08 | 2024-11-08 | N | 9 | (int) | N
RP | Wilkins | 375MS | 2.5 | H | 2003-07-03 | 2024-07-03 | N | 9 | (gg),ee,ff,hh,ll,mm,tt,uu,yy,zz,ppp,qqq,zzz,dddd,ssss,tttt,vvvv,wwww,yyyy,zzzz,kkkkk | N |  |  | Up to serial number L61205
RP | Wilkins | 375MS | 2.5 | H | 2010-09-09 | 2022-09-09 | Y | 9 | (gg),hh,ppp,qqq,ssss,tttt,vvvv,wwww,yyyy,zzzz,kkkkk | N |  |  | Serial number L61205 and higher
RP | Wilkins | 375MS | 3 | H | 2003-07-03 | 2024-07-03 | N | 9 | (gg),ee,ff,hh,ll,mm,tt,uu,yy,zz,ppp,qqq,zzz,dddd,ssss,tttt,vvvv,wwww,yyyy,zzzz,kkkkk | N |  |  | Up to serial number L61205
RP | Wilkins | 375MS | 3 | H | 2010-09-09 | 2022-09-09 | Y | 9 | (gg),hh,ppp,qqq,ssss,tttt,vvvv,wwww,yyyy,zzzz,kkkkk | N |  |  | Serial number L61205 and higher
RP | Wilkins | 375MS | 4 | H | 2003-07-03 | 2024-07-03 | N | 9 | (gg),ee,ff,hh,ll,mm,tt,uu,yy,zz,ppp,qqq,vvv,www,zzz,dddd,eeee,ssss,tttt,vvvv,wwww,yyyy,zzzz,kkkkk | N |  |  | Up to serial number L61205
RP | Wilkins | 375MS | 4 | H | 2010-09-09 | 2022-09-09 | Y | 9 | (gg),hh,ppp,qqq,vvv,www,,ssss,tttt,vvvv,wwww,yyyy,zzzz,kkkkk | N |  |  | Serial number L61205 and higher
RP | Wilkins | 375MS | 6 | H | 2003-07-03 | 2024-07-03 | N | 9 | (gg),ee,ff,hh,ll,mm,tt,uu,yy,zz,ppp,qqq,vvv,www,zzz,dddd,eeee,ssss,tttt,vvvv,wwww,yyyy,zzzz,kkkkk | N |  |  | Up to serial number L61205
RP | Wilkins | 375MS | 6 | H | 2010-09-09 | 2022-09-09 | Y | 9 | (gg),hh,ppp,qqq,vvv,www,zzz,ssss,tttt,vvvv,wwww,yyyy,zzzz,kkkkk | N |  |  | Serial number L61205 and higher
RP | Wilkins | 375MS | 8 | H | 2003-07-03 | 2024-07-03 | N | 9 | (gg),ee,ff,hh,ll,mm,tt,uu,yy,zz,ppp,qqq,vvv,www,zzz,dddd,eeee,ssss,tttt,vvvv,wwww,yyyy,zzzz,kkkkk | N |  |  | Up to serial number L61205
RP | Wilkins | 375MS | 8 | H | 2010-09-09 | 2022-09-09 | Y | 9 | (gg),hh,ppp,qqq,vvv,www,ssss,tttt,vvvv,wwww,yyyy,zzzz,kkkkk | N |  |  | Serial number L61205 and higher
RP | Wilkins | 375MS | 10 | H | 2005-03-29 | 2023-03-29 | N | 9 | (gg),ee,ff,hh,ll,mm,tt,uu,yy,zz,ppp,qqq,vvv,www,zzz,dddd,eeee,ssss,tttt,vvvv,wwww,yyyy,zzzz,kkkkk | N |  |  | Up to serial number L61205
RP | Wilkins | 375MS | 10 | H | 2010-09-09 | 2022-09-09 | Y | 9 | (gg),hh,ppp,qqq,vvv,www,ssss,tttt,vvvv,wwww,yyyy,zzzz,kkkkk | N |  |  | Serial number L61205 and higher
RP | Wilkins | 375ST | 0.5 | H | 2011-02-22 | 2023-02-22 | Y | 9 | (int) | N
RP | Wilkins | 375ST | 0.75 | H | 2011-02-22 | 2023-02-22 | Y | 9 | (int) | N
RP | Wilkins | 375ST | 1 | H | 2011-10-31 | 2023-10-31 | Y | 9 | int | N
RP | Wilkins | 375W1 | 2.5 | H | 2019-03-12 | 2022-03-12 | Y | 9 | (gg),hh,ppp,qqq,ssss,tttt,vvvv,wwww,yyyy,zzzz,kkkkk,gggggg,hhhhhh,jjjjjj,kkkkkk,mmmmmm,nnnnnn | N
RP | Wilkins | 375W1 | 3 | H | 2019-03-12 | 2022-03-12 | Y | 9 | (gg),hh,ppp,qqq,ssss,tttt,vvvv,wwww,yyyy,zzzz,kkkkk,gggggg,hhhhhh,jjjjjj,kkkkkk,mmmmmm,nnnnnn | N
RP | Wilkins | 375W1 | 4 | H | 2019-03-12 | 2022-03-12 | Y | 9 | (gg),hh,ppp,qqq,ssss,tttt,vvvv,wwww,yyyy,zzzz,kkkkk,gggggg,hhhhhh,jjjjjj,kkkkkk,mmmmmm,nnnnnn | N
RP | Wilkins | 375W1 | 6 | H | 2019-03-12 | 2022-03-12 | Y | 9 | (gg),hh,ppp,qqq,ssss,tttt,vvvv,wwww,yyyy,zzzz,kkkkk,gggggg,hhhhhh,jjjjjj,kkkkkk,mmmmmm,nnnnnn | N
RP | Wilkins | 375W1 | 8 | H | 2019-04-25 | 2022-04-25 | Y | 9 | (gg),hh,ppp,qqq,vvv,www,ssss,tttt,vvvv,wwww,yyyy,zzzz,kkkkk,gggggg,hhhhhh,jjjjjj,kkkkkk,mmmmmm,nnnnnn | N
RP | Wilkins | 375W1 | 10 | H | 2019-04-25 | 2022-04-25 | Y | 9 | (gg),hh,ppp,qqq,vvv,www,ssss,tttt,vvvv,wwww,yyyy,zzzz,kkkkk,gggggg,hhhhhh,jjjjjj,kkkkkk,mmmmmm,nnnnnn | N
RP | Wilkins | 375XL | 0.5 | H | 2009-04-07 | 2024-04-07 | Y | 9 | (int) | N |  |  | Testcocks: Female Threaded End or 45 degree male SAE flare
RP | Wilkins | 375XL | 0.75 | H | 2007-03-09 | 2022-03-09 | Y | 9 | (int) | N |  |  | Testcocks: Female Threaded End or 45 degree male SAE flare
RP | Wilkins | 375XL | 1 | H | 2007-03-09 | 2022-03-09 | Y | 9 | (int) | N |  |  | Testcocks: Female Threaded End or 45 degree male SAE flare
RP | Wilkins | 375XL | 1.25 | H | 2010-04-20 | 2022-04-20 | Y | 9 | (int) | N
RP | Wilkins | 375XL | 1.5 | H | 2010-04-20 | 2022-04-20 | Y | 9 | (int) | N
RP | Wilkins | 375XL | 2 | H | 2010-04-20 | 2022-04-20 | Y | 9 | (int) | N
RP | Wilkins | 375XLB | 0.5 | H | 2012-11-08 | 2024-11-08 | Y | 9 | (int) | N |  |  | Testcocks: Female Threaded End or 45 degree male SAE flare
RP | Wilkins | 375XLB | 0.75 | H | 2012-11-08 | 2024-11-08 | Y | 9 | (int) | N |  |  | Testcocks: Female Threaded End or 45 degree male SAE flare
RP | Wilkins | 375XLB | 1 | H | 2012-11-08 | 2024-11-08 | Y | 9 | (int) | N |  |  | Testcocks: Female Threaded End or 45 degree male SAE flare
RP | Wilkins | 375XLB | 1.25 | H | 2012-11-08 | 2024-11-08 | Y | 9 | (int) | N
RP | Wilkins | 375XLB | 1.5 | H | 2012-11-08 | 2024-11-08 | Y | 9 | (int) | N
RP | Wilkins | 375XLB | 2 | H | 2012-11-08 | 2024-11-08 | Y | 9 | (int) | N
RP | Wilkins | 475MS | 2.5 | VUVD | 2003-07-03 | 2024-07-03 | N | 9 | (gg),ee,ff,hh,ll,mm,tt,uu,yy,zz,ppp,qqq,zzz,dddd,ssss,uuuu,vvvv,xxxx,yyyy,aaaaa,kkkkk | N |  |  | Up to serial number Q05664
RP | Wilkins | 475MS | 2.5 | VUVD | 2010-09-09 | 2022-09-09 | Y | 9 | (gg),hh,ppp,qqq,ssss,uuuu,vvvv,xxxx,yyyy,aaaaa,kkkkk | N |  |  | Serial number Q05664 and higher
RP | Wilkins | 475MS | 3 | VUVD | 2003-07-03 | 2024-07-03 | N | 9 | (gg),ee,ff,hh,ll,mm,tt,uu,yy,zz,ppp,qqq,zzz,dddd,ssss,uuuu,vvvv,xxxx,yyyy,aaaaa,kkkkk,lllll | N |  |  | Up to serial number Q05664
RP | Wilkins | 475MS | 3 | VUVD | 2010-09-09 | 2022-09-09 | Y | 9 | (gg),hh,ppp,qqq,ssss,uuuu,vvvv,xxxx,yyyy,aaaaa,kkkkk,lllll | N |  |  | Serial number Q05664 and higher
RP | Wilkins | 475MS | 4 | VUVD | 2003-07-03 | 2024-07-03 | N | 9 | (ppp),qqq,sss,ttt,www,yyy,zzz,dddd,eeee,ssss,uuuu,vvvv,xxxx,yyyy,aaaaa,kkkkk,lllll | N |  |  | Up to serial number Q05664
RP | Wilkins | 475MS | 4 | VUVD | 2010-09-09 | 2022-09-09 | Y | 9 | (ppp),qqq,sss,ttt,www,yyy,ssss,uuuu,vvvv,xxxx,yyyy,aaaaa,kkkkk,lllll | N |  |  | Serial number Q05664 and higher
RP | Wilkins | 475MS | 6 | VUVD | 2003-07-03 | 2024-07-03 | N | 9 | (ppp),qqq,sss,ttt,www,yyy,zzz,dddd,eeee,ssss,uuuu,vvvv,xxxx,yyyy,aaaaa,kkkkk,lllll | N |  |  | Up to serial number Q05664
RP | Wilkins | 475MS | 6 | VUVD | 2010-09-09 | 2022-09-09 | Y | 9 | (ppp),qqq,sss,ttt,www,yyy,ssss,uuuu,vvvv,xxxx,yyyy,aaaaa,kkkkk,lllll | N |  |  | Serial number Q05664 and higher
RP | Wilkins | 475MS | 8 | VUVD | 2003-07-03 | 2024-07-03 | N | 9 | (ppp),qqq,sss,ttt,www,yyy,zzz,dddd,eeee,ssss,uuuu,vvvv,xxxx,yyyy,aaaaa,kkkkk,lllll | N |  |  | Up to serial number Q05664
RP | Wilkins | 475MS | 8 | VUVD | 2010-09-09 | 2022-09-09 | Y | 9 | (ppp),qqq,sss,ttt,www,yyy,ssss,uuuu,vvvv,xxxx,yyyy,aaaaa,kkkkk,lllll | N |  |  | Serial number Q05664 and higher
RP | Wilkins | 475MS | 10 | H | 2005-03-29 | 2023-03-29 | N | 9 | (ppp),qqq,sss,ttt,www,zzz,dddd,eeee,ssss,uuuu,vvvv,xxxx,yyyy,aaaaa,kkkkk,lllll | N |  |  | Up to serial number Q05664
RP | Wilkins | 475MS | 10 | H | 2010-09-09 | 2022-09-09 | Y | 9 | (ppp),qqq,sss,ttt,www,ssss,uuuu,vvvv,xxxx,yyyy,aaaaa,kkkkk,lllll | N |  |  | Serial number Q05664 and higher
RP | Wilkins | 475ST | 4 | VUVD | 2018-12-18 | 2024-12-18 | Y | 10 | (kkkkk),yyy,ssss,uuuu,vvvv,xxxx,yyyy,aaaaa,lllll,gggggg,iiiiii,jjjjjj,llllll,mmmmmm,oooooo | N
RP | Wilkins | 475ST | 4 | VUVU | 2018-12-18 | 2024-12-18 | Y | 10 | (kkkkk),yyy,ssss,uuuu,vvvv,xxxx,yyyy,aaaaa,lllll,gggggg,iiiiii,jjjjjj,llllll,mmmmmm,oooooo | N
RP | Wilkins | 475ST | 6 | VUVD | 2018-12-18 | 2024-12-18 | Y | 10 | (kkkkk),yyy,ssss,uuuu,vvvv,xxxx,yyyy,aaaaa,lllll,gggggg,iiiiii,jjjjjj,llllll,mmmmmm,oooooo | N
RP | Wilkins | 475ST | 6 | VUVU | 2018-12-18 | 2024-12-18 | Y | 10 | (kkkkk),yyy,ssss,uuuu,vvvv,xxxx,yyyy,aaaaa,lllll,gggggg,iiiiii,jjjjjj,llllll,mmmmmm,oooooo | N
RP | Wilkins | 475ST | 8 | VUVD | 2018-12-18 | 2024-12-18 | Y | 10 | (kkkkk),yyy,ssss,uuuu,vvvv,xxxx,yyyy,aaaaa,lllll,gggggg,iiiiii,jjjjjj,llllll,mmmmmm,oooooo | N
RP | Wilkins | 475ST | 8 | VUVU | 2018-12-18 | 2024-12-18 | Y | 10 | (kkkkk),yyy,ssss,uuuu,vvvv,xxxx,yyyy,aaaaa,lllll,gggggg,iiiiii,jjjjjj,llllll,mmmmmm,oooooo | N
RP | Wilkins | 475ST | 10 | VUVD | 2018-12-18 | 2024-12-18 | Y | 10 | (kkkkk),yyy,ssss,uuuu,vvvv,xxxx,yyyy,aaaaa,lllll,gggggg,iiiiii,jjjjjj,llllll,mmmmmm,oooooo | N
RP | Wilkins | 475ST | 10 | VUVU | 2018-12-18 | 2024-12-18 | Y | 10 | (kkkkk),yyy,ssss,uuuu,vvvv,xxxx,yyyy,aaaaa,lllll,gggggg,iiiiii,jjjjjj,llllll,mmmmmm,oooooo | N
RP | Wilkins | 475STR | 4 | VUVD | 2018-12-18 | 2024-12-18 | Y | 10 | (kkkkk),yyy,ssss,uuuu,vvvv,xxxx,yyyy,aaaaa,lllll,gggggg,iiiiii,jjjjjj,llllll,mmmmmm,oooooo | N
RP | Wilkins | 475STR | 4 | VUVU | 2018-12-18 | 2024-12-18 | Y | 10 | (kkkkk),yyy,ssss,uuuu,vvvv,xxxx,yyyy,aaaaa,lllll,gggggg,iiiiii,jjjjjj,llllll,mmmmmm,oooooo | N
RP | Wilkins | 475STR | 6 | VUVD | 2018-12-18 | 2024-12-18 | Y | 10 | (kkkkk),yyy,ssss,uuuu,vvvv,xxxx,yyyy,aaaaa,lllll,gggggg,iiiiii,jjjjjj,llllll,mmmmmm,oooooo | N
RP | Wilkins | 475STR | 6 | VUVU | 2018-12-18 | 2024-12-18 | Y | 10 | (kkkkk),yyy,ssss,uuuu,vvvv,xxxx,yyyy,aaaaa,lllll,gggggg,iiiiii,jjjjjj,llllll,mmmmmm,oooooo | N
RP | Wilkins | 475STR | 8 | VUVD | 2018-12-18 | 2024-12-18 | Y | 10 | (kkkkk),yyy,ssss,uuuu,vvvv,xxxx,yyyy,aaaaa,lllll,gggggg,iiiiii,jjjjjj,llllll,mmmmmm,oooooo | N
RP | Wilkins | 475STR | 8 | VUVU | 2018-12-18 | 2024-12-18 | Y | 10 | (kkkkk),yyy,ssss,uuuu,vvvv,xxxx,yyyy,aaaaa,lllll,gggggg,iiiiii,jjjjjj,llllll,mmmmmm,oooooo | N
RP | Wilkins | 475STR | 10 | VUVD | 2018-12-18 | 2024-12-18 | Y | 10 | (kkkkk),yyy,ssss,uuuu,vvvv,xxxx,yyyy,aaaaa,lllll,gggggg,iiiiii,jjjjjj,llllll,mmmmmm,oooooo | N
RP | Wilkins | 475STR | 10 | VUVU | 2018-12-18 | 2024-12-18 | Y | 10 | (kkkkk),yyy,ssss,uuuu,vvvv,xxxx,yyyy,aaaaa,lllll,gggggg,iiiiii,jjjjjj,llllll,mmmmmm,oooooo | N
RP | Wilkins | 475V | 2.5 | VUVU | 2002-01-24 | 2023-01-24 | N | 9 | (gg),ee,ff,hh,ll,mm,tt,uu,yy,zz,ppp,qqq,zzz,dddd,ssss,tttt,vvvv,wwww,yyyy,zzzz,kkkkk,gggggg,hhhhhh,jjjjjj,kkkkkk,mmmmmm,nnnnnn | N |  |  | Up to serial number Q05664
RP | Wilkins | 475V | 2.5 | VUVU | 2010-09-09 | 2022-09-09 | Y | 9 | (gg),hh,ppp,qqq,ssss,tttt,vvvv,wwww,yyyy,zzzz,kkkkk,gggggg,hhhhhh,jjjjjj,kkkkkk,mmmmmm,nnnnnn | N |  |  | Serial number Q05664 and higher
RP | Wilkins | 475V | 3 | VUVU | 2002-01-24 | 2023-01-24 | N | 9 | (gg),ee,ff,hh,ll,mm,tt,uu,yy,zz,ppp,qqq,zzz,dddd,ssss,tttt,vvvv,wwww,yyyy,zzzz,kkkkk,gggggg,hhhhhh,jjjjjj,kkkkkk,mmmmmm,nnnnnn,lllll | N |  |  | Up to serial number Q05664
RP | Wilkins | 475V | 3 | VUVU | 2010-09-09 | 2022-09-09 | Y | 9 | (gg),hh,ppp,qqq,ssss,tttt,vvvv,wwww,yyyy,zzzz,kkkkk,gggggg,hhhhhh,jjjjjj,kkkkkk,mmmmmm,nnnnnn,lllll | N |  |  | Serial number Q05664 and higher
RP | Wilkins | 475V | 4 | VUVU | 2000-09-09 | 2024-09-09 | N | 9 | (ppp),qqq,sss,ttt,www,yyy,zzz,dddd,eeee,ssss,uuuu,vvvv,xxxx,yyyy,aaaaa,kkkkk,lllll,gggggg,iiiiii,jjjjjj,llllll,mmmmmm,oooooo | N |  |  | Up to serial number Q05664
RP | Wilkins | 475V | 4 | VUVU | 2010-09-09 | 2022-09-09 | Y | 9 | (ppp),qqq,sss,ttt,www,yyy,ssss,uuuu,vvvv,xxxx,yyyy,aaaaa,kkkkk,lllll,gggggg,iiiiii,jjjjjj,llllll,mmmmmm,oooooo | N |  |  | Serial number Q05664 and higher
RP | Wilkins | 475V | 6 | VUVU | 2001-05-31 | 2022-05-31 | N | 9 | (ppp),qqq,sss,ttt,www,yyy,zzz,dddd,eeee,ssss,uuuu,vvvv,xxxx,yyyy,aaaaa,kkkkk,lllll,gggggg,iiiiii,jjjjjj,llllll,mmmmmm,oooooo | N |  |  | Up to serial number Q05664
RP | Wilkins | 475V | 6 | VUVU | 2010-09-09 | 2022-09-09 | Y | 9 | (ppp),qqq,sss,ttt,www,yyy,ssss,uuuu,vvvv,xxxx,yyyy,aaaaa,kkkkk,lllll,gggggg,iiiiii,jjjjjj,llllll,mmmmmm,oooooo | N |  |  | Serial number Q05664 and higher
RP | Wilkins | 475V | 8 | VUVU | 2004-06-08 | 2022-06-08 | N | 9 | (ppp),qqq,sss,ttt,www,yyy,zzz,dddd,eeee,ssss,uuuu,vvvv,xxxx,yyyy,aaaaakkkkk,lllll,gggggg,iiiiii,jjjjjj,llllll,mmmmmm,oooooo | N |  |  | Up to serial number Q05664
RP | Wilkins | 475V | 8 | VUVU | 2010-09-09 | 2022-09-09 | Y | 9 | (ppp),qqq,sss,ttt,www,yyy,ssss,uuuu,vvvv,xxxx,yyyy,aaaaa,kkkkk,lllll,gggggg,iiiiii,jjjjjj,llllll,mmmmmm,oooooo | N |  |  | Serial number Q05664 and higher
RP | Wilkins | 475V | 10 | VUVU | 2004-11-22 | 2022-11-22 | N | 9 | (ppp),qqq,sss,ttt,www,zzz,dddd,eeee,ssss,uuuu,vvvv,xxxx,yyyy,aaaaa,kkkkk,lllll,gggggg,iiiiii,jjjjjj,llllll,mmmmmm,oooooo | N |  |  | Up to serial number Q05664
RP | Wilkins | 475V | 10 | VUVU | 2010-09-09 | 2022-09-09 | Y | 9 | (ppp),qqq,sss,ttt,www,ssss,uuuu,vvvv,xxxx,yyyy,aaaaa,kkkkk,lllll,gggggg,iiiiii,jjjjjj,llllll,mmmmmm,oooooo | N |  |  | Serial number Q05664 and higher
RP | Wilkins | 475VMS | 2.5 | VUVU | 2003-07-03 | 2024-07-03 | N | 9 | (gg),ee,ff,hh,ll,mm,tt,uu,yy,zz,ppp,qqq,zzz,dddd,ssss,uuuu,vvvv,xxxx,yyyy,aaaaa,kkkkk | N |  |  | Up to serial number Q05664
RP | Wilkins | 475VMS | 2.5 | VUVU | 2010-09-09 | 2022-09-09 | Y | 9 | (gg),hh,ppp,qqq,ssss,uuuu,vvvv,xxxx,yyyy,aaaaa,kkkkk | N |  |  | Serial number Q05664 and higher
RP | Wilkins | 475VMS | 3 | VUVU | 2003-07-03 | 2024-07-03 | N | 9 | (gg),ee,ff,hh,ll,mm,tt,uu,yy,zz,ppp,qqq,zzz,dddd,ssss,uuuu,vvvv,xxxx,yyyy,aaaaa,kkkkk,lllll | N |  |  | Up to serial number Q05664
RP | Wilkins | 475VMS | 3 | VUVU | 2010-09-09 | 2022-09-09 | Y | 9 | (gg),hh,ppp,qqq,ssss,uuuu,vvvv,xxxx,yyyy,aaaaa,kkkkk,lllll | N |  |  | Serial number Q05664 and higher
RP | Wilkins | 475VMS | 4 | VUVU | 2003-07-03 | 2024-07-03 | N | 9 | (ppp),qqq,sss,ttt,www,yyy,zzz,dddd,eeee,ssss,uuuu,vvvv,xxxx,yyyy,aaaaa,kkkkk,lllll | N |  |  | Up to serial number Q05664
RP | Wilkins | 475VMS | 4 | VUVU | 2010-09-09 | 2022-09-09 | Y | 9 | (ppp),qqq,sss,ttt,www,yyy,ssss,uuuu,vvvv,xxxx,yyyy,aaaaa,kkkkk,lllll | N |  |  | Serial number Q05664 and higher
RP | Wilkins | 475VMS | 6 | VUVU | 2003-07-03 | 2024-07-03 | N | 9 | (ppp),qqq,sss,ttt,www,yyy,zzz,dddd,eeee,ssss,uuuu,vvvv,xxxx,yyyy,aaaaa,kkkkk,lllll | N |  |  | Up to serial number Q05664
RP | Wilkins | 475VMS | 6 | VUVU | 2010-09-09 | 2022-09-09 | Y | 9 | (ppp),qqq,sss,ttt,www,yyy,ssss,uuuu,vvvv,xxxx,yyyy,aaaaa,kkkkk,lllll | N |  |  | Serial number Q05664 and higher
RP | Wilkins | 475VMS | 8 | VUVU | 2003-07-03 | 2024-07-03 | N | 9 | (ppp),qqq,sss,ttt,www,yyy,zzz,dddd,eeee,ssss,uuuu,vvvv,xxxx,yyyy,aaaaa,kkkkk,lllll | N |  |  | Up to serial number Q05664
RP | Wilkins | 475VMS | 8 | VUVU | 2010-09-09 | 2022-09-09 | Y | 9 | (ppp),qqq,sss,ttt,www,yyy,ssss,uuuu,vvvv,xxxx,yyyy,aaaaa,kkkkk,lllll | N |  |  | Serial number Q05664 and higher
RP | Wilkins | 475VMS | 10 | H | 2005-03-29 | 2023-03-29 | N | 9 | (ppp),qqq,sss,ttt,www,zzz,dddd,eeee,ssss,uuuu,vvvv,xxxx,yyyy,aaaaa,kkkkk,lllll | N |  |  | Up to serial number Q05664
RP | Wilkins | 475VMS | 10 | H | 2010-09-09 | 2022-09-09 | Y | 9 | (ppp),qqq,sss,ttt,www,ssss,uuuu,vvvv,xxxx,yyyy,aaaaa,kkkkk,lllll | N |  |  | Serial number Q05664 and higher
RP | Wilkins | 575 | 2.5 | H | 1986-09-25 | 2022-09-25 | N | 7 | gg,ee,tt,yy | Y
RP | Wilkins | 575 (MOD-III) | 1.25 | H | 1976-10-11 | 2024-10-11 | N | 5 | ii | Y
RP | Wilkins | 575 (MOD-III) | 1.5 | H | 1976-10-11 | 2024-10-11 | N | 5 | ii | Y
RP | Wilkins | 575 (MOD-III) | 2 | H | 1976-10-11 | 2024-10-11 | N | 5 | ii | Y
RP | Wilkins | 575A | 0.75 | H | 1987-04-17 | 2023-04-17 | N | 7 | ii | Y
RP | Wilkins | 575A | 1 | H | 1987-04-17 | 2023-04-17 | N | 7 | ii | Y
RP | Wilkins | 575M10 | 10 | H | 1983-06-01 | 2022-06-01 | N | 6 | gg,ee,tt,yy | Y |  |  | 6"x6"x10" manifold, formerly MBC-10"
RP | Wilkins | 575M8 | 8 | H | 1983-04-11 | 2022-04-11 | N | 6 | gg,ee,tt,yy | Y |  |  | 4"x4"x8" manifold, formerly MBC-8"
RP | Wilkins | 975 | 0.75 | H | 1991-07-18 | 2024-07-18 | N | 8 | ii | Y
RP | Wilkins | 975 | 1 | H | 1991-07-18 | 2024-07-18 | N | 8 | ii | Y
RP | Wilkins | 975 | 1.25 | H | 1991-07-18 | 2024-07-18 | N | 8 | ii | Y
RP | Wilkins | 975 | 1.5 | H | 1991-07-18 | 2024-07-18 | N | 8 | ii | Y
RP | Wilkins | 975 | 2 | H | 1991-07-18 | 2024-07-18 | N | 8 | ii | Y
RP | Wilkins | 975 | 2.5 | H | 1991-11-26 | 2024-11-26 | N | 8 | gg,ee,ff,hh,tt,uu,yy,zz,ssss,tttt,vvvv,wwww,yyyy,zzzz | Y
RP | Wilkins | 975 | 3 | H | 1991-11-08 | 2024-11-08 | N | 8 | gg,ee,ff,hh,tt,uu,yy,zz,ssss,tttt,vvvv,wwww,yyyy,zzzz | Y
RP | Wilkins | 975 | 4 | H | 1991-11-08 | 2024-11-08 | N | 8 | gg,ee,ff,hh,tt,uu,yy,zz,ppp,ssss,tttt,vvvv,wwww,yyyy,zzzz | Y
RP | Wilkins | 975 | 6 | H | 1991-11-08 | 2024-11-08 | N | 8 | gg,ee,ff,hh,tt,uu,yy,zz,ppp,ssss,tttt,vvvv,wwww,yyyy,zzzz | Y
RP | Wilkins | 975A | 0.75 | H | 1991-07-18 | 2024-07-18 | N | 8 | ii | Y
RP | Wilkins | 975A | 1 | H | 1991-07-18 | 2024-07-18 | N | 8 | ii | Y
RP | Wilkins | 975A | 1.25 | H | 1991-07-18 | 2024-07-18 | N | 8 | ii | Y
RP | Wilkins | 975A | 1.5 | H | 1991-07-18 | 2024-07-18 | N | 8 | ii | Y
RP | Wilkins | 975A | 2 | H | 1991-07-18 | 2024-07-18 | N | 8 | ii | Y
RP | Wilkins | 975BMS | 2.5 | H | 1997-06-17 | 2024-06-17 | N | 8 | (gg),ee,ff,hh,tt,uu,yy,zz,ssss,tttt,vvvv,wwww,yyyy,zzzz | Y
RP | Wilkins | 975BMS | 3 | H | 1997-06-17 | 2024-06-17 | N | 8 | (gg),ee,ff,hh,tt,uu,yy,zz,ssss,tttt,vvvv,wwww,yyyy,zzzz | Y
RP | Wilkins | 975BMS | 4 | H | 1997-06-17 | 2024-06-17 | N | 8 | gg,ee,ff,hh,tt,uu,yy,zz,ssss,tttt,vvvv,wwww,yyyy,zzzz | Y
RP | Wilkins | 975BMS | 6 | H | 1997-06-17 | 2024-06-17 | N | 8 | gg,ee,ff,hh,tt,uu,yy,zz,ssss,tttt,vvvv,wwww,yyyy,zzzz | Y
RP | Wilkins | 975BMS | 8 | H | 1997-06-17 | 2024-06-17 | N | 8 | (gg),ee,ff,hh,tt,uu,yy,zz,ppp,ssss,tttt,vvvv,wwww,yyyy,zzzz | Y
RP | Wilkins | 975BMS | 10 | H | 1997-06-17 | 2024-06-17 | N | 8 | (gg),ee,ff,hh,tt,uu,yy,zz,ppp,ssss,tttt,vvvv,wwww,yyyy,zzzz | Y
RP | Wilkins | 975MS | 2.5 | H | 1995-05-05 | 2022-05-05 | N | 8 | (gg),ee,ff,hh,tt,uu,yy,zz,ssss,tttt,vvvv,wwww,yyyy,zzzz | Y
RP | Wilkins | 975MS | 3 | H | 1995-05-05 | 2022-05-05 | N | 8 | (gg),ee,ff,hh,tt,uu,yy,zz,ssss,tttt,vvvv,wwww,yyyy,zzzz | Y
RP | Wilkins | 975MS | 4 | H | 1995-05-05 | 2022-05-05 | N | 8 | gg,ee,ff,hh,tt,uu,yy,zz,ssss,tttt,vvvv,wwww,yyyy,zzzz | Y
RP | Wilkins | 975MS | 6 | H | 1995-05-05 | 2022-05-05 | N | 8 | gg,ee,ff,hh,tt,uu,yy,zz,ssss,tttt,vvvv,wwww,yyyy,zzzz | Y
RP | Wilkins | 975MS | 8 | H | 1996-12-05 | 2023-12-05 | N | 8 | (gg),ee,ff,hh,tt,uu,yy,zz,ppp,ssss,tttt,vvvv,wwww,yyyy,zzzz | Y
RP | Wilkins | 975MS | 10 | H | 1996-12-05 | 2023-12-05 | N | 8 | (gg),ee,ff,hh,tt,uu,yy,zz,ppp,ssss,tttt,vvvv,wwww,yyyy,zzzz | Y
RP | Wilkins | 975XL | 0.25 | H | 1994-07-12 | 2024-07-12 | N | 8 | (ii) | N |  |  | Testcocks: Female Threaded End or 45 degree male SAE flare
RP | Wilkins | 975XL | 0.375 | H | 1994-07-12 | 2024-07-12 | N | 8 | (ii) | N |  |  | Testcocks: Female Threaded End or 45 degree male SAE flare
RP | Wilkins | 975XL | 0.5 | H | 1994-07-12 | 2024-07-12 | N | 8 | (ii) | N |  |  | Testcocks: Female Threaded End or 45 degree male SAE flare
RP | Wilkins | 975XL | 0.75 | H | 1992-11-02 | 2022-11-02 | N | 8 | (ii),ooo | N |  |  | Testcocks: Female Threaded End or 45 degree male SAE flare
RP | Wilkins | 975XL | 1 | H | 1992-11-02 | 2022-11-02 | N | 8 | (ii),ooo | N |  |  | Testcocks: Female Threaded End or 45 degree male SAE flare
RP | Wilkins | 975XL | 1.25 | H | 1992-11-02 | 2022-11-02 | N | 8 | (ii),ooo,ggg | N
RP | Wilkins | 975XL | 1.5 | H | 1992-11-02 | 2022-11-02 | N | 8 | (ii),ooo | N
RP | Wilkins | 975XL | 2 | H | 1992-11-02 | 2022-11-02 | N | 8 | (ii),bbb,ooo,bbbbb,ccccc,pppppp | N
RP | Wilkins | 975XL2 | 0.25 | H | 2009-10-01 | 2024-10-01 | Y | 8 | (iiii) | N |  |  | Testcocks: Female Threaded End or 45 degree male SAE flare
RP | Wilkins | 975XL2 | 0.375 | H | 2009-10-01 | 2024-10-01 | Y | 8 | (iiii) | N |  |  | Testcocks: Female Threaded End or 45 degree male SAE flare
RP | Wilkins | 975XL2 | 0.5 | H | 2009-10-01 | 2024-10-01 | Y | 8 | (iiii) | N |  |  | Testcocks: Female Threaded End or 45 degree male SAE flare
RP | Wilkins | 975XL2 | 0.75 | H | 2009-07-29 | 2024-07-29 | Y | 8 | (iiii) | N |  |  | Testcocks: Female Threaded End or 45 degree male SAE flare
RP | Wilkins | 975XL2 | 1 | H | 2009-07-29 | 2024-07-29 | Y | 8 | (iiii) | N |  |  | Testcocks: Female Threaded End or 45 degree male SAE flare
RP | Wilkins | 975XL2 | 1.25 | H | 2009-08-21 | 2024-08-21 | Y | 8 | (iiii) | N
RP | Wilkins | 975XL2 | 1.5 | H | 2009-08-21 | 2024-08-21 | Y | 8 | (iiii) | N
RP | Wilkins | 975XL2 | 2 | H | 2009-08-21 | 2024-08-21 | Y | 8 | (iiii),pppppp | N
RP | Wilkins | 975XL2BMS | 0.75 | H | 2010-09-09 | 2022-09-09 | Y | 8 | (iiii) | N
RP | Wilkins | 975XL2BMS | 1 | H | 2010-09-09 | 2022-09-09 | Y | 8 | (iiii) | N
RP | Wilkins | 975XL2BMS | 1.25 | H | 2010-09-09 | 2022-09-09 | Y | 8 | (iiii) | N
RP | Wilkins | 975XL2BMS | 1.5 | H | 2010-09-09 | 2022-09-09 | Y | 8 | (iiii) | N
RP | Wilkins | 975XL2BMS | 2 | H | 2010-09-09 | 2022-09-09 | Y | 8 | (iiii) | N
RP | Wilkins | 975XL2MS | 0.75 | H | 2010-09-09 | 2022-09-09 | Y | 8 | (iiii) | N |  |  | Testcocks: Female Threaded End or 45 degree male SAE flare
RP | Wilkins | 975XL2MS | 1 | H | 2010-09-09 | 2022-09-09 | Y | 8 | (iiii) | N |  |  | Testcocks: Female Threaded End or 45 degree male SAE flare
RP | Wilkins | 975XL2MS | 1.25 | H | 2010-09-09 | 2022-09-09 | Y | 8 | (iiii) | N
RP | Wilkins | 975XL2MS | 1.5 | H | 2010-09-09 | 2022-09-09 | Y | 8 | (iiii) | N
RP | Wilkins | 975XL2MS | 2 | H | 2010-09-09 | 2022-09-09 | Y | 8 | (iiii) | N
RP | Wilkins | 975XL2SE | 0.75 | VUVD | 2011-02-22 | 2023-02-22 | Y | 9 | (iiii) | N |  |  | Testcocks: Female Threaded End or 45 degree male SAE flare
RP | Wilkins | 975XL2SE | 0.75 | VUVU | 2011-02-22 | 2023-02-22 | Y | 9 | (iiii) | N |  |  | Testcocks: Female Threaded End or 45 degree male SAE flare
RP | Wilkins | 975XL2SE | 1 | VUVD | 2011-02-22 | 2023-02-22 | Y | 9 | (iiii) | N |  |  | Testcocks: Female Threaded End or 45 degree male SAE flare
RP | Wilkins | 975XL2SE | 1 | VUVU | 2011-02-22 | 2023-02-22 | Y | 9 | (iiii) | N |  |  | Testcocks: Female Threaded End or 45 degree male SAE flare
RP | Wilkins | 975XL2SE | 1.25 | VUVD | 2011-02-22 | 2023-02-22 | Y | 9 | (iiii) | N
RP | Wilkins | 975XL2SE | 1.25 | VUVU | 2011-02-22 | 2023-02-22 | Y | 9 | (iiii) | N
RP | Wilkins | 975XL2SE | 1.5 | VUVD | 2011-02-22 | 2023-02-22 | Y | 9 | (iiii) | N
RP | Wilkins | 975XL2SE | 1.5 | VUVU | 2011-02-22 | 2023-02-22 | Y | 9 | (iiii) | N
RP | Wilkins | 975XL2SE | 2 | VUVD | 2011-02-22 | 2023-02-22 | Y | 9 | (iiii) | N
RP | Wilkins | 975XL2SE | 2 | VUVU | 2011-02-22 | 2023-02-22 | Y | 9 | (iiii) | N
RP | Wilkins | 975XL2SEU | 0.75 | VUVD | 2011-03-29 | 2023-03-29 | Y | 9 | (mmmmm) | N |  |  | Testcocks: Female Threaded End or 45 degree male SAE flare
RP | Wilkins | 975XL2SEU | 0.75 | VUVU | 2011-03-29 | 2023-03-29 | Y | 9 | (mmmmm) | N |  |  | Testcocks: Female Threaded End or 45 degree male SAE flare
RP | Wilkins | 975XL2SEU | 1 | VUVD | 2011-03-29 | 2023-03-29 | Y | 9 | (mmmmm) | N |  |  | Testcocks: Female Threaded End or 45 degree male SAE flare
RP | Wilkins | 975XL2SEU | 1 | VUVU | 2011-03-29 | 2023-03-29 | Y | 9 | (mmmmm) | N |  |  | Testcocks: Female Threaded End or 45 degree male SAE flare
RP | Wilkins | 975XL2SEU | 1.25 | VUVD | 2011-02-22 | 2023-02-22 | Y | 9 | (mmmmm) | N
RP | Wilkins | 975XL2SEU | 1.25 | VUVU | 2011-02-22 | 2023-02-22 | Y | 9 | (mmmmm) | N
RP | Wilkins | 975XL2SEU | 1.5 | VUVD | 2011-02-22 | 2023-02-22 | Y | 9 | (mmmmm) | N
RP | Wilkins | 975XL2SEU | 1.5 | VUVU | 2011-02-22 | 2023-02-22 | Y | 9 | (mmmmm) | N
RP | Wilkins | 975XL2SEU | 2 | VUVD | 2011-02-22 | 2023-02-22 | Y | 9 | (mmmmm) | N
RP | Wilkins | 975XL2SEU | 2 | VUVU | 2011-02-22 | 2023-02-22 | Y | 9 | (mmmmm) | N
RP | Wilkins | 975XL2TCU | 0.5 | H | 2010-09-09 | 2022-09-09 | Y | 8 | (iiii) | N |  |  | Testcocks: Female Threaded End or 45 degree male SAE flare
RP | Wilkins | 975XL2TCU | 0.75 | H | 2010-09-09 | 2022-09-09 | Y | 8 | (iiii) | N |  |  | Testcocks: Female Threaded End or 45 degree male SAE flare
RP | Wilkins | 975XL2TCU | 1 | H | 2010-09-09 | 2022-09-09 | Y | 8 | (iiii) | N |  |  | Testcocks: Female Threaded End or 45 degree male SAE flare
RP | Wilkins | 975XL2TCU | 1.25 | H | 2010-09-09 | 2022-09-09 | Y | 8 | (iiii) | N
RP | Wilkins | 975XL2TCU | 1.5 | H | 2010-09-09 | 2022-09-09 | Y | 8 | (iiii) | N
RP | Wilkins | 975XL2TCU | 2 | H | 2010-09-09 | 2022-09-09 | Y | 8 | (iiii) | N
RP | Wilkins | 975XL2U | 0.75 | H | 2011-02-22 | 2023-02-22 | Y | 8 | (mmmmm) | N |  |  | Testcocks: Female Threaded End or 45 degree male SAE flare
RP | Wilkins | 975XL2U | 1 | H | 2011-02-22 | 2023-02-22 | Y | 8 | (mmmmm) | N |  |  | Testcocks: Female Threaded End or 45 degree male SAE flare
RP | Wilkins | 975XL2U | 1.5 | H | 2011-02-22 | 2023-02-22 | Y | 8 | (mmmmm) | N
RP | Wilkins | 975XL2U | 2 | H | 2011-02-22 | 2023-02-22 | Y | 8 | (mmmmm) | N
RP | Wilkins | 975XL2V | 0.75 | VUVD | 2011-02-22 | 2023-02-22 | Y | 9 | (iiii) | N |  |  | Testcocks: Female Threaded End or 45 degree male SAE flare
RP | Wilkins | 975XL2V | 0.75 | VUVU | 2011-02-22 | 2023-02-22 | Y | 9 | (iiii) | N |  |  | Testcocks: Female Threaded End or 45 degree male SAE flare
RP | Wilkins | 975XL2V | 1 | VUVD | 2011-02-22 | 2023-02-22 | Y | 9 | (iiii) | N |  |  | Testcocks: Female Threaded End or 45 degree male SAE flare
RP | Wilkins | 975XL2V | 1 | VUVU | 2011-02-22 | 2023-02-22 | Y | 9 | (iiii) | N |  |  | Testcocks: Female Threaded End or 45 degree male SAE flare
RP | Wilkins | 975XL3 | 0.5 | H | 2022-09-06 |  | Y | 10 | (iiii) | N
RP | Wilkins | 975XL3 | 0.75 | H | 2022-09-06 |  | Y | 10 | (iiii) | N
RP | Wilkins | 975XL3 | 1 | H | 2022-09-06 |  | Y | 10 | (iiii) | N
RP | Wilkins | 975XL3 | 1.25 | H | 2022-09-06 |  | Y | 10 | (iiii) | N
RP | Wilkins | 975XL3 | 1.5 | H | 2022-09-06 |  | Y | 10 | (iiii) | N
RP | Wilkins | 975XL3 | 2 | H | 2022-09-06 |  | Y | 10 | (iiii) | N
RP | Wilkins | 975XL3BFSS | 2 | H | 2023-05-23 |  | Y | 10 | (pppppp) | N
RP | Wilkins | 975XL3SE | 0.5 | VUVD | 2022-09-06 |  | Y | 10 | (iiii) | N
RP | Wilkins | 975XL3SE | 0.5 | VUVU | 2022-09-06 |  | Y | 10 | (iiii) | N
RP | Wilkins | 975XL3SE | 0.75 | VUVD | 2022-09-06 |  | Y | 10 | (iiii) | N
RP | Wilkins | 975XL3SE | 0.75 | VUVU | 2022-09-06 |  | Y | 10 | (iiii) | N
RP | Wilkins | 975XL3SE | 1 | VUVD | 2022-09-06 |  | Y | 10 | (iiii) | N
RP | Wilkins | 975XL3SE | 1 | VUVU | 2022-09-06 |  | Y | 10 | (iiii) | N
RP | Wilkins | 975XL3SEU | 0.75 | VUVD | 2022-09-06 |  | Y | 10 | (mmmmm) | N
RP | Wilkins | 975XL3SEU | 0.75 | VUVU | 2022-09-06 |  | Y | 10 | (mmmmm) | N
RP | Wilkins | 975XL3SEU | 1 | VUVD | 2022-09-06 |  | Y | 10 | (mmmmm) | N
RP | Wilkins | 975XL3SEU | 1 | VUVU | 2022-09-06 |  | Y | 10 | (mmmmm) | N
RP | Wilkins | 975XL3U | 0.75 | H | 2022-09-06 |  | Y | 10 | (mmmmm) | N
RP | Wilkins | 975XL3U | 1 | H | 2022-09-06 |  | Y | 10 | (mmmmm) | N
RP | Wilkins | 975XL3U | 1.25 | H | 2022-09-06 |  | Y | 10 | (mmmmm) | N
RP | Wilkins | 975XL3U | 1.5 | H | 2022-09-06 |  | Y | 10 | (mmmmm) | N
RP | Wilkins | 975XL3U | 2 | H | 2022-09-06 |  | Y | 10 | (mmmmm) | N
RP | Wilkins | 975XLBF | 2 | H | 2011-02-22 | 2023-02-22 | N | 8 | (bbbbb),pppppp | N
RP | Wilkins | 975XLBFSS | 2 | H | 2011-02-22 | 2023-02-22 | N | 8 | (ccccc),pppppp | N
RP | Wilkins | 975XLBMS | 0.75 | H | 1997-05-09 | 2024-05-09 | N | 8 | (ii),ooo | N
RP | Wilkins | 975XLBMS | 1 | H | 1997-05-09 | 2024-05-09 | N | 8 | (ii),ooo | N
RP | Wilkins | 975XLBMS | 1.25 | H | 1997-05-09 | 2024-05-09 | N | 8 | (ii),ooo | N
RP | Wilkins | 975XLBMS | 1.5 | H | 1997-05-09 | 2024-05-09 | N | 8 | (ii),ooo | N
RP | Wilkins | 975XLBMS | 2 | H | 1997-05-09 | 2024-05-09 | N | 8 | (ii),ooo | N
RP | Wilkins | 975XLD | 0.75 | H | 2002-10-08 | 2023-10-08 | N | 9 | (ii),ooo, iiii, mmmmm | N |  |  | Testcocks: Female Threaded End or 45 degree male SAE flare
RP | Wilkins | 975XLD | 0.75 | H | 2013-07-03 | 2022-07-03 | Y | 10 | (iiii), mmmmm | N |  |  | Testcocks: Female Threaded End or 45 degree male SAE flare
RP | Wilkins | 975XLDTCU | 0.75 | H | 2018-12-18 | 2024-12-18 | Y | 10 | (iiii), mmmmm | N |  |  | Testcocks: Female Threaded End or 45 degree male SAE flare
RP | Wilkins | 975XLMS | 0.75 | H | 1994-08-30 | 2024-08-30 | N | 8 | (ii),ooo | N
RP | Wilkins | 975XLMS | 1 | H | 1994-08-30 | 2024-08-30 | N | 8 | (ii),ooo | N
RP | Wilkins | 975XLMS | 1.25 | H | 1994-08-30 | 2024-08-30 | N | 8 | (ii),ooo | N
RP | Wilkins | 975XLMS | 1.5 | H | 1994-08-30 | 2024-08-30 | N | 8 | (ii),ooo | N
RP | Wilkins | 975XLMS | 2 | H | 1994-08-30 | 2024-08-30 | N | 8 | (ii),ooo | N
RP | Wilkins | 975XLSE | 0.75 | VUVD | 2000-10-16 | 2024-10-16 | N | 9 | (ii),ooo | N |  |  | Testcocks: Female Threaded End or 45 degree male SAE flare
RP | Wilkins | 975XLSE | 0.75 | VUVU | 2000-10-16 | 2024-10-16 | N | 9 | (ii),ooo | N |  |  | Testcocks: Female Threaded End or 45 degree male SAE flare
RP | Wilkins | 975XLSE | 1 | VUVD | 2000-10-16 | 2024-10-16 | N | 9 | (ii),ooo | N |  |  | Testcocks: Female Threaded End or 45 degree male SAE flare
RP | Wilkins | 975XLSE | 1 | VUVU | 2000-10-16 | 2024-10-16 | N | 9 | (ii),ooo | N |  |  | Testcocks: Female Threaded End or 45 degree male SAE flare
RP | Wilkins | 975XLSE | 1.25 | VUVD | 1999-11-04 | 2023-11-04 | N | 9 | (ii),ooo | N
RP | Wilkins | 975XLSE | 1.25 | VUVU | 1999-11-04 | 2023-11-04 | N | 9 | (ii),ooo | N
RP | Wilkins | 975XLSE | 1.5 | VUVD | 1999-11-04 | 2023-11-04 | N | 9 | (ii),ooo | N
RP | Wilkins | 975XLSE | 1.5 | VUVU | 1999-11-04 | 2023-11-04 | N | 9 | (ii),ooo | N
RP | Wilkins | 975XLSE | 2 | VUVD | 1999-11-04 | 2023-11-04 | N | 9 | (ii),ooo | N
RP | Wilkins | 975XLSE | 2 | VUVU | 1999-11-04 | 2023-11-04 | N | 9 | (ii).ooo | N
RP | Wilkins | 975XLSEU | 0.75 | VUVD | 2000-10-16 | 2024-10-16 | N | 9 | (ggg),xxx | N |  |  | Testcocks: Female Threaded End or 45 degree male SAE flare
RP | Wilkins | 975XLSEU | 0.75 | VUVU | 2000-10-16 | 2024-10-16 | N | 9 | (ggg),xxx | N |  |  | Testcocks: Female Threaded End or 45 degree male SAE flare
RP | Wilkins | 975XLSEU | 1 | VUVD | 2000-10-16 | 2024-10-16 | N | 9 | (ggg),xxx | N |  |  | Testcocks: Female Threaded End or 45 degree male SAE flare
RP | Wilkins | 975XLSEU | 1 | VUVU | 2000-10-16 | 2024-10-16 | N | 9 | (ggg),xxx | N |  |  | Testcocks: Female Threaded End or 45 degree male SAE flare
RP | Wilkins | 975XLSEU | 1.25 | VUVD | 2000-03-27 | 2023-03-27 | N | 9 | (ggg),xxx | Y
RP | Wilkins | 975XLSEU | 1.25 | VUVU | 2000-03-27 | 2023-03-27 | N | 9 | (ggg),xxx | Y
RP | Wilkins | 975XLSEU | 1.5 | VUVD | 2000-03-27 | 2023-03-27 | N | 9 | (ggg),xxx | Y
RP | Wilkins | 975XLSEU | 1.5 | VUVU | 2000-03-27 | 2023-03-27 | N | 9 | (ggg),xxx | Y
RP | Wilkins | 975XLSEU | 2 | VUVD | 2000-03-27 | 2023-03-27 | N | 9 | (ggg),xxx | Y
RP | Wilkins | 975XLSEU | 2 | VUVU | 2000-03-27 | 2023-03-27 | N | 9 | (ggg),xxx | Y
RP | Wilkins | 975XLST | 0.375 | H | 2002-11-19 | 2023-11-19 | Y | 9 | (ggggg) | N
RP | Wilkins | 975XLST | 0.5 | H | 2002-11-19 | 2023-11-19 | Y | 9 | (ggggg) | N
RP | Wilkins | 975XLTCU | 0.5 | H | 2007-04-05 | 2022-04-05 | N | 8 | (ii),ooo | N |  |  | Testcocks: Female Threaded End or 45 degree male SAE flare
RP | Wilkins | 975XLTCU | 0.75 | H | 2006-06-27 | 2024-06-27 | N | 8 | (ii),ooo,xxx | N |  |  | Testcocks: Female Threaded End or 45 degree male SAE flare
RP | Wilkins | 975XLTCU | 1 | H | 2006-06-27 | 2024-06-27 | N | 8 | (ii),ooo,xxx | N |  |  | Testcocks: Female Threaded End or 45 degree male SAE flare
RP | Wilkins | 975XLTCU | 1.25 | H | 2006-06-27 | 2024-06-27 | N | 8 | (ii),ooo,xxx | N
RP | Wilkins | 975XLTCU | 1.5 | H | 2006-06-27 | 2024-06-27 | N | 8 | (ii),ooo,xxx | N
RP | Wilkins | 975XLTCU | 2 | H | 2006-06-27 | 2024-06-27 | N | 8 | (ii),ooo,xxx | N
RP | Wilkins | 975XLU | 0.75 | H | 1993-09-02 | 2023-09-02 | N | 8 | (ggg),xxx | N |  |  | Testcocks: Female Threaded End or 45 degree male SAE flare
RP | Wilkins | 975XLU | 1 | H | 1993-09-02 | 2023-09-02 | N | 8 | (ggg),xxx | N |  |  | Testcocks: Female Threaded End or 45 degree male SAE flare
RP | Wilkins | 975XLU | 1.5 | H | 1993-09-02 | 2023-09-02 | N | 8 | (ggg),xxx | N
RP | Wilkins | 975XLU | 2 | H | 1993-09-02 | 2023-09-02 | N | 8 | (ggg),xxx | N
RP | Wilkins | 975XLV | 0.75 | VUVD | 2001-01-07 | 2022-01-07 | N | 9 | (ii),ooo | N
RP | Wilkins | 975XLV | 0.75 | VUVU | 2001-01-07 | 2022-01-07 | N | 9 | (ii),ooo | N
RP | Wilkins | 975XLV | 1 | VUVD | 2001-01-07 | 2022-01-07 | N | 9 | (ii),ooo | N
RP | Wilkins | 975XLV | 1 | VUVU | 2001-01-07 | 2022-01-07 | N | 9 | (ii),ooo | N
RP | Wilkins | MBC-10" | 10 | [9 empty] | 6"x6"x10" manifold, Model designation changed to 575M10
RP | Wilkins | MBC-8" | 8 | [9 empty] | 4"x4"x8" manifold,Model designation changed to 575M8
RPDA | Ames | 5000 | 4 | H | 1989-12-28 | 2022-12-28 | N | 8 | (uu),ee,ff,gg,hh,ll,mm,oo,pp,tt,ccc,ddd,ffff,gggg | Y | Conbraco 4020402 3/4 (H) | (M),A,B,C,D,E,F,G,H,I,J,K,L,N,O,P,Q,T
RPDA | Ames | 5000 | 6 | H | 1989-12-28 | 2022-12-28 | N | 8 | (uu),ee,ff,gg,hh,ll,mm,oo,pp,tt,ccc,ddd,ffff,gggg | Y | Conbraco 4020402 3/4 (H) | (K),A,B,C,D,E,F,G,H,I,J,L,M,N,O,P,Q,T
RPDA | Ames | 5000 | 8 | H | 1989-07-01 | 2022-07-01 | N | 8 | (uu),ee,ff,gg,hh,ll,mm,oo,pp,tt,ccc,ddd,ffff,gggg | Y | Conbraco 4020402 3/4 (H) | (K),A,B,C,D,E,F,G,H,I,J,L,M,N,O,P,Q,T
RPDA | Ames | 5000 | 10 | H | 1990-03-19 | 2023-03-19 | N | 8 | uu,ee,ff,gg,hh,ll,mm,oo,pp,tt,ccc,ddd,ffff,gggg | Y | Conbraco 4020402 3/4 (H) | (M),A,B,C,D,E,F,G,H,I,J,K,L,N,O,P,Q,T
RPDA | Ames | 5000CIV | 2.5 | H | 2000-07-07 | 2024-07-07 | N | 8 | (pp),hh,mm,uu | Y | Watts 909QT 3/4 (H) | (H),C,D,E,F,G,I,J,K,L,M,N,O,P,Q,T
RPDA | Ames | 5000CIV | 3 | H | 2000-07-07 | 2024-07-07 | N | 8 | (pp),hh,mm,uu,eee | Y | Watts 909QT 3/4 (H) | (N),B,C,D,E,F,G,H,I,J,K,L,M,O,P,Q,T
RPDA | Ames | 5000CIV | 4 | H | 2000-07-07 | 2024-07-07 | N | 8 | (pp),hh,mm,uu,eee | Y | Watts 909QT 3/4 (H) | (N),B,C,D,E,F,G,H,I,J,K,L,M,O,P,Q,T
RPDA | Ames | 5000CIV | 6 | H | 2000-07-07 | 2024-07-07 | N | 8 | (pp),hh,mm,uu,eee | Y | Watts 909QT 3/4 (H) | (N),B,C,D,E,F,G,H,I,J,K,L,M,O,P,Q,T
RPDA | Ames | 5000CIV | 8 | H | 2000-07-07 | 2024-07-07 | N | 8 | (pp),hh,mm,uu,eee | Y | Watts 909QT 3/4 (H) | (N),B,C,D,E,F,G,H,I,J,K,L,M,O,P,Q,T
RPDA | Ames | 5000CIV | 10 | H | 2000-07-07 | 2024-07-07 | N | 8 | (pp),hh,mm,uu,eee | Y | Watts 909QT 3/4 (H) | (N),B,C,D,E,F,G,H,I,J,K,L,M,O,P,Q,T
RPDA | Ames | Colt 500-GV | 2.5 | H | 2006-06-20 | 2024-06-20 | N | 9 | (zzz) | N | Watts 919QT 3/4" (H), Watts LF919QT 3/4" (H) | (N),H,I,J,K,L,M,N,O,P,Q
RPDA | Ames | Colt 500-GV | 3 | H | 2006-06-20 | 2024-06-20 | N | 9 | (zzz) | N | Watts 919QT 3/4" (H), Watts LF919QT 3/4" (H) | (N),H,I,J,K,L,M,N,O,P,Q
RPDA | Ames | Colt 500-GV | 4 | H | 2006-06-20 | 2024-06-20 | N | 9 | (zzz) | N | Watts 919QT 3/4" (H), Watts LF919QT 3/4" (H) | (N),H,I,J,K,L,M,N,O,P,Q
RPDA | Ames | Colt 500-GV | 6 | H | 2006-06-20 | 2024-06-20 | N | 9 | (zzz) | N | Watts 919QT 3/4" (H), Watts LF919QT 3/4" (H) | (N),H,I,J,K,L,M,N,O,P,Q
RPDA | Ames | Colt 500-GV | 8 | H | 2010-11-15 | 2022-11-15 | N | 9 | (zzz) | N | Watts 919QT 3/4" (H), Watts LF919QT 3/4" (H) | (N),H,I,J,K,L,M,N,O,P,Q
RPDA | Ames | Colt 500-GV | 10 | H | 2010-09-27 | 2022-09-27 | N | 9 | (zzz) | N | Watts 919QT 3/4" (H), Watts LF919QT 3/4" (H) | (N),H,I,J,K,L,M,N,O,P,Q
RPDA | Ames | Colt 500NBF | 2.5 | VUVD | 2013-06-24 | 2022-06-24 | N | 9 | (yyy) | N | Watts 919QT 3/4" (H), Watts LF919QT 3/4" (H) | (N),H,I,J,K,L,M,N,O,P,Q
RPDA | Ames | Colt 500NBF | 3 | VUVD | 2009-05-28 | 2024-05-28 | N | 9 | (yyy) | N | Watts 919QT 3/4" (H), Watts LF919QT 3/4" (H) | (N),H,I,J,K,L,M,N,O,P,Q
RPDA | Ames | Colt 500NBF | 4 | VUVD | 2009-05-28 | 2024-05-28 | N | 9 | (yyy) | N | Watts 919QT 3/4" (H), Watts LF919QT 3/4" (H) | (N),H,I,J,K,L,M,N,O,P,Q
RPDA | Ames | Colt 500NBF | 8 | VUVD | 2013-06-14 | 2022-06-14 | N | 9 | (yyy) | N | Watts 919QT 3/4" (H), Watts LF919QT 3/4" (H) | (N),H,I,J,K,L,M,N,O,P,Q
RPDA | Ames | Colt 500NGV | 2.5 | VUVD | 2009-05-28 | 2024-05-28 | N | 9 | (zzz) | N | Watts 919QT 3/4" (H), Watts LF919QT 3/4" (H) | (N),H,I,J,K,L,M,N,O,P,Q
RPDA | Ames | Colt 500NGV | 3 | VUVD | 2009-04-07 | 2024-04-07 | N | 9 | (zzz) | N | Watts 919QT 3/4" (H), Watts LF919QT 3/4" (H) | (N),H,I,J,K,L,M,N,O,P,Q
RPDA | Ames | Colt 500NGV | 4 | VUVD | 2009-04-07 | 2024-04-07 | N | 9 | (zzz) | N | Watts 919QT 3/4" (H), Watts LF919QT 3/4" (H) | (N),H,I,J,K,L,M,N,O,P,Q
RPDA | Ames | Colt 500NGV | 6 | VUVD | 2010-11-15 | 2022-11-15 | N | 9 | (zzz) | N | Watts 919QT 3/4" (H), Watts LF919QT 3/4" (H) | (N),H,I,J,K,L,M,N,O,P,Q
RPDA | Ames | Colt 500NGV | 8 | VUVD | 2013-06-14 | 2022-06-14 | N | 9 | (zzz) | N | Watts 919QT 3/4" (H), Watts LF919QT 3/4" (H) | (N),H,I,J,K,L,M,N,O,P,Q
RPDA | Ames | Colt 500ZBF | 2.5 | VUVU | 2013-06-24 | 2022-06-24 | N | 9 | (yyy) | N | Watts 919QT 3/4" (H), Watts LF919QT 3/4" (H) | (N),H,I,J,K,L,M,N,O,P,Q
RPDA | Ames | Colt 500ZBF | 3 | VUVU | 2013-06-24 | 2022-06-24 | N | 9 | (yyy) | N | Watts 919QT 3/4" (H), Watts LF919QT 3/4" (H) | (N),H,I,J,K,L,M,N,O,P,Q
RPDA | Ames | Colt 500ZBF | 4 | VUVU | 2013-06-24 | 2022-06-24 | N | 9 | (yyy) | N | Watts 919QT 3/4" (H), Watts LF919QT 3/4" (H) | (N),H,I,J,K,L,M,N,O,P,Q
RPDA | Ames | Colt 500ZBF | 8 | VUVU | 2013-06-14 | 2022-06-14 | N | 9 | (yyy) | N | Watts 919QT 3/4" (H), Watts LF919QT 3/4" (H) | (N),H,I,J,K,L,M,N,O,P,Q
RPDA | Ames | Colt 500ZGV | 2.5 | VUVU | 2013-06-24 | 2022-06-24 | N | 9 | (zzz) | N | Watts 919QT 3/4" (H), Watts LF919QT 3/4" (H) | (N),H,I,J,K,L,M,N,O,P,Q
RPDA | Ames | Colt 500ZGV | 3 | VUVU | 2013-06-24 | 2022-06-24 | N | 9 | (zzz) | N | Watts 919QT 3/4" (H), Watts LF919QT 3/4" (H) | (N),H,I,J,K,L,M,N,O,P,Q
RPDA | Ames | Colt 500ZGV | 4 | VUVU | 2013-06-24 | 2022-06-24 | N | 9 | (zzz) | N | Watts 919QT 3/4" (H), Watts LF919QT 3/4" (H) | (N),H,I,J,K,L,M,N,O,P,Q
RPDA | Ames | Colt 500ZGV | 8 | VUVU | 2013-06-14 | 2022-06-14 | N | 9 | (zzz) | N | Watts 919QT 3/4" (H), Watts LF919QT 3/4" (H) | (N),H,I,J,K,L,M,N,O,P,Q
RPDA | Ames | LFColt 500GV | 2.5 | H | 2014-01-08 | 2023-01-08 | Y | 9 | (zzz) | N | Watts LF919QT 3/4" (H) | (O) | Lead free compliant version identified with NSF61 mark on meter
RPDA | Ames | LFColt 500GV | 2.5 | H | 2014-01-08 | 2023-01-08 | Y | 9 | (zzz) | N | Watts LF919QT 3/4" (H) | (O) | Lead free compliant version identified with NSF61 mark on meter
RPDA | Ames | LFColt 500GV | 3 | H | 2014-01-08 | 2023-01-08 | Y | 9 | (zzz) | N | Watts LF919QT 3/4" (H) | (O) | Lead free compliant version identified with NSF61 mark on meter
RPDA | Ames | LFColt 500GV | 3 | H | 2014-01-08 | 2023-01-08 | Y | 9 | (zzz) | N | Watts LF919QT 3/4" (H) | (O) | Lead free compliant version identified with NSF61 mark on meter
RPDA | Ames | LFColt 500GV | 4 | H | 2014-01-08 | 2023-01-08 | Y | 9 | (zzz) | N | Watts LF919QT 3/4" (H) | (O) | Lead free compliant version identified with NSF61 mark on meter
RPDA | Ames | LFColt 500GV | 4 | H | 2014-01-08 | 2023-01-08 | Y | 9 | (zzz) | N | Watts LF919QT 3/4" (H) | (O) | Lead free compliant version identified with NSF61 mark on meter
RPDA | Ames | LFColt 500GV | 6 | H | 2014-01-08 | 2023-01-08 | Y | 9 | (zzz) | N | Watts LF919QT 3/4" (H) | (O) | Lead free compliant version identified with NSF61 mark on meter
RPDA | Ames | LFColt 500GV | 6 | H | 2014-01-08 | 2023-01-08 | Y | 9 | (zzz) | N | Watts LF919QT 3/4" (H) | (O) | Lead free compliant version identified with NSF61 mark on meter
RPDA | Ames | LFColt 500GV | 8 | H | 2015-08-13 | 2024-08-13 | Y | 9 | (zzz) | N | Watts LF919QT 3/4" (H) | (M) | Lead free compliant version identified with NSF61 mark on meter
RPDA | Ames | LFColt 500GV | 10 | H | 2015-10-12 | 2024-10-12 | Y | 9 | (zzz) | N | Watts LF919QT 3/4" (H) | (M) | Lead free compliant version identified with NSF61 mark on meter
RPDA | Ames | LFColt 500NBF | 2.5 | VUVD | 2014-01-08 | 2023-01-08 | Y | 9 | (zzz) | N | Watts LF919QT 3/4" (H) | (O) | Lead free compliant version identified with NSF61 mark on meter
RPDA | Ames | LFColt 500NBF | 3 | VUVD | 2014-01-08 | 2023-01-08 | Y | 9 | (zzz) | N | Watts LF919QT 3/4" (H) | (O) | Lead free compliant version identified with NSF61 mark on meter
RPDA | Ames | LFColt 500NBF | 4 | VUVD | 2014-01-08 | 2023-01-08 | Y | 9 | (zzz) | N | Watts LF919QT 3/4" (H) | (O) | Lead free compliant version identified with NSF61 mark on meter
RPDA | Ames | LFColt 500NGV | 2.5 | VUVD | 2014-01-08 | 2023-01-08 | Y | 9 | (zzz) | N | Watts LF919QT 3/4" (H) | (O) | Lead free compliant version identified with NSF61 mark on meter
RPDA | Ames | LFColt 500NGV | 3 | VUVD | 2014-01-08 | 2023-01-08 | Y | 9 | (zzz) | N | Watts LF919QT 3/4" (H) | (O) | Lead free compliant version identified with NSF61 mark on meter
RPDA | Ames | LFColt 500NGV | 4 | VUVD | 2014-01-08 | 2023-01-08 | Y | 9 | (zzz) | N | Watts LF919QT 3/4" (H) | (O) | Lead free compliant version identified with NSF61 mark on meter
RPDA | Ames | LFColt 500ZBF | 2.5 | VUVD | 2014-01-08 | 2023-01-08 | Y | 9 | (zzz) | N | Watts LF919QT 3/4" (H) | (O) | Lead free compliant version identified with NSF61 mark on meter
RPDA | Ames | LFColt 500ZBF | 3 | VUVD | 2014-01-08 | 2023-01-08 | Y | 9 | (zzz) | N | Watts LF919QT 3/4" (H) | (O) | Lead free compliant version identified with NSF61 mark on meter
RPDA | Ames | LFColt 500ZBF | 4 | VUVD | 2014-01-08 | 2023-01-08 | Y | 9 | (zzz) | N | Watts LF919QT 3/4" (H) | (O) | Lead free compliant version identified with NSF61 mark on meter
RPDA | Ames | LFColt 500ZGV | 2.5 | VUVD | 2014-01-08 | 2023-01-08 | Y | 9 | (zzz) | N | Watts LF919QT 3/4" (H) | (O) | Lead free compliant version identified with NSF61 mark on meter
RPDA | Ames | LFColt 500ZGV | 3 | VUVD | 2014-01-08 | 2023-01-08 | Y | 9 | (zzz) | N | Watts LF919QT 3/4" (H) | (O) | Lead free compliant version identified with NSF61 mark on meter
RPDA | Ames | LFColt 500ZGV | 4 | VUVD | 2014-01-08 | 2023-01-08 | Y | 9 | (zzz) | N | Watts LF919QT 3/4" (H) | (O) | Lead free compliant version identified with NSF61 mark on meter
RPDA | Ames | LFMaxim 500GV | 2.5 | H | 2014-01-08 | 2023-01-08 | Y | 9 | (zzz) | N | Watts LF919QT 3/4" (H) | (O) | Lead free compliant version identified with NSF61 mark on meter
RPDA | Ames | LFMaxim 500GV | 3 | H | 2014-01-08 | 2023-01-08 | Y | 9 | (zzz) | N | Watts LF919QT 3/4" (H) | (O) | Lead free compliant version identified with NSF61 mark on meter
RPDA | Ames | LFMaxim 500GV | 4 | H | 2014-01-08 | 2023-01-08 | Y | 9 | (zzz) | N | Watts LF919QT 3/4" (H) | (O) | Lead free compliant version identified with NSF61 mark on meter
RPDA | Ames | LFMaxim 500GV | 6 | H | 2015-08-13 | 2024-08-13 | Y | 9 | (zzz) | N | Watts LF919QT 3/4" (H) | (M) | Lead free compliant version identified with NSF61 mark on meter
RPDA | Ames | LFMaxim 500GV | 8 | H | 2015-10-12 | 2024-10-12 | Y | 9 | (zzz) | N | Watts LF919QT 3/4" (H) | (M) | Lead free compliant version identified with NSF61 mark on meter
RPDA | Ames | LFMaxim 500GV | 10 | H | 2015-10-12 | 2024-10-12 | Y | 9 | (zzz) | N | Watts LF919QT 3/4" (H) | (M) | Lead free compliant version identified with NSF61 mark on meter
RPDA | Ames | LFMaxim 500NBF | 2.5 | VUVD | 2014-01-08 | 2023-01-08 | Y | 9 | (zzz) | N | Watts LF919QT 3/4" (H) | (O) | Lead free compliant version identified with NSF61 mark on meter
RPDA | Ames | LFMaxim 500NBF | 3 | VUVD | 2014-01-08 | 2023-01-08 | Y | 9 | (zzz) | N | Watts LF919QT 3/4" (H) | (O) | Lead free compliant version identified with NSF61 mark on meter
RPDA | Ames | LFMaxim 500NGV | 2.5 | VUVD | 2014-01-08 | 2023-01-08 | Y | 9 | (zzz) | N | Watts LF919QT 3/4" (H) | (O) | Lead free compliant version identified with NSF61 mark on meter
RPDA | Ames | LFMaxim 500NGV | 3 | VUVD | 2014-01-08 | 2023-01-08 | Y | 9 | (zzz) | N | Watts LF919QT 3/4" (H) | (O) | Lead free compliant version identified with NSF61 mark on meter
RPDA | Ames | LFMaxim 500ZBF | 2.5 | VUVD | 2014-01-08 | 2023-01-08 | Y | 9 | (zzz) | N | Watts LF919QT 3/4" (H) | (O) | Lead free compliant version identified with NSF61 mark on meter
RPDA | Ames | LFMaxim 500ZBF | 3 | VUVD | 2014-01-08 | 2023-01-08 | Y | 9 | (zzz) | N | Watts LF919QT 3/4" (H) | (O) | Lead free compliant version identified with NSF61 mark on meter
RPDA | Ames | LFMaxim 500ZGV | 2.5 | VUVD | 2014-01-08 | 2023-01-08 | Y | 9 | (zzz) | N | Watts LF919QT 3/4" (H) | (O) | Lead free compliant version identified with NSF61 mark on meter
RPDA | Ames | LFMaxim 500ZGV | 3 | VUVD | 2014-01-08 | 2023-01-08 | Y | 9 | (zzz) | N | Watts LF919QT 3/4" (H) | (O) | Lead free compliant version identified with NSF61 mark on meter
RPDA | Ames | Maxim 500-GV | 2.5 | H | 2006-06-20 | 2024-06-20 | N | 9 | (zzz) | N | Watts 919QT 3/4" (H), Watts LF919QT 3/4" (H) | (N),H,I,J,K,L,M,N,O,P,Q
RPDA | Ames | Maxim 500-GV | 3 | H | 2006-06-20 | 2024-06-20 | N | 9 | (zzz) | N | Watts 919QT 3/4" (H), Watts LF919QT 3/4" (H) | (N),H,I,J,K,L,M,N,O,P,Q
RPDA | Ames | Maxim 500-GV | 4 | H | 2006-06-20 | 2024-06-20 | N | 9 | (zzz) | N | Watts 919QT 3/4" (H), Watts LF919QT 3/4" (H) | (N),H,I,J,K,L,M,N,O,P,Q
RPDA | Ames | Maxim 500-GV | 6 | H | 2010-11-15 | 2022-11-15 | N | 9 | (zzz) | N | Watts 919QT 3/4" (H), Watts LF919QT 3/4" (H) | (N),H,I,J,K,L,M,N,O,P,Q
RPDA | Ames | Maxim 500-GV | 8 | H | 2010-09-27 | 2022-09-27 | N | 9 | (zzz) | N | Watts 919QT 3/4" (H), Watts LF919QT 3/4" (H) | (N),H,I,J,K,L,M,N,O,P,Q
RPDA | Ames | Maxim 500-GV | 10 | H | 2010-09-27 | 2022-09-27 | N | 9 | (zzz) | N | Watts 919QT 3/4" (H), Watts LF919QT 3/4" (H) | (N),H,I,J,K,L,M,N,O,P,Q
RPDA | Ames | Maxim 500NBF | 2.5 | VUVD | 2013-06-24 | 2022-06-24 | N | 9 | (yyy) | N | Watts 919QT 3/4" (H), Watts LF919QT 3/4" (H) | (N),H,I,J,K,L,M,N,O,P,Q
RPDA | Ames | Maxim 500NBF | 3 | VUVD | 2009-04-07 | 2024-04-07 | N | 9 | (yyy) | N | Watts 919QT 3/4" (H), Watts LF919QT 3/4" (H) | (N),H,I,J,K,L,M,N,O,P,Q
RPDA | Ames | Maxim 500NBF | 4 | VUVD | 2010-11-15 | 2022-11-15 | N | 9 | (yyy) | N | Watts 919QT 3/4" (H), Watts LF919QT 3/4" (H) | (N),H,I,J,K,L,M,N,O,P,Q
RPDA | Ames | Maxim 500NBF | 6 | VUVD | 2013-06-14 | 2022-06-14 | N | 9 | (yyy) | N | Watts 919QT 3/4" (H), Watts LF919QT 3/4" (H) | (N),H,I,J,K,L,M,N,O,P,Q
RPDA | Ames | Maxim 500NGV | 2.5 | VUVD | 2009-04-07 | 2024-04-07 | N | 9 | (zzz) | N | Watts 919QT 3/4" (H), Watts LF919QT 3/4" (H) | (N),H,I,J,K,L,M,N,O,P,Q
RPDA | Ames | Maxim 500NGV | 3 | VUVD | 2009-04-07 | 2024-04-07 | N | 9 | (zzz) | N | Watts 919QT 3/4" (H), Watts LF919QT 3/4" (H) | (N),H,I,J,K,L,M,N,O,P,Q
RPDA | Ames | Maxim 500NGV | 4 | VUVD | 2010-11-15 | 2022-11-15 | N | 9 | (zzz) | N | Watts 919QT 3/4" (H), Watts LF919QT 3/4" (H) | (N),H,I,J,K,L,M,N,O,P,Q
RPDA | Ames | Maxim 500NGV | 6 | VUVD | 2013-06-14 | 2022-06-14 | N | 9 | (zzz) | N | Watts 919QT 3/4" (H), Watts LF919QT 3/4" (H) | (N),H,I,J,K,L,M,N,O,P,Q
RPDA | Ames | Maxim 500ZBF | 2.5 | VUVU | 2013-06-24 | 2022-06-24 | N | 9 | (yyy) | N | Watts 919QT 3/4" (H), Watts LF919QT 3/4" (H) | (N),H,I,J,K,L,M,N,O,P,Q
RPDA | Ames | Maxim 500ZBF | 3 | VUVU | 2013-06-24 | 2022-06-24 | N | 9 | (yyy) | N | Watts 919QT 3/4" (H), Watts LF919QT 3/4" (H) | (N),H,I,J,K,L,M,N,O,P,Q
RPDA | Ames | Maxim 500ZBF | 6 | VUVU | 2013-06-14 | 2022-06-14 | N | 9 | (yyy) | N | Watts 919QT 3/4" (H), Watts LF919QT 3/4" (H) | (N),H,I,J,K,L,M,N,O,P,Q
RPDA | Ames | Maxim 500ZGV | 2.5 | VUVU | 2013-06-24 | 2022-06-24 | N | 9 | (zzz) | N | Watts 919QT 3/4" (H), Watts LF919QT 3/4" (H) | (N),H,I,J,K,L,M,N,O,P,Q
RPDA | Ames | Maxim 500ZGV | 3 | VUVU | 2013-06-24 | 2022-06-24 | N | 9 | (zzz) | N | Watts 919QT 3/4" (H), Watts LF919QT 3/4" (H) | (N),H,I,J,K,L,M,N,O,P,Q
RPDA | Ames | Maxim 500ZGV | 6 | VUVU | 2013-06-14 | 2022-06-14 | N | 9 | (zzz) | N | Watts 919QT 3/4" (H), Watts LF919QT 3/4" (H) | (N),H,I,J,K,L,M,N,O,P,Q
RPDA | Apollo/Conbraco | RPDALF4A | 2.5 | H | 2014-06-10 | 2023-06-10 | Y | 10 | (yyy), cccc, dddd, mmmm, nnnn, xxxxx, yyyyy, zzzzz, aaaaaa, xxxxxx | N | Apollo RPLF4A 1/2" (H) | (P),O
RPDA | Apollo/Conbraco | RPDALF4A | 3 | H | 2014-06-10 | 2023-06-10 | Y | 10 | (yyy), cccc, dddd, mmmm, nnnn, xxxxx, yyyyy, zzzzz, aaaaaa, xxxxxx | N | Apollo RPLF4A 1/2" (H) | (P),O
RPDA | Apollo/Conbraco | RPDALF4A | 4 | H | 2013-06-24 | 2022-06-24 | Y | 10 | (yyy), cccc, dddd, mmmm, nnnn, xxxxx, yyyyy, zzzzz, aaaaaa, xxxxxx | N | Apollo RPLF4A 1/2" (H) | (P),G,H,I,J,K,L,M,N,O,Q,T
RPDA | Apollo/Conbraco | RPDALF4A | 6 | H | 2013-06-24 | 2022-06-24 | Y | 10 | (yyy), cccc, dddd, mmmm, nnnn, xxxxx, yyyyy, zzzzz, aaaaaa, xxxxxx | N | Apollo RPLF4A 1/2" (H) | (P),G,H,I,J,K,L,M,N,O,Q,T
RPDA | Apollo/Conbraco | RPDALF4A | 8 | H | 2018-02-22 | 2024-02-22 | Y | 10 | (yyy), cccc, dddd, mmmm, nnnn, xxxxx, yyyyy, zzzzz, aaaaaa, xxxxxx | N | Apollo RPLF4A 1/2" (H) | (M),G,H,I,J,K,L,N,O,P,Q,T
RPDA | Apollo/Conbraco | RPDALF4AN | 2.5 | VUVD | 2016-05-12 | 2022-05-12 | Y | 10 | (yyy), cccc, dddd, mmmm, nnnn, xxxxx, yyyyy, zzzzz, aaaaaa, xxxxxx | N | Apollo RPLF4A 1/2" (H) | (M),G,H,I,J,K,L,N,O,P,Q,T
RPDA | Apollo/Conbraco | RPDALF4AN | 2.5 | VUVU | 2016-05-12 | 2022-05-12 | Y | 10 | (yyy), cccc, dddd, mmmm, nnnn, xxxxx, yyyyy, zzzzz, aaaaaa, xxxxxx | N | Apollo RPLF4A 1/2" (H) | (M),G,H,I,J,K,L,N,O,P,Q,T
RPDA | Apollo/Conbraco | RPDALF4AN | 3 | VUVD | 2016-05-12 | 2022-05-12 | Y | 10 | (yyy), cccc, dddd, mmmm, nnnn, xxxxx, yyyyy, zzzzz, aaaaaa, xxxxxx | N | Apollo RPLF4A 1/2" (H) | (M),G,H,I,J,K,L,N,O,P,Q,T
RPDA | Apollo/Conbraco | RPDALF4AN | 3 | VUVU | 2016-05-12 | 2022-05-12 | Y | 10 | (yyy), cccc, dddd, mmmm, nnnn, xxxxx, yyyyy, zzzzz, aaaaaa, xxxxxx | N | Apollo RPLF4A 1/2" (H) | (M),G,H,I,J,K,L,N,O,P,Q,T
RPDA | Apollo/Conbraco | RPDALF4AN | 4 | VUVD | 2014-06-10 | 2023-06-10 | Y | 10 | (yyy), cccc, dddd, mmmm, nnnn, xxxxx, yyyyy, zzzzz, aaaaaa, xxxxxx | N | Apollo RPLF4A 1/2" (H) | (P),G,H,I,J,K,L,M,N,O,Q,T
RPDA | Apollo/Conbraco | RPDALF4AN | 4 | VUVU | 2014-06-11 | 2023-06-11 | Y | 10 | (yyy), cccc, dddd, mmmm, nnnn, xxxxx, yyyyy, zzzzz, aaaaaa, xxxxxx | N | Apollo RPLF4A 1/2" (H) | (P),G,H,I,J,K,L,M,N,O,Q,T
RPDA | Apollo/Conbraco | RPDALF4AN | 6 | VUVD | 2015-05-12 | 2024-05-12 | Y | 10 | (yyy), cccc, dddd, mmmm, nnnn, xxxxx, yyyyy, zzzzz, aaaaaa, xxxxxx | N | Apollo RPLF4A 1/2" (H) | (M),G,H,I,J,K,L,N,O,P,Q,T
RPDA | Apollo/Conbraco | RPDALF4AN | 6 | VUVU | 2015-05-12 | 2024-05-12 | Y | 10 | (yyy), cccc, dddd, mmmm, nnnn, xxxxx, yyyyy, zzzzz, aaaaaa, xxxxxx | N | Apollo RPLF4A 1/2" (H) | (M),G,H,I,J,K,L,N,O,P,Q,T
RPDA | Apollo/Conbraco | RPDALF4AN | 8 | VUVD | 2018-02-22 | 2024-02-22 | Y | 10 | (yyy), cccc, dddd, mmmm, nnnn, xxxxx, yyyyy, zzzzz, aaaaaa, xxxxxx | N | Apollo RPLF4A 1/2" (H) | (M),G,H,I,J,K,L,N,O,P,Q,T
RPDA | Apollo/Conbraco | RPDALF4AN | 8 | VUVU | 2018-02-22 | 2024-02-22 | Y | 10 | (yyy), cccc, dddd, mmmm, nnnn, xxxxx, yyyyy, zzzzz, aaaaaa, xxxxxx | N | Apollo RPLF4A 1/2" (H) | (M),G,H,I,J,K,L,N,O,P,Q,T
RPDA | Apollo/Conbraco | RPDALF4AR | 2.5 | H | 2015-12-21 | 2024-12-21 | Y | 10 | (cccc), dddd, mmmm, nnnn, xxxxx, yyyyy, zzzzz, aaaaaa | Y | Apollo RPLF4A 1/2" | (M),G,H,I,J,K,L,N,O,Q,T | Integral Stainless Steel grooved spool between the #2 ck and #2 SOV - assembly length: min. 34" and max. 47 1/8"
RPDA | Apollo/Conbraco | RPDALF4AR | 3 | H | 2015-12-21 | 2024-12-21 | Y | 10 | (cccc), dddd, mmmm, nnnn, xxxxx, yyyyy, zzzzz, aaaaaa | Y | Apollo RPLF4A 1/2" | (M),G,H,I,J,K,L,N,O,Q,T | Integral Stainless Steel grooved spool between the #2 ck and #2 SOV - assembly length: min. 35" and max. 48 1/8"
RPDA | Apollo/Conbraco | RPDALF4AR | 4 | H | 2015-12-21 | 2024-12-21 | Y | 10 | (cccc), dddd, mmmm, nnnn, xxxxx, yyyyy, zzzzz, aaaaaa | Y | Apollo RPLF4A 1/2" | (M),G,H,I,J,K,L,N,O,Q,T | Integral Stainless Steel grooved spool between the #2 ck and #2 SOV - assembly length: min. 37 3/8" and max. 62 1/4"
RPDA | Apollo/Conbraco | RPDALF4AR | 6 | H | 2015-12-21 | 2024-12-21 | Y | 10 | (cccc), dddd, mmmm, nnnn, xxxxx, yyyyy, zzzzz, aaaaaa | Y | Apollo RPLF4A 1/2" | (M),G,H,I,J,K,L,N,O,Q,T | Integral Stainless Steel grooved spool between the #2 ck and #2 SOV - assembly length: min. 46" and max. 71 1/4"
RPDA | Apollo/Conbraco | RPDALF4AR | 8 | H | 2018-02-22 | 2024-02-22 | Y | 10 | (xxxxx), cccc, dddd, mmmm, nnnn, yyyyy, zzzzz, aaaaaa | Y | Apollo RPLF4A 1/2" (H) | (M),G,H,I,J,K,L,N,O,P,Q,T | Integral Stainless Steel grooved spool between the #2 ck and #2 SOV - assembly length: min. 55 3/4" and max. 86"
RPDA | Cla-Val | 18-4 | 10 | H | 1990-08-23 | 2023-08-23 | N | 8 | hh,gg,qq,rr | Y | Cla-Val RP2 3/4 (H) | (H),A,B,C,D,E,F,G,I,J,K,L,M,N,O,P,Q,T
RPDA | Conbraco | [5 empty] | N | [5 empty] | See Apollo/Conbraco
RPDA | Febco | 826 Type YD | 2.5 | [9 empty] | model designation changed to 826YD
RPDA | Febco | 826 Type YD | 3 | [9 empty] | model designation changed to 826YD
RPDA | Febco | 826 Type YD | 4 | [9 empty] | model designation changed to 826YD
RPDA | Febco | 826 Type YD | 6 | [9 empty] | model designation changed to 826YD
RPDA | Febco | 826 Type YD | 8 | [9 empty] | model designation changed to 826YD
RPDA | Febco | 826 Type YD | 10 | [9 empty] | model designation changed to 826YD
RPDA | Febco | 826YD | 2.5 | H | 1988-11-11 | 2024-11-11 | N | 8 | (ff),mm,oo,pp,uu,zzz,ffff,gggg | Y | Febco 825Y 3/4 (H) | (M),B,C,D,E,F,G,H,I,J,K,L,N,O,P,Q,T | formerly 826 Type YD
RPDA | Febco | 826YD | 3 | H | 1988-11-11 | 2024-11-11 | N | 8 | (ff),mm,oo,pp,uu,zzz,ffff,gggg | Y | Febco 825Y 3/4 (H) | (M),B,C,D,E,F,G,H,I,J,K,L,N,O,P,Q,T | formerly 826 Type YD
RPDA | Febco | 826YD | 4 | H | 1988-10-14 | 2024-10-14 | N | 8 | (ff),mm,oo,pp,uu,zzz,ffff,gggg | Y | Febco 825Y 3/4 (H) | (M),B,C,D,E,F,G,H,I,J,K,L,N,O,P,Q,T | formerly 826 Type YD
RPDA | Febco | 826YD | 6 | H | 1990-03-01 | 2023-03-01 | N | 8 | (ff),mm,oo,pp,uu,zzz,ffff,gggg | Y | Febco 825Y 3/4 (H) | (M),B,C,D,E,F,G,H,I,J,K,L,N,O,P,Q,T | formerly 826 Type YD
RPDA | Febco | 826YD | 8 | H | 1990-06-22 | 2023-06-22 | N | 8 | (ff),mm,oo,pp,uu,zzz,ffff,gggg | Y | Febco 825Y 3/4 (H) | (M),B,C,D,E,F,G,H,I,J,K,L,N,O,P,Q,T | formerly 826 Type YD
RPDA | Febco | 826YD | 10 | H | 1990-06-22 | 2023-06-22 | N | 8 | (ff),mm,oo,pp,uu,zzz,ffff,gggg | N | Febco 825Y 3/4 (H) | (M),B,C,D,E,F,G,H,I,J,K,L,N,O,P,Q,T | formerly 826 Type YD
RPDA | Neptune | [5 empty] | N | [5 empty] | See Wilkins
RPDA | Watts | 909DDC | 6 | [9 empty] | model designation changed to 909RPDA
RPDA | Watts | 909DDCM2 | 3 | [9 empty] | model designation changed to 909RPDA
RPDA | Watts | 909RPDA | 2.5 | H | 1999-06-16 | 2023-06-16 | N | 8 | (pp),hh,mm,uu,zz,ffff,gggg,aaaaaaa | N | Watts 909QT 3/4 (H) | (H),C,D,E,F,G,I,J,K,L,M,O,P,Q,T,U
RPDA | Watts | 909RPDA | 3 | H | 1988-10-05 | 2024-10-05 | N | 8 | (pp),hh,mm,uu,zz,eee,ffff,gggg,aaaaaaa | N | Watts 909QT 3/4 (H) | (N),B,C,D,E,F,G,H,I,J,K,L,M,O,P,Q,T,U | formerly 909DDCM2
RPDA | Watts | 909RPDA | 4 | H | 1988-02-09 | 2024-02-09 | N | 8 | (pp),hh,mm,uu,zz,eee,ffff,gggg,aaaaaaa | N | Watts 909QT 3/4 (H) | (N),B,C,D,E,F,G,H,I,J,K,L,M,O,P,Q,T,U
RPDA | Watts | 909RPDA | 6 | H | 1988-10-05 | 2024-10-05 | N | 8 | (pp),hh,mm,uu,zz,eee,ffff,gggg,aaaaaaa | N | Watts 909QT 3/4 (H) | (N),B,C,D,E,F,G,H,I,J,K,L,M,O,P,Q,T,U | formerly 909DDC
RPDA | Watts | 909RPDA | 8 | H | 1988-02-14 | 2024-02-14 | N | 8 | (pp),hh,mm,uu,zz,eee,ffff,gggg,aaaaaaa | N | Watts 909QT 3/4 (H) | (N),B,C,D,E,F,G,H,I,J,K,L,M,O,P,Q,T,U
RPDA | Watts | 909RPDA | 10 | H | 1988-02-15 | 2024-02-15 | N | 8 | (pp),hh,mm,uu,zz,eee,ffff,gggg | N | Watts 909QT 3/4 (H) | (N),B,C,D,E,F,G,H,I,J,K,L,M,O,P,Q,T,U
RPDA | Watts | 957NRPDA-BF | 2.5 | VUVD | 2013-06-24 | 2022-06-24 | N | 9 | (yyy) | N | Watts 919QT 3/4" (H), Watts LF919QT 3/4" (H) | (N),H,I,J,K,L,M,N,O,P,Q
RPDA | Watts | 957NRPDA-BF | 3 | VUVD | 2009-04-07 | 2024-04-07 | N | 9 | (yyy) | N | Watts 919QT 3/4" (H), Watts LF919QT 3/4" (H) | (N),H,I,J,K,L,M,N,O,P,Q
RPDA | Watts | 957NRPDA-BF | 4 | VUVD | 2009-04-07 | 2024-04-07 | N | 9 | (yyy) | N | Watts 919QT 3/4" (H), Watts LF919QT 3/4" (H) | (N),H,I,J,K,L,M,N,O,P,Q
RPDA | Watts | 957NRPDA-BF | 8 | VUVD | 2013-06-14 | 2022-06-14 | N | 9 | (yyy) | N | Watts 919QT 3/4" (H), Watts LF919QT 3/4" (H) | (N),H,I,J,K,L,M,N,O,P,Q
RPDA | Watts | 957NRPDA-GV | 2.5 | VUVD | 2009-04-07 | 2024-04-07 | N | 9 | (zzz) | N | Watts 919QT 3/4" (H), Watts LF919QT 3/4" (H) | (N),H,I,J,K,L,M,N,O,P,Q
RPDA | Watts | 957NRPDA-GV | 3 | VUVD | 2009-04-07 | 2024-04-07 | N | 9 | (zzz) | N | Watts 919QT 3/4" (H), Watts LF919QT 3/4" (H) | (N),H,I,J,K,L,M,N,O,P,Q
RPDA | Watts | 957NRPDA-GV | 4 | VUVD | 2009-04-07 | 2024-04-07 | N | 9 | (zzz) | N | Watts 919QT 3/4" (H), Watts LF919QT 3/4" (H) | (N),H,I,J,K,L,M,N,O,P,Q
RPDA | Watts | 957NRPDA-GV | 6 | VUVD | 2010-11-15 | 2022-11-15 | N | 9 | (zzz) | N | Watts 919QT 3/4" (H), Watts LF919QT 3/4" (H) | (N),H,I,J,K,L,M,N,O,P,Q
RPDA | Watts | 957NRPDA-GV | 8 | VUVD | 2013-06-14 | 2022-06-14 | N | 9 | (zzz) | N | Watts 919QT 3/4" (H), Watts LF919QT 3/4" (H) | (N),H,I,J,K,L,M,N,O,P,Q
RPDA | Watts | 957RPDA-GV | 2.5 | H | 2006-06-20 | 2024-06-20 | N | 9 | (zzz) | N | Watts 919QT 3/4" (H), Watts LF919QT 3/4" (H) | (N), H, I J, K L, M, N, O, P, Q
RPDA | Watts | 957RPDA-GV | 3 | H | 2006-06-20 | 2024-06-20 | N | 9 | (zzz) | N | Watts 919QT 3/4" (H), Watts LF919QT 3/4" (H) | (N), H, I J, K L, M, N, O, P, Q
RPDA | Watts | 957RPDA-GV | 4 | H | 2006-06-20 | 2024-06-20 | N | 9 | (zzz) | N | Watts 919QT 3/4" (H), Watts LF919QT 3/4" (H) | (N), H, I J, K L, M, N, O, P, Q
RPDA | Watts | 957RPDA-GV | 6 | H | 2006-06-20 | 2024-06-20 | N | 9 | (zzz) | N | Watts 919QT 3/4" (H), Watts LF919QT 3/4" (H) | (N), H, I J, K L, M, N, O, P, Q
RPDA | Watts | 957RPDA-GV | 8 | H | 2010-11-15 | 2022-11-15 | N | 9 | (zzz) | N | Watts 919QT 3/4" (H), Watts LF919QT 3/4" (H) | (N),H,I,J,K,L,M,N,O,P,Q
RPDA | Watts | 957RPDA-GV | 10 | H | 2010-09-27 | 2022-09-27 | N | 9 | (zzz) | N | Watts 919QT 3/4" (H), Watts LF919QT 3/4" (H) | (N), H, I J, K L, M, N, O, P, Q
RPDA | Watts | 957ZRPDA-BF | 2.5 | VUVU | 2013-06-24 | 2022-06-24 | N | 9 | (yyy) | N | Watts 919QT 3/4" (H), Watts LF919QT 3/4" (H) | (N),H,I,J,K,L,M,N,O,P,Q
RPDA | Watts | 957ZRPDA-BF | 3 | VUVU | 2013-06-24 | 2022-06-24 | N | 9 | (yyy) | N | Watts 919QT 3/4" (H), Watts LF919QT 3/4" (H) | (N),H,I,J,K,L,M,N,O,P,Q
RPDA | Watts | 957ZRPDA-BF | 4 | VUVU | 2013-06-24 | 2022-06-24 | N | 9 | (yyy) | N | Watts 919QT 3/4" (H), Watts LF919QT 3/4" (H) | (N),H,I,J,K,L,M,N,O,P,Q
RPDA | Watts | 957ZRPDA-BF | 8 | VUVU | 2013-06-14 | 2022-06-14 | N | 9 | (yyy) | N | Watts 919QT 3/4" (H), Watts LF919QT 3/4" (H) | (N),H,I,J,K,L,M,N,O,P,Q
RPDA | Watts | 957ZRPDA-GV | 2.5 | VUVU | 2013-06-24 | 2022-06-24 | N | 9 | (zzz) | N | Watts 919QT 3/4" (H), Watts LF919QT 3/4" (H) | (N),H,I,J,K,L,M,N,O,P,Q
RPDA | Watts | 957ZRPDA-GV | 3 | VUVU | 2013-06-24 | 2022-06-24 | N | 9 | (zzz) | N | Watts 919QT 3/4" (H), Watts LF919QT 3/4" (H) | (N),H,I,J,K,L,M,N,O,P,Q
RPDA | Watts | 957ZRPDA-GV | 4 | VUVU | 2013-06-24 | 2022-06-24 | N | 9 | (zzz) | N | Watts 919QT 3/4" (H), Watts LF919QT 3/4" (H) | (N),H,I,J,K,L,M,N,O,P,Q
RPDA | Watts | 957ZRPDA-GV | 8 | VUVU | 2013-06-14 | 2022-06-14 | N | 9 | (zzz) | N | Watts 919QT 3/4" (H), Watts LF919QT 3/4" (H) | (N),H,I,J,K,L,M,N,O,P,Q
RPDA | Watts | 967NRPDA-BF | 2.5 | VUVD | 2013-06-24 | 2022-06-24 | N | 9 | (yyy) | N | Watts 919QT 3/4" (H), Watts LF919QT 3/4" (H) | (N),H,I,J,K,L,M,N,O,P,Q
RPDA | Watts | 967NRPDA-BF | 3 | VUVD | 2009-04-07 | 2024-04-07 | N | 9 | (yyy) | N | Watts 919QT 3/4" (H), Watts LF919QT 3/4" (H) | (N),H,I,J,K,L,M,N,O,P,Q
RPDA | Watts | 967NRPDA-BF | 4 | VUVD | 2010-11-15 | 2022-11-15 | N | 9 | (yyy) | N | Watts 919QT 3/4" (H), Watts LF919QT 3/4" (H) | (N),H,I,J,K,L,M,N,O,P,Q
RPDA | Watts | 967NRPDA-BF | 6 | VUVD | 2013-06-14 | 2022-06-14 | N | 9 | (yyy) | N | Watts 919QT 3/4" (H), Watts LF919QT 3/4" (H) | (N),H,I,J,K,L,M,N,O,P,Q
RPDA | Watts | 967NRPDA-GV | 2.5 | VUVD | 2009-04-07 | 2024-04-07 | N | 9 | (zzz) | N | Watts 919QT 3/4" (H), Watts LF919QT 3/4" (H) | (N),H,I,J,K,L,M,N,O,P,Q
RPDA | Watts | 967NRPDA-GV | 3 | VUVD | 2009-04-07 | 2024-04-07 | N | 9 | (zzz) | N | Watts 919QT 3/4" (H), Watts LF919QT 3/4" (H) | (N),H,I,J,K,L,M,N,O,P,Q
RPDA | Watts | 967NRPDA-GV | 4 | VUVD | 2010-11-15 | 2022-11-15 | N | 9 | (zzz) | N | Watts 919QT 3/4" (H), Watts LF919QT 3/4" (H) | (N),H,I,J,K,L,M,N,O,P,Q
RPDA | Watts | 967NRPDA-GV | 6 | VUVD | 2013-06-14 | 2022-06-14 | N | 9 | (zzz) | N | Watts 919QT 3/4" (H), Watts LF919QT 3/4" (H) | (N),H,I,J,K,L,M,N,O,P,Q
RPDA | Watts | 967RPDA-GV | 2.5 | H | 2006-06-20 | 2024-06-20 | N | 9 | (zzz) | N | Watts 919QT 3/4" (H), Watts LF919QT 3/4" (H) | (N), H, I J, K L, M, N, O, P, Q
RPDA | Watts | 967RPDA-GV | 3 | H | 2006-06-20 | 2024-06-20 | N | 9 | (zzz) | N | Watts 919QT 3/4" (H), Watts LF919QT 3/4" (H) | (N), H, I J, K L, M, N, O, P, Q
RPDA | Watts | 967RPDA-GV | 4 | H | 2006-06-20 | 2024-06-20 | N | 9 | (zzz) | N | Watts 919QT 3/4" (H), Watts LF919QT 3/4" (H) | (N), H, I J, K L, M, N, O, P, Q
RPDA | Watts | 967RPDA-GV | 6 | H | 2010-11-15 | 2022-11-15 | N | 9 | (zzz) | N | Watts 919QT 3/4" (H), Watts LF919QT 3/4" (H) | (N),H,I,J,K,L,M,N,O,P,Q
RPDA | Watts | 967RPDA-GV | 8 | H | 2010-09-27 | 2022-09-27 | N | 9 | (zzz) | N | Watts 919QT 3/4" (H), Watts LF919QT 3/4" (H) | (N), H, I J, K L, M, N, O, P, Q
RPDA | Watts | 967RPDA-GV | 10 | H | 2010-09-27 | 2022-09-27 | N | 9 | (zzz) | N | Watts 919QT 3/4" (H), Watts LF919QT 3/4" (H) | (N), H, I J, K L, M, N, O, P, Q
RPDA | Watts | 967ZRPDA-BF | 2.5 | VUVU | 2013-06-24 | 2022-06-24 | N | 9 | (yyy) | N | Watts 919QT 3/4" (H), Watts LF919QT 3/4" (H) | (N),H,I,J,K,L,M,N,O,P,Q
RPDA | Watts | 967ZRPDA-BF | 3 | VUVU | 2013-06-24 | 2022-06-24 | N | 9 | (yyy) | N | Watts 919QT 3/4" (H), Watts LF919QT 3/4" (H) | (N),H,I,J,K,L,M,N,O,P,Q
RPDA | Watts | 967ZRPDA-BF | 6 | VUVU | 2013-06-14 | 2022-06-14 | N | 9 | (yyy) | N | Watts 919QT 3/4" (H), Watts LF919QT 3/4" (H) | (N),H,I,J,K,L,M,N,O,P,Q
RPDA | Watts | 967ZRPDA-GV | 2.5 | VUVU | 2013-06-24 | 2022-06-24 | N | 9 | (zzz) | N | Watts 919QT 3/4" (H), Watts LF919QT 3/4" (H) | (N),H,I,J,K,L,M,N,O,P,Q
RPDA | Watts | 967ZRPDA-GV | 3 | VUVU | 2013-06-24 | 2022-06-24 | N | 9 | (zzz) | N | Watts 919QT 3/4" (H), Watts LF919QT 3/4" (H) | (N),H,I,J,K,L,M,N,O,P,Q
RPDA | Watts | 967ZRPDA-GV | 6 | VUVU | 2013-06-14 | 2022-06-14 | N | 9 | (zzz) | N | Watts 919QT 3/4" (H), Watts LF919QT 3/4" (H) | (N),H,I,J,K,L,M,N,O,P,Q
RPDA | Watts | 990RPDA | 4 | H | 1992-11-01 | 2022-11-01 | N | 8 | pp,hh,mm,uu,zz | Y | Watts 009QT 3/4 (H) | (H),A,B,C,D,E,F,G,I,J,K,L,M,N,O,P,Q,T
RPDA | Watts | 990RPDA | 8 | H | 1993-01-13 | 2023-01-13 | N | 8 | oo,gg,hh,ll,mm,pp,tt,uu | Y | Watts 009QT 3/4 (H) | (H),D,E,F,G,I,J,K,L,M,N,O,P,Q,T
RPDA | Watts | 992RPDA | 4 | H | 1992-11-01 | 2022-11-01 | N | 8 | oo | Y | Watts 009QT 3/4 (H) | (H),A,B,C,D,E,F,G,I,J,K,L,M,N,O,P,Q,T
RPDA | Watts | 992RPDA | 10 | H | 1993-01-13 | 2023-01-13 | N | 8 | oo | Y | Watts 009QT 3/4 (H) | (H),D,E,F,G,I,J,K,L,M,N,O,P,Q,T
RPDA | Watts | LF957NRPDA-BF | 2.5 | VUVD | 2014-01-08 | 2023-01-08 | Y | 9 | (zzz) | N | Watts LF919QT 3/4" (H) | (O) | Lead free compliant version identified with NSF61 mark on meter
RPDA | Watts | LF957NRPDA-BF | 3 | VUVD | 2014-01-08 | 2023-01-08 | Y | 9 | (zzz) | N | Watts LF919QT 3/4" (H) | (O) | Lead free compliant version identified with NSF61 mark on meter
RPDA | Watts | LF957NRPDA-BF | 4 | VUVD | 2014-01-08 | 2023-01-08 | Y | 9 | (zzz) | N | Watts LF919QT 3/4" (H) | (O) | Lead free compliant version identified with NSF61 mark on meter
RPDA | Watts | LF957NRPDA-GV | 2.5 | VUVD | 2014-01-08 | 2023-01-08 | Y | 9 | (zzz) | N | Watts LF919QT 3/4" (H) | (O) | Lead free compliant version identified with NSF61 mark on meter
RPDA | Watts | LF957NRPDA-GV | 3 | VUVD | 2014-01-08 | 2023-01-08 | Y | 9 | (zzz) | N | Watts LF919QT 3/4" (H) | (O) | Lead free compliant version identified with NSF61 mark on meter
RPDA | Watts | LF957NRPDA-GV | 4 | VUVD | 2014-01-08 | 2023-01-08 | Y | 9 | (zzz) | N | Watts LF919QT 3/4" (H) | (O) | Lead free compliant version identified with NSF61 mark on meter
RPDA | Watts | LF957RPDA-GV | 2.5 | H | 2014-05-15 | 2023-05-15 | Y | 9 | (zzz) | N | Watts LF919QT 3/4" (H) | (O) | Water meter identified with NSF61 mark
RPDA | Watts | LF957RPDA-GV | 3 | H | 2014-05-15 | 2023-05-15 | Y | 9 | (zzz) | N | Watts LF919QT 3/4" (H) | (O) | Water meter identified with NSF61 mark
RPDA | Watts | LF957RPDA-GV | 4 | H | 2014-05-15 | 2023-05-15 | Y | 9 | (zzz) | N | Watts LF919QT 3/4" (H) | (O) | Water meter identified with NSF61 mark
RPDA | Watts | LF957RPDA-GV | 6 | H | 2014-05-15 | 2023-05-15 | Y | 9 | (zzz) | N | Watts LF919QT 3/4" (H) | (O) | Water meter identified with NSF61 mark
RPDA | Watts | LF957RPDAGV | 8 | H | 2015-08-13 | 2024-08-13 | Y | 9 | (zzz) | N | Watts LF919QT 3/4" (H) | (M) | Water meter identified with NSF61 mark
RPDA | Watts | LF957RPDAGV | 10 | H | 2015-09-21 | 2024-09-21 | Y | 9 | (zzz) | N | Watts LF919QT 3/4" (H) | (M) | Lead free compliant version identified with NSF61 mark on meter
RPDA | Watts | LF957ZRPDA-BF | 2.5 | VUVD | 2014-01-08 | 2023-01-08 | Y | 9 | (zzz) | N | Watts LF919QT 3/4" (H) | (O) | Lead free compliant version identified with NSF61 mark on meter
RPDA | Watts | LF957ZRPDA-BF | 3 | VUVD | 2014-01-08 | 2023-01-08 | Y | 9 | (zzz) | N | Watts LF919QT 3/4" (H) | (O) | Lead free compliant version identified with NSF61 mark on meter
RPDA | Watts | LF957ZRPDA-BF | 4 | VUVD | 2014-01-08 | 2023-01-08 | Y | 9 | (zzz) | N | Watts LF919QT 3/4" (H) | (O) | Lead free compliant version identified with NSF61 mark on meter
RPDA | Watts | LF957ZRPDA-GV | 2.5 | VUVD | 2014-01-08 | 2023-01-08 | Y | 9 | (zzz) | N | Watts LF919QT 3/4" (H) | (O) | Lead free compliant version identified with NSF61 mark on meter
RPDA | Watts | LF957ZRPDA-GV | 3 | VUVD | 2014-01-08 | 2023-01-08 | Y | 9 | (zzz) | N | Watts LF919QT 3/4" (H) | (O) | Lead free compliant version identified with NSF61 mark on meter
RPDA | Watts | LF957ZRPDA-GV | 4 | VUVD | 2014-01-08 | 2023-01-08 | Y | 9 | (zzz) | N | Watts LF919QT 3/4" (H) | (O) | Lead free compliant version identified with NSF61 mark on meter
RPDA | Wilkins | 375ADA | 2.5 | H | 2008-10-20 | 2023-10-20 | N | 9 | (qqq),ttt,www,yyy,zzz,uuuu,vvvv,xxxx,yyyy,kkkkk,lllll,iiiiii,jjjjjj,llllll,mmmmmm | N | Wilkins 975XLD 3/4 (H) | (M),H,I,J,K,L,N,O,P,Q
RPDA | Wilkins | 375ADA | 2.5 | H | 2014-02-18 | 2023-02-18 | Y | 9 | (qqq),ttt,www,yyy,uuuu,vvvv,xxxx,yyyy,kkkkk,lllll,iiiiii,jjjjjj,llllll,mmmmmm | N | Wilkins 975XLD 3/4 (H) | (O), M | Lead free compliant version: Starting Serial # Y09616; By-pass Assembly Starting Serial # 3863325 and identified with NSF61 mark on meter
RPDA | Wilkins | 375ADA | 3 | H | 2008-10-20 | 2023-10-20 | N | 9 | (qqq),ttt,www,yyy,zzz,uuuu,vvvv,xxxx,yyyy,kkkkk,lllll,iiiiii,jjjjjj,llllll,mmmmmm | N | Wilkins 975XLD 3/4 (H) | (M),H,I,J,K,L,N,O,P,Q
RPDA | Wilkins | 375ADA | 3 | H | 2014-02-18 | 2023-02-18 | Y | 9 | (qqq),ttt,www,yyy,uuuu,vvvv,xxxx,yyyy,kkkkk,lllll,iiiiii,jjjjjj,llllll,mmmmmm | N | Wilkins 975XLD 3/4 (H) | (O), M | Lead free compliant version: Starting Serial # Y09616; By-pass Assembly Starting Serial # 3863325 and identified with NSF61 mark on meter
RPDA | Wilkins | 375ADA | 4 | H | 2004-06-02 | 2022-06-02 | N | 9 | (qqq),ttt,www,yyy,zzz,eeee,uuuu,vvvv,xxxx,yyyy,kkkkk,lllll,iiiiii,jjjjjj,llllll,mmmmmm | N | Wilkins 975XLD 3/4" (H) | (M),B,C,D,E,F,G,H,I,J,K,L,N,O,P,Q,T
RPDA | Wilkins | 375ADA | 4 | H | 2014-02-18 | 2023-02-18 | Y | 9 | (qqq),ttt,www,yyy,xxxx,yyyy,kkkkk,lllll,llllll,mmmmmm | N | Wilkins 975XLD 3/4" (H) | (O), M | Lead free compliant version: Starting Serial # Y09616; By-pass Assembly Starting Serial # 3863325 and identified with NSF61 mark on meter
RPDA | Wilkins | 375ADA | 6 | H | 2003-11-25 | 2024-11-25 | N | 9 | (qqq),ttt,www,yyy,zzz,eeee,uuuu,vvvv,xxxx,yyyy,kkkkk,lllll,iiiiii,jjjjjj,llllll,mmmmmm | N | Wilkins 975XLD 3/4 (H) | (M),C,D,E,F,G,H,I,J,K,L,N,O,P,Q,T
RPDA | Wilkins | 375ADA | 6 | H | 2014-02-18 | 2023-02-18 | Y | 9 | (qqq),ttt,www,yyy,xxxx,yyyy,kkkkk,lllll,llllll,mmmmmm | N | Wilkins 975XLD 3/4 (H) | (O), M | Lead free compliant version: Starting Serial # Y09616; By-pass Assembly Starting Serial # 3863325 and identified with NSF61 mark on meter
RPDA | Wilkins | 375ADA | 8 | H | 2004-06-15 | 2022-06-15 | N | 9 | (qqq),ttt,www,yyy,zzz,eeee,uuuu,vvvv,xxxx,yyyy,kkkkk,lllll,iiiiii,jjjjjj,llllll,mmmmmm | N | Wilkins 975XLD 3/4" (H) | (N),G,H,I,J,K,L,N,O,P,Q,T
RPDA | Wilkins | 375ADA | 8 | H | 2014-02-18 | 2023-02-18 | Y | 9 | (qqq),ttt,www,yyy,xxxx,yyyy,kkkkk,lllll,llllll,mmmmmm | N | Wilkins 975XLD 3/4" (H) | (O), M | Lead free compliant version: Starting Serial # Y09616; By-pass Assembly Starting Serial # 3863325 and identified with NSF61 mark on meter
RPDA | Wilkins | 375ADA | 10 | H | 2009-03-11 | 2024-03-11 | N | 9 | (qqq),ttt,www,yyy,zzz,eeee,uuuu,vvvv,xxxx,yyyy,kkkkk,lllll,iiiiii,jjjjjj,llllll,mmmmmm | N | Wilkins 975XLD 3/4" (H) | (N),H,I,J,K,L,M,N,O,P,Q
RPDA | Wilkins | 375ADA | 10 | H | 2014-02-18 | 2023-02-18 | Y | 9 | (qqq),ttt,www,yyy,xxxx,yyyy,kkkkk,lllll,llllll,mmmmmm | N | Wilkins 975XLD 3/4" (H) | (O), M | Lead free compliant version: Starting Serial # Y09616; By-pass Assembly Starting Serial # 3863325 and identified with NSF61 mark on meter
RPDA | Wilkins | 375ADAR | 2.5 | H | 2010-06-16 | 2022-06-16 | N | 9 | (qqq),ttt,www,yyy,zzz,uuuu,vvvv,xxxx,yyyy,kkkkk,lllll,iiiiii,jjjjjj,llllll,mmmmmm | N | Wilkins 975XLD 3/4 (H) | (M),H,I,J,K,L,N,O,P,Q | Integral grooved spool between the #2 ck and #2 SOV - assembly length: min. 34 1/4" and max. 47 1/8"
RPDA | Wilkins | 375ADAR | 2.5 | H | 2014-02-18 | 2023-02-18 | Y | 9 | (qqq),ttt,www,yyy,uuuu,vvvv,xxxx,yyyy,kkkkk,lllll,iiiiii,jjjjjj,llllll,mmmmmm | N | Wilkins 975XLD 3/4 (H) | (O), M | Integral grooved spool between the #2 ck and #2 SOV - assembly length: min. 34 1/4" and max. 47 1/8" and Lead free compliant version: Starting Serial # T00466; By-pass Assembly Starting Serial # 3863325 and identified with NSF61 mark on meter
RPDA | Wilkins | 375ADAR | 3 | H | 2010-06-16 | 2022-06-16 | N | 9 | (qqq),ttt,www,yyy,zzz,uuuu,vvvv,xxxx,yyyy,kkkkk,lllll,iiiiii,jjjjjj,llllll,mmmmmm | N | Wilkins 975XLD 3/4 (H) | (M),H,I,J,K,L,N,O,P,Q | Integral grooved spool between the #2 ck and #2 SOV - assembly length: min. 34 3/4" and max. 48 1/8"
RPDA | Wilkins | 375ADAR | 3 | H | 2014-02-18 | 2023-02-18 | Y | 9 | (qqq),ttt,www,yyy,uuuu,vvvv,xxxx,yyyy,kkkkk,lllll,iiiiii,jjjjjj,llllll,mmmmmm | N | Wilkins 975XLD 3/4 (H) | (O), M | Integral grooved spool between the #2 ck and #2 SOV - assembly length: min. 34 3/4" and max. 48 1/8" and Lead free compliant version: Starting Serial # T00466; By-pass Assembly Starting Serial # 3863325 and identified with NSF61 mark on meter
RPDA | Wilkins | 375ADAR | 4 | H | 2010-03-25 | 2022-03-25 | N | 9 | (qqq),ttt,www,yyy,zzz,eeee,uuuu,vvvv,xxxx,yyyy,kkkkk,lllll,iiiiii,jjjjjj,llllll,mmmmmm | N | Wilkins 975XLD 3/4 (H) | (M),A,B,C,D,E,F,G,H,I,J,K,L,N,O,P,Q,T | Integral grooved spool between the #2 ck and #2 SOV - assembly length: min. 35 3/4" and max. 62 1/4"
RPDA | Wilkins | 375ADAR | 4 | H | 2014-02-18 | 2023-02-18 | Y | 9 | (qqq),ttt,www,yyy,xxxx,yyyy,kkkkk,lllll,llllll,mmmmmm | N | Wilkins 975XLD 3/4 (H) | (O), M | Integral grooved spool between the #2 ck and #2 SOV - assembly length: min. 35 3/4" and max. 62 1/4" and Lead free compliant version: Starting Serial # T00466; By-pass Assembly Starting Serial # 3863325 and identified with NSF61 mark on meter
RPDA | Wilkins | 375ADAR | 6 | H | 2010-03-25 | 2022-03-25 | N | 9 | (qqq),ttt,www,yyy,zzz,eeee,uuuu,vvvv,xxxx,yyyy,kkkkk,lllll,iiiiii,jjjjjj,llllll,mmmmmm | N | Wilkins 975XLD 3/4 (H) | (M),A,B,C,D,E,F,G,H,I,J,K,L,N,O,P,Q,T | Integral grooved spool between the #2 ck and #2 SOV - assembly length: min. 42 1/2" and max. 71 1/4"
RPDA | Wilkins | 375ADAR | 6 | H | 2014-02-18 | 2023-02-18 | Y | 9 | (qqq),ttt,www,yyy,xxxx,yyyy,kkkkk,lllll,llllll,mmmmmm | N | Wilkins 975XLD 3/4 (H) | (O), M | Integral grooved spool between the #2 ck and #2 SOV - assembly length: min. 42 1/2" and max. 71 1/4" and Lead free compliant version: Starting Serial # T00466; By-pass Assembly Starting Serial # 3863325 and identified with NSF61 mark on meter
RPDA | Wilkins | 375ADAR | 8 | H | 2010-03-25 | 2022-03-25 | N | 9 | (qqq),ttt,www,yyy,zzz,eeee,uuuu,vvvv,xxxx,yyyy,kkkkk,lllll,iiiiii,jjjjjj,llllll,mmmmmm | N | Wilkins 975XLD 3/4 (H) | (M),A,B,C,D,E,F,G,H,I,J,K,L,N,O,P,Q,T | Integral grooved spool between the #2 ck and #2 SOV - assembly length: min. 57 7/8" and max. 86"
RPDA | Wilkins | 375ADAR | 8 | H | 2014-02-18 | 2023-02-18 | Y | 9 | (qqq),ttt,www,yyy,xxxx,yyyy,kkkkk,lllll,llllll,mmmmmm | N | Wilkins 975XLD 3/4 (H) | (O), M | Integral grooved spool between the #2 ck and #2 SOV - assembly length: min. 57 7/8" and max. 86" and Lead free compliant version: Starting Serial # T00466; By-pass Assembly Starting Serial # 3863325 and identified with NSF61 mark on meter
RPDA | Wilkins | 375ADAR | 10 | H | 2010-03-25 | 2022-03-25 | N | 9 | (qqq),ttt,www,yyy,zzz,eeee,uuuu,vvvv,xxxx,yyyy,kkkkk,lllll,iiiiii,jjjjjj,llllll,mmmmmm | N | Wilkins 975XLD 3/4 (H) | (M),A,B,C,D,E,F,G,H,I,J,K,L,N,O,P,Q,T | Integral grooved spool between the #2 ck and #2 SOV - assembly length: min. 61 3/8" and max. 100 5/8"
RPDA | Wilkins | 375ADAR | 10 | H | 2014-02-18 | 2023-02-18 | Y | 9 | (qqq),ttt,www,yyy,xxxx,yyyy,kkkkk,lllll,llllll,mmmmmm | N | Wilkins 975XLD 3/4 (H) | (O), M | Integral grooved spool between the #2 ck and #2 SOV - assembly length: min. 61 3/8" and max. 100 5/8" and Lead free compliant version: Starting Serial # T00466; By-pass Assembly Starting Serial # 3863325 and identified with NSF61 mark on meter
RPDA | Wilkins | 375ASTDA | 2.5 | H | 2013-06-14 | 2022-06-14 | N | 10 | (yyy),qqq,ttt,uuuu,vvvv,xxxx,yyyy,kkkkk,lllll,iiiiii,jjjjjj,llllll,mmmmmm | N | Wilkins 975XLD 3/4 (H) | (M),H,I,J,K,L,N,O,P,Q
RPDA | Wilkins | 375ASTDA | 2.5 | H | 2014-02-20 | 2023-02-20 | Y | 10 | (yyy),qqq,ttt,uuuu,vvvv,xxxx,yyyy,kkkkk,lllll,iiiiii,jjjjjj,llllll,mmmmmm | N | Wilkins 975XLD 3/4 (H) | (O), M | Lead free compliant version: By-pass Assembly Starting Serial # 3863325 and identified with NSF61 mark on meter
RPDA | Wilkins | 375ASTDA | 3 | H | 2013-06-14 | 2022-06-14 | N | 10 | (yyy),qqq,ttt,uuuu,vvvv,xxxx,yyyy,kkkkk,lllll,iiiiii,jjjjjj,llllll,mmmmmm | N | Wilkins 975XLD 3/4 (H) | (M),H,I,J,K,L,N,O,P,Q
RPDA | Wilkins | 375ASTDA | 3 | H | 2014-02-20 | 2023-02-20 | Y | 10 | (yyy),qqq,ttt,uuuu,vvvv,xxxx,yyyy,kkkkk,lllll,iiiiii,jjjjjj,llllll,mmmmmm | N | Wilkins 975XLD 3/4 (H) | (O), M | Lead free compliant version: By-pass Assembly Starting Serial # 3863325 and identified with NSF61 mark on meter
RPDA | Wilkins | 375ASTDA | 4 | H | 2013-06-14 | 2022-06-14 | N | 10 | (yyy),qqq,ttt,uuuu,vvvv,xxxx,yyyy,kkkkk,lllll,iiiiii,jjjjjj,llllll,mmmmmm | N | Wilkins 975XLD 3/4" (H) | (M),H,I,J,K,L,N,O,P,Q
RPDA | Wilkins | 375ASTDA | 4 | H | 2014-02-20 | 2023-02-20 | Y | 10 | (yyy),qqq,ttt,uuuu,vvvv,xxxx,yyyy,kkkkk,lllll,iiiiii,jjjjjj,llllll,mmmmmm | N | Wilkins 975XLD 3/4" (H) | (O), M | Lead free compliant version: By-pass Assembly Starting Serial # 3863325 and identified with NSF61 mark on meter
RPDA | Wilkins | 375ASTDA | 6 | H | 2014-09-18 | 2023-09-18 | Y | 10 | (yyyy),ttt,www,yyy,uuuu,vvvv,xxxx,kkkkk,lllll,iiiiii,jjjjjj,llllll,mmmmmm | N | Wilkins 975XLD 3/4" (H) | (O), M
RPDA | Wilkins | 375ASTDA | 8 | H | 2014-09-18 | 2023-09-18 | Y | 10 | (yyyy),ttt,www,yyy,uuuu,vvvv,xxxx,kkkkk,lllll,iiiiii,jjjjjj,llllll,mmmmmm | N | Wilkins 975XLD 3/4" (H) | (O), M
RPDA | Wilkins | 375ASTDA | 10 | H | 2014-09-18 | 2023-09-18 | Y | 10 | (yyyy),ttt,www,yyy,uuuu,vvvv,xxxx,kkkkk,lllll,iiiiii,jjjjjj,llllll,mmmmmm | N | Wilkins 975XLD 3/4" (H) | (O)
RPDA | Wilkins | 375ASTDAR | 2.5 | H | 2014-10-09 | 2023-10-09 | Y | 10 | (yyyy),ttt,www,yyy,uuuu,vvvv,xxxx,kkkkk,lllll,iiiiii,jjjjjj,llllll,mmmmmm | N | Wilkins 975XLD 3/4" (H) | (O), M | Integral grooved spool between the #2 ck and #2 SOV - assembly length: min. 31" and max. 47 1/8"
RPDA | Wilkins | 375ASTDAR | 3 | H | 2014-10-09 | 2023-10-09 | Y | 10 | (yyyy),ttt,www,yyy,uuuu,vvvv,xxxx,kkkkk,lllll,iiiiii,jjjjjj,llllll,mmmmmm | N | Wilkins 975XLD 3/4" (H) | (O), M | Integral grooved spool between the #2 ck and #2 SOV - assembly length: min. 31 1/2" and max. 48 1/8"
RPDA | Wilkins | 375ASTDAR | 4 | H | 2014-10-09 | 2023-10-09 | Y | 10 | (yyyy),ttt,www,yyy,uuuu,vvvv,xxxx,kkkkk,lllll,iiiiii,jjjjjj,llllll,mmmmmm | N | Wilkins 975XLD 3/4" (H) | (O), M | Integral grooved spool between the #2 ck and #2 SOV - assembly length: min. 32 5/8" and max. 62 1/4"
RPDA | Wilkins | 375ASTDAR | 6 | H | 2014-09-18 | 2023-09-18 | Y | 10 | (yyyy),ttt,www,yyy,uuuu,vvvv,xxxx,kkkkk,lllll,iiiiii,jjjjjj,llllll,mmmmmm | N | Wilkins 975XLD 3/4" (H) | (O), M | Integral grooved spool between the #2 ck and #2 SOV - assembly length: min. 39" and max. 71 1/4"
RPDA | Wilkins | 375ASTDAR | 8 | H | 2014-09-18 | 2023-09-18 | Y | 10 | (yyyy),ttt,www,yyy,uuuu,vvvv,xxxx,kkkkk,lllll,iiiiii,jjjjjj,llllll,mmmmmm | N | Wilkins 975XLD 3/4" (H) | (O), M | Integral grooved spool between the #2 ck and #2 SOV - assembly length: min. 48 3/4" and max. 86"
RPDA | Wilkins | 375ASTDAR | 10 | H | 2014-09-18 | 2023-09-18 | Y | 10 | (yyyy),ttt,www,yyy,uuuu,vvvv,xxxx,kkkkk,lllll,iiiiii,jjjjjj,llllll,mmmmmm | N | Wilkins 975XLD 3/4" (H) | (O) | Integral grooved spool between the #2 ck and #2 SOV - assembly length: min. 52 5/8" and max. 100 5/8"
RPDA | Wilkins | 375DA | 2.5 | H | 2002-10-08 | 2023-10-08 | N | 9 | (hh),ff,mm,uu,zz,vvvv,wwww,yyyy,zzzz,kkkkk,jjjjjj,kkkkkk,mmmmmm,nnnnnn | N | Wilkins 975XLD 3/4 (H) | (M),C,D,E,F,G,H,I,J,K,L,N,O,P,Q,T
RPDA | Wilkins | 375DA | 2.5 | H | 2014-02-18 | 2023-02-18 | Y | 9 | (hh),qqq,vvv,www,yyyy,zzzz,kkkkk,mmmmmm,nnnnnn | N | Wilkins 975XLD 3/4 (H) | (O), M | Lead free compliant version: Starting Serial # M08452; By-pass Assembly Starting Serial # 3863325 and identified with NSF61 mark on meter
RPDA | Wilkins | 375DA | 3 | H | 2002-10-08 | 2023-10-08 | N | 9 | (hh),ff,mm,uu,zz,vvvv,wwww,yyyy,zzzz,kkkkk,jjjjjj,kkkkkk,mmmmmm,nnnnnn | N | Wilkins 975XLD 3/4 (H) | (M),C,D,E,F,G,H,I,J,K,L,N,O,P,Q,T
RPDA | Wilkins | 375DA | 3 | H | 2014-02-18 | 2023-02-18 | Y | 9 | (hh),qqq,vvv,www,yyyy,zzzz,kkkkk,mmmmmm,nnnnnn | N | Wilkins 975XLD 3/4 (H) | (O), M | Lead free compliant version: Starting Serial # M08452; By-pass Assembly Starting Serial # 3863325 and identified with NSF61 mark on meter
RPDA | Wilkins | 375DA | 4 | H | 2000-12-13 | 2024-12-13 | N | 9 | (hh),ff,mm,uu,zz,qqq,vvv,www.zzz,eeee,vvvv,wwww,yyyy,zzzz,kkkkk,jjjjjj,kkkkkk,mmmmmm,nnnnnn | N | Wilkins 975XLD 3/4 (H) | (M),C,D,E,F,G,H,I,J,K,L,N,O,P,Q,T
RPDA | Wilkins | 375DA | 4 | H | 2014-02-18 | 2023-02-18 | Y | 9 | (hh),qqq,vvv,www,yyyy,zzzz,kkkkk,mmmmmm,nnnnnn | N | Wilkins 975XLD 3/4 (H) | (O), M | Lead free compliant version: Starting Serial # M08452; By-pass Assembly Starting Serial # 3863325 and identified with NSF61 mark on meter
RPDA | Wilkins | 375DA | 6 | H | 2001-05-31 | 2022-05-31 | N | 9 | (hh),ff,mm,uu,zz,qqq,vvv,www.zzz,eeee,vvvv,wwww,yyyy,zzzz,kkkkk,jjjjjj,kkkkkk,mmmmmm,nnnnnn | N | Wilkins 975XLD 3/4 (H) | (N),C,D,E,F,G,H,I,J,K,L,M,O,P,Q,T
RPDA | Wilkins | 375DA | 6 | H | 2014-02-18 | 2023-02-18 | Y | 9 | (hh),qqq,vvv,www,yyyy,zzzz,kkkkk,mmmmmm,nnnnnn | N | Wilkins 975XLD 3/4 (H) | (O), M | Lead free compliant version: Starting Serial # M08452; By-pass Assembly Starting Serial # 3863325 and identified with NSF61 mark on meter
RPDA | Wilkins | 375DA | 8 | H | 2004-06-15 | 2022-06-15 | N | 9 | (hh),ff,mm,uu,zz,qqq,vvv,www.zzz,eeee,vvvv,wwww,yyyy,zzzz,kkkkk,jjjjjj,kkkkkk,mmmmmm,nnnnnn | N | Wilkins 975XLD 3/4" (H) | (N),G,H,I,J,K,L,M,O,P,Q,T
RPDA | Wilkins | 375DA | 8 | H | 2014-02-18 | 2023-02-18 | Y | 9 | (hh),qqq,vvv,www,yyyy,zzzz,kkkkk,mmmmmm,nnnnnn | N | Wilkins 975XLD 3/4" (H) | (O), M | Lead free compliant version: Starting Serial # M08452; By-pass Assembly Starting Serial # 3863325 and identified with NSF61 mark on meter
RPDA | Wilkins | 375DA | 10 | H | 2004-11-22 | 2022-11-22 | N | 9 | (hh),ff,mm,uu,zz,qqq,vvv,www.zzz,eeee,vvvv,wwww,yyyy,zzzz,kkkkk,jjjjjj,kkkkkk,mmmmmm,nnnnnn | N | Wilkins 975XLD 3/4" (H) | (N),G,H,I,J,K,L,M,O,P,Q,T
RPDA | Wilkins | 375DA | 10 | H | 2014-02-18 | 2023-02-18 | Y | 9 | (hh),qqq,vvv,www,yyyy,zzzz,kkkkk,mmmmmm,nnnnnn | N | Wilkins 975XLD 3/4" (H) | (O), M | Lead free compliant version: Starting Serial # M08452; By-pass Assembly Starting Serial # 3863325 and identified with NSF61 mark on meter
RPDA | Wilkins | 475DA | 4 | VUVD | 2001-03-20 | 2022-03-20 | N | 9 | (qqq),ttt,www,yyy,zzz,eeee,uuuu,vvvv,xxxx,yyyy,kkkkk,lllll,iiiiii,jjjjjj,llllll,mmmmmm | N | Wilkins 975XLD 3/4 (H) | (N),F,G,H,I,J,K,L,M,O,P,Q,T
RPDA | Wilkins | 475DA | 4 | VUVD | 2014-02-18 | 2023-02-18 | Y | 9 | (hh),qqq,vvv,www,yyyy,zzzz,kkkkk,mmmmmm,nnnnnn | N | Wilkins 975XLD 3/4 (H) | (O), M | Lead free compliant version: Starting Serial # R04847; By-pass Assembly Starting Serial # 3863325 and identified with NSF61 mark on meter
RPDA | Wilkins | 475DA | 6 | VUVD | 2001-05-31 | 2022-05-31 | N | 9 | (qqq),ttt,www,yyy,zzz,eeee,uuuu,vvvv,xxxx,yyyy,kkkkk,lllll,iiiiii,jjjjjj,llllll,mmmmmm | N | Wilkins 975XLD 3/4 (H) | (N),F,G,H,I,J,K,L,M,O,P,Q,T
RPDA | Wilkins | 475DA | 6 | VUVD | 2014-02-18 | 2023-02-18 | Y | 9 | (hh),qqq,vvv,www,yyyy,zzzz,kkkkk,mmmmmm,nnnnnn | N | Wilkins 975XLD 3/4 (H) | (O), M | Lead free compliant version: Starting Serial # R04847; By-pass Assembly Starting Serial # 3863325 and identified with NSF61 mark on meter
RPDA | Wilkins | 475DA | 8 | VUVD | 2004-08-11 | 2022-08-11 | N | 9 | (qqq),ttt,www,yyy,zzz,eeee,uuuu,vvvv,xxxx,yyyy,kkkkk,lllll,iiiiii,jjjjjj,llllll,mmmmmm | N | Wilkins 975XLD 3/4 (H) | (M),B,C,D,E,F,G,H,I,J,K,L,N,O,P,Q,T
RPDA | Wilkins | 475DA | 8 | VUVD | 2014-02-18 | 2023-02-18 | Y | 9 | (hh),qqq,vvv,www,yyyy,zzzz,mmmmmm,nnnnnn | N | Wilkins 975XLD 3/4 (H) | (O), M | Lead free compliant version: Starting Serial # R04847; By-pass Assembly Starting Serial # 3863325 and identified with NSF61 mark on meter
RPDA | Wilkins | 475DAV | 4 | VUVU | 2001-03-20 | 2022-03-20 | N | 9 | (qqq),mm,ttt,www,yyy,zzz,eeee,uuuu,vvvv,xxxx,yyyy,kkkkk,lllll,iiiiii,jjjjjj,llllll,mmmmmm | N | Wilkins 975XLD 3/4 (H) | (N),F,G,H,I,J,K,L,M,O,P,Q,T
RPDA | Wilkins | 475DAV | 4 | VUVU | 2014-02-18 | 2023-02-18 | Y | 9 | (hh),qqq,vvv,www,yyyy,zzzz,kkkkk,mmmmmm,nnnnnn | N | Wilkins 975XLD 3/4 (H) | (O), M | Lead free compliant version: Starting Serial # R04847; By-pass Assembly Starting Serial # 3863325 and identified with NSF61 mark on meter
RPDA | Wilkins | 475DAV | 6 | VUVU | 2004-07-20 | 2022-07-20 | N | 9 | (qqq),mm,ttt,www,yyy,zzz,eeee,uuuu,vvvv,xxxx,yyyy,kkkkk,lllll,iiiiii,jjjjjj,llllll,mmmmmm | N | Wilkins 975XLD 3/4 (H) | (N),F,G,H,I,J,K,L,M,O,P,Q,T
RPDA | Wilkins | 475DAV | 6 | VUVU | 2014-02-18 | 2023-02-18 | Y | 9 | (hh),qqq,vvv,www,yyyy,zzzz,kkkkk,mmmmmm,nnnnnn | N | Wilkins 975XLD 3/4 (H) | (O), M | Lead free compliant version: Starting Serial # R04847; By-pass Assembly Starting Serial # 3863325 and identified with NSF61 mark on meter
RPDA | Wilkins | 475DAV | 8 | VUVU | 2004-04-24 | 2022-04-24 | N | 9 | (qqq),mm,ttt,www,yyy,zzz,eeee,uuuu,vvvv,xxxx,yyyy,kkkkk,lllll,iiiiii,jjjjjj,llllll,mmmmmm | N | Wilkins 975XLD 3/4 (H) | (M),B,C,D,E,F,G,H,I,J,K,L,N,O,P,Q,T
RPDA | Wilkins | 475DAV | 8 | VUVU | 2014-02-18 | 2023-02-18 | Y | 9 | (hh),qqq,vvv,www,yyyy,zzzz,mmmmmm,nnnnnn | N | Wilkins 975XLD 3/4 (H) | (O), M | Lead free compliant version: Starting Serial # R04847; By-pass Assembly Starting Serial # 3863325 and identified with NSF61 mark on meter
RPDA | Wilkins | 475STDA | 4 | VUVD | 2018-12-18 | 2024-12-18 | Y | 10 | (kkkkk),yyy,ssss,uuuu,vvvv,xxxx,yyyy,aaaaa,lllll,gggggg,iiiiii,jjjjjj,llllll,mmmmmm,oooooo | N | Wilkins 975XLDTCU 3/4 (H) | (O),G,H,I,J,K,L,M,N,Q,T
RPDA | Wilkins | 475STDA | 4 | VUVU | 2018-12-18 | 2024-12-18 | Y | 10 | (kkkkk),yyy,ssss,uuuu,vvvv,xxxx,yyyy,aaaaa,lllll,gggggg,iiiiii,jjjjjj,llllll,mmmmmm,oooooo | N | Wilkins 975XLDTCU 3/4 (H) | (O),G,H,I,J,K,L,M,N,Q,T
RPDA | Wilkins | 475STDA | 6 | VUVD | 2018-12-18 | 2024-12-18 | Y | 10 | (kkkkk),yyy,ssss,uuuu,vvvv,xxxx,yyyy,aaaaa,lllll,gggggg,iiiiii,jjjjjj,llllll,mmmmmm,oooooo | N | Wilkins 975XLDTCU 3/4 (H) | (O),G,H,I,J,K,L,M,N,Q,T
RPDA | Wilkins | 475STDA | 6 | VUVU | 2018-12-18 | 2024-12-18 | Y | 10 | (kkkkk),yyy,ssss,uuuu,vvvv,xxxx,yyyy,aaaaa,lllll,gggggg,iiiiii,jjjjjj,llllll,mmmmmm,oooooo | N | Wilkins 975XLDTCU 3/4 (H) | (O),G,H,I,J,K,L,M,N,Q,T
RPDA | Wilkins | 475STDA | 8 | VUVD | 2018-12-18 | 2024-12-18 | Y | 10 | (kkkkk),yyy,ssss,uuuu,vvvv,xxxx,yyyy,aaaaa,lllll,gggggg,iiiiii,jjjjjj,llllll,mmmmmm,oooooo | N | Wilkins 975XLDTCU 3/4 (H) | (O),G,H,I,J,K,L,M,N,Q,T
RPDA | Wilkins | 475STDA | 8 | VUVU | 2018-12-18 | 2024-12-18 | Y | 10 | (kkkkk),yyy,ssss,uuuu,vvvv,xxxx,yyyy,aaaaa,lllll,gggggg,iiiiii,jjjjjj,llllll,mmmmmm,oooooo | N | Wilkins 975XLDTCU 3/4 (H) | (O),G,H,I,J,K,L,M,N,Q,T
RPDA | Wilkins | 475STDA | 10 | VUVD | 2018-12-18 | 2024-12-18 | Y | 10 | (kkkkk),yyy,ssss,uuuu,vvvv,xxxx,yyyy,aaaaa,lllll,gggggg,iiiiii,jjjjjj,llllll,mmmmmm,oooooo | N | Wilkins 975XLDTCU 3/4 (H) | (O),G,H,I,J,K,L,M,N,Q,T
RPDA | Wilkins | 475STDA | 10 | VUVU | 2018-12-18 | 2024-12-18 | Y | 10 | (kkkkk),yyy,ssss,uuuu,vvvv,xxxx,yyyy,aaaaa,lllll,gggggg,iiiiii,jjjjjj,llllll,mmmmmm,oooooo | N | Wilkins 975XLDTCU 3/4 (H) | (O),G,H,I,J,K,L,M,N,Q,T
RPDA | Wilkins | 475STDAR | 4 | VUVD | 2018-12-18 | 2024-12-18 | Y | 10 | (kkkkk),yyy,ssss,uuuu,vvvv,xxxx,yyyy,aaaaa,lllll,gggggg,iiiiii,jjjjjj,llllll,mmmmmm,oooooo | N | Wilkins 975XLD 3/4 (H) | (O),G,H,I,J,K,L,M,N,Q,T
RPDA | Wilkins | 475STDAR | 4 | VUVU | 2018-12-18 | 2024-12-18 | Y | 10 | (kkkkk),yyy,ssss,uuuu,vvvv,xxxx,yyyy,aaaaa,lllll,gggggg,iiiiii,jjjjjj,llllll,mmmmmm,oooooo | N | Wilkins 975XLD 3/4 (H) | (O),G,H,I,J,K,L,M,N,Q,T
RPDA | Wilkins | 475STDAR | 6 | VUVD | 2018-12-18 | 2024-12-18 | Y | 10 | (kkkkk),yyy,ssss,uuuu,vvvv,xxxx,yyyy,aaaaa,lllll,gggggg,iiiiii,jjjjjj,llllll,mmmmmm,oooooo | N | Wilkins 975XLD 3/4 (H) | (O),G,H,I,J,K,L,M,N,Q,T
RPDA | Wilkins | 475STDAR | 6 | VUVU | 2018-12-18 | 2024-12-18 | Y | 10 | (kkkkk),yyy,ssss,uuuu,vvvv,xxxx,yyyy,aaaaa,lllll,gggggg,iiiiii,jjjjjj,llllll,mmmmmm,oooooo | N | Wilkins 975XLD 3/4 (H) | (O),G,H,I,J,K,L,M,N,Q,T
RPDA | Wilkins | 475STDAR | 8 | VUVD | 2018-12-18 | 2024-12-18 | Y | 10 | (kkkkk),yyy,ssss,uuuu,vvvv,xxxx,yyyy,aaaaa,lllll,gggggg,iiiiii,jjjjjj,llllll,mmmmmm,oooooo | N | Wilkins 975XLD 3/4 (H) | (O),G,H,I,J,K,L,M,N,Q,T
RPDA | Wilkins | 475STDAR | 8 | VUVU | 2018-12-18 | 2024-12-18 | Y | 10 | (kkkkk),yyy,ssss,uuuu,vvvv,xxxx,yyyy,aaaaa,lllll,gggggg,iiiiii,jjjjjj,llllll,mmmmmm,oooooo | N | Wilkins 975XLD 3/4 (H) | (O),G,H,I,J,K,L,M,N,Q,T
RPDA | Wilkins | 475STDAR | 10 | VUVD | 2018-12-18 | 2024-12-18 | Y | 10 | (kkkkk),yyy,ssss,uuuu,vvvv,xxxx,yyyy,aaaaa,lllll,gggggg,iiiiii,jjjjjj,llllll,mmmmmm,oooooo | N | Wilkins 975XLD 3/4 (H) | (O),G,H,I,J,K,L,M,N,Q,T
RPDA | Wilkins | 475STDAR | 10 | VUVU | 2018-12-18 | 2024-12-18 | Y | 10 | (kkkkk),yyy,ssss,uuuu,vvvv,xxxx,yyyy,aaaaa,lllll,gggggg,iiiiii,jjjjjj,llllll,mmmmmm,oooooo | N | Wilkins 975XLD 3/4 (H) | (O),G,H,I,J,K,L,M,N,Q,T
RPDA | Wilkins | 975DA | 2.5 | H | 1994-02-01 | 2024-02-01 | N | 8 | (hh),ff,uu,zz,vvvv,wwww,yyyy,zzzz | Y | Wilkins 975 3/4 (H) | (M),A,B,C,D,E,F,G,H,I,J,K,L,N,O,P,Q,T
RPDA | Wilkins | 975DA | 3 | H | 1994-02-01 | 2024-02-01 | N | 8 | (hh),ff,uu,zz,vvvv,wwww,yyyy,zzzz | Y | Wilkins 975 3/4 (H) | (M),A,B,C,D,E,F,G,H,I,J,K,L,N,O,P,Q,T
RPDA | Wilkins | 975DA | 4 | H | 1993-11-01 | 2023-11-01 | N | 8 | hh,ff,mm,uu,zz,vvvv,wwww,yyyy,zzzz | Y | Wilkins 975 3/4 (H) | (M),A,B,C,D,E,F,G,H,I,J,K,L,N,O,P,Q,T
RPDA | Wilkins | 975DA | 6 | H | 1994-03-14 | 2024-03-14 | N | 8 | hh,ff,mm,uu,zz,vvvv,wwww,yyyy,zzzz | Y | Wilkins 975 3/4 (H) | (M),A,B,C,D,E,F,G,H,I,J,K,L,N,O,P,Q,T
RPDA | Wilkins | 975DA | 8 | H | 1996-12-05 | 2023-12-05 | N | 8 | (hh),ff,uu,zz,vvvv,wwww,yyyy.zzzz | Y | Wilkins 975 3/4 (H) | (M),A,B,C,D,E,F,G,H,I,J,K,L,N,O,P,Q,T
RPDA | Wilkins | 975DA | 10 | H | 1996-12-05 | 2023-12-05 | N | 8 | (hh),ff,uu,zz,vvvv,wwww,yyyy.zzzz | Y | Wilkins 975 3/4 (H) | (M),A,B,C,D,E,F,G,H,I,J,K,L,N,O,P,Q,T
RPDA-II | Ames | Deringer 50 | 2.5 | H | 2020-03-26 | 2023-03-26 | Y | 10 | (int) | N | Backflow Direct 1/2" CV(HVD) | (O),G,H,I,J,K,L,M,N,Q,T
RPDA-II | Ames | Deringer 50 | 3 | H | 2020-03-26 | 2023-03-26 | Y | 10 | (int) | N | Backflow Direct 1/2" CV(HVD) | (O),G,H,I,J,K,L,M,N,Q,T
RPDA-II | Ames | Deringer 50 | 4 | H | 2020-03-26 | 2023-03-26 | Y | 10 | (int) | N | Backflow Direct 1/2" CV(HVD) | (O),G,H,I,J,K,L,M,N,Q,T
RPDA-II | Ames | Deringer 50 | 6 | H | 2022-08-03 |  | Y | 10 | (int) | N | Backflow Direct 1/2" CV(HVD) | (O),G,H,I,J,K,L,M,N,Q,T
RPDA-II | Ames | Deringer 50 | 8 | H | 2020-03-26 | 2023-03-26 | Y | 10 | (int) | N | Backflow Direct 1/2" CV(HVD) | (O),G,H,I,J,K,L,M,N,Q,T
RPDA-II | Ames | Deringer 50G | 2.5 | H | 2020-03-26 | 2023-03-26 | Y | 10 | (ssssss), tttttt | N | Backflow Direct 1/2" CV(HVD) | (O),G,H,I,J,K,L,M,N,Q,T
RPDA-II | Ames | Deringer 50G | 3 | H | 2020-03-26 | 2023-03-26 | Y | 10 | (ssssss), tttttt | N | Backflow Direct 1/2" CV(HVD) | (O),G,H,I,J,K,L,M,N,Q,T
RPDA-II | Ames | Deringer 50G | 4 | H | 2020-03-26 | 2023-03-26 | Y | 10 | (ssssss), tttttt | N | Backflow Direct 1/2" CV(HVD) | (O),G,H,I,J,K,L,M,N,Q,T
RPDA-II | Ames | Deringer 50G | 6 | H | 2024-10-01 |  | Y | 10 | (ssssss), tttttt
RPDA-II | Ames | Deringer 50G | 8 | H | 2020-03-26 | 2023-03-26 | Y | 10 | (ssssss), tttttt | N | Backflow Direct 1/2" CV(HVD) | (O),G,H,I,J,K,L,M,N,Q,T
RPDA-II | Ames | Deringer 50GX | 4 | H | 2024-10-01 |  | Y | 10 | (ssssss), tttttt
RPDA-II | Ames | Deringer 50GX | 6 | H | 2020-03-26 | 2023-03-26 | Y | 10 | (ssssss), tttttt | N | Backflow Direct 1/2" CV(HVD) | (O),G,H,I,J,K,L,M,N,Q,T
RPDA-II | Ames | Deringer 50X | 4 | H | 2022-08-03 |  | Y | 10 | (int) | N | Backflow Direct 1/2" CV(HVD) | (O),G,H,I,J,K,L,M,N,Q,T
RPDA-II | Ames | Deringer 50X | 6 | H | 2020-03-26 | 2023-03-26 | Y | 10 | (int) | N | Backflow Direct 1/2" CV(HVD) | (O),G,H,I,J,K,L,M,N,Q,T
RPDA-II | Apollo/Conbraco | RPDA24A | 1.5 | H | 2016-10-31 | 2022-10-31 | N | 10 | (dddddd) | N | Apollo 1/2" Model CVA4A (HVD) | (M),G,H,I,J,K,L,N,O,P,Q,T
RPDA-II | Apollo/Conbraco | RPDA24A | 2 | H | 2016-10-31 | 2022-10-31 | N | 10 | (dddddd) | N | Apollo 1/2" Model CVA4A (HVD) | (M),G,H,I,J,K,L,N,O,P,Q,T
RPDA-II | Apollo/Conbraco | RPDA2LF4A | 1.5 | H | 2016-10-31 | 2022-10-31 | N | 10 | (eeeeee) | N | Apollo 1/2" Model CVALF4A (HVD) | (M),G,H,I,J,K,L,N,O,P,Q,T
RPDA-II | Apollo/Conbraco | RPDA2LF4A | 2 | H | 2016-10-31 | 2022-10-31 | N | 10 | (eeeeee) | N | Apollo 1/2" Model CVALF4A (HVD) | (M),G,H,I,J,K,L,N,O,P,Q,T
RPDA-II | Apollo/Conbraco | RPDA2LF4A | 2.5 | H | 2017-12-15 | 2023-12-15 | Y | 10 | (xxxxx),yyy,yyyyy,zzzzz,aaaaaa,xxxxxx | N | Apollo 1/2" Model CVALF4A (HVD) | (M),G,H,I,J,K,L,N,O,P,Q,T
RPDA-II | Apollo/Conbraco | RPDA2LF4A | 3 | H | 2017-12-15 | 2023-12-15 | Y | 10 | (xxxxx),yyy,yyyyy,zzzzz,aaaaaa,xxxxxx | N | Apollo 1/2" Model CVALF4A (HVD) | (M),G,H,I,J,K,L,N,O,P,Q,T
RPDA-II | Apollo/Conbraco | RPDA2LF4A | 4 | H | 2017-12-15 | 2023-12-15 | Y | 10 | (xxxxx),yyy,yyyyy,zzzzz,aaaaaa,xxxxxx | N | Apollo 1/2" Model CVALF4A (HVD) | (M),G,H,I,J,K,L,N,O,P,Q,T
RPDA-II | Apollo/Conbraco | RPDA2LF4A | 6 | H | 2017-12-15 | 2023-12-15 | Y | 10 | (xxxxx),yyy,yyyyy,zzzzz,aaaaaa,xxxxxx | N | Apollo 1/2" Model CVALF4A (HVD) | (M),G,H,I,J,K,L,N,O,P,Q,T
RPDA-II | Apollo/Conbraco | RPDA2LF4A | 8 | H | 2017-12-15 | 2023-12-15 | Y | 10 | (xxxxx),yyy,yyyyy,zzzzz,aaaaaa,xxxxxx | N | Apollo 1/2" Model CVALF4A (HVD) | (M),G,H,I,J,K,L,N,O,P,Q,T
RPDA-II | Apollo/Conbraco | RPDA2LF4A | 10 | H | 2021-11-05 | 2024-11-05 | Y | 10 | (zzzzz), zzz,cccc,dddd,kkkk,llll,mmmm,nnnn,xxxxx, yyyyy,aaaaaa | N | Apollo 1/2" Model CVALF4A (HVD) | (M),G,H,I,J,K,L,N,O,P,Q,T
RPDA-II | Apollo/Conbraco | RPDA2LF4A | 12 | H | 2021-11-05 | 2024-11-05 | Y | 10 | (bbbbbb), ll,mm,cccccc | N | Apollo 1/2" Model CVALF4A (HVD) | (M),G,H,I,J,K,L,N,O,P,Q,T
RPDA-II | Apollo/Conbraco | RPDA2LF4AN | 10 | VUVD | 2022-04-12 |  | Y | 10 | (zzzzz), yyy,zzz,cccc,dddd,kkkk,llll,mmmm,nnnn,xxxxx, yyyyy,aaaaaa | N | Apollo 1/2" Model CVALF4A (HVD)
RPDA-II | Apollo/Conbraco | RPDA2LF4AN | 12 | VUVD | 2022-04-12 |  | Y | 10 | (bbbbbb), ll,mm,cccccc | N | Apollo 1/2" Model CVALF4A (HVD)
RPDA-II | Apollo/Conbraco | RPDA2LF4AR | 2.5 | H | 2018-03-27 | 2024-03-27 | Y | 10 | (xxxxx),zzz,cccc,dddd,kkkk,llll,mmmm,nnnn,yyyyy,zzzzz,aaaaaa | Y | Apollo 1/2" Model CVALF4A (HVD) | (M),G,H,I,J,K,L,N,O,P,Q,T | Integral Stainless Steel grooved spool between the #2 ck and #2 SOV - assembly length: min. 34" and max. 47 1/8"
RPDA-II | Apollo/Conbraco | RPDA2LF4AR | 3 | H | 2018-03-27 | 2024-03-27 | Y | 10 | (xxxxx),zzz,cccc,dddd,kkkk,llll,mmmm,nnnn,yyyyy,zzzzz,aaaaaa | Y | Apollo 1/2" Model CVALF4A (HVD) | (M),G,H,I,J,K,L,N,O,P,Q,T | Integral Stainless Steel grooved spool between the #2 ck and #2 SOV - assembly length: min. 35" and max. 48 1/8"
RPDA-II | Apollo/Conbraco | RPDA2LF4AR | 4 | H | 2018-03-27 | 2024-03-27 | Y | 10 | (xxxxx),zzz,cccc,dddd,kkkk,llll,mmmm,nnnn,yyyyy,zzzzz,aaaaaa | Y | Apollo 1/2" Model CVALF4A (HVD) | (M),G,H,I,J,K,L,N,O,P,Q,T | Integral Stainless Steel grooved spool between the #2 ck and #2 SOV - assembly length: min. 37 3/8" and max. 62 1/4"
RPDA-II | Apollo/Conbraco | RPDA2LF4AR | 6 | H | 2018-03-27 | 2024-03-27 | Y | 10 | (xxxxx),zzz,cccc,dddd,kkkk,llll,mmmm,nnnn,yyyyy,zzzzz,aaaaaa | Y | Apollo 1/2" Model CVALF4A (HVD) | (M),G,H,I,J,K,L,N,O,P,Q,T | Integral Stainless Steel grooved spool between the #2 ck and #2 SOV - assembly length: min. 46" and max. 71 1/4"
RPDA-II | Apollo/Conbraco | RPDA2LF4AR | 8 | H | 2018-03-27 | 2024-03-27 | Y | 10 | (xxxxx),zzz,cccc,dddd,kkkk,llll,mmmm,nnnn,yyyyy,zzzzz,aaaaaa | Y | Apollo 1/2" Model CVALF4A (HVD) | (M),G,H,I,J,K,L,N,O,P,Q,T | Integral Stainless Steel grooved spool between the #2 ck and #2 SOV - assembly length: min. 55 3/4" and max. 86"
RPDA-II | Apollo/Conbraco | RPDA2LF4AR | 10 | H | 2021-11-05 | 2024-11-05 | Y | 10 | (zzzzz), zzz,cccc,dddd,kkkk,llll,mmmm,nnnn,xxxxx, yyyyy,aaaaaa | Y | Apollo 1/2" Model CVALF4A (HVD) | (M),G,H,I,J,K,L,N,O,P,Q,T | Integral Stainless Steel grooved spool between the #2 ck and #2 SOV - assembly length: min. 65 3/4" and max. 100 5/8"
RPDA-II | Backflow Direct | Deringer 50 | 2.5 | H | 2017-01-20 | 2023-01-20 | Y | 10 | (int) | N | Backflow Direct 1/2" CV(HVD) | (O),G,H,I,J,K,L,M,N,Q,T
RPDA-II | Backflow Direct | Deringer 50 | 3 | H | 2017-01-20 | 2023-01-20 | Y | 10 | (int) | N | Backflow Direct 1/2" CV(HVD) | (O),G,H,I,J,K,L,M,N,Q,T
RPDA-II | Backflow Direct | Deringer 50 | 4 | H | 2017-01-20 | 2023-01-20 | Y | 10 | (int) | N | Backflow Direct 1/2" CV(HVD) | (O),G,H,I,J,K,L,M,N,Q,T
RPDA-II | Backflow Direct | Deringer 50 | 6 | H | 2022-08-03 |  | Y | 10 | (int) | N | Backflow Direct 1/2" CV(HVD) | (O),G,H,I,J,K,L,M,N,Q,T
RPDA-II | Backflow Direct | Deringer 50 | 8 | H | 2017-06-27 | 2023-06-27 | Y | 10 | (int) | N | Backflow Direct 1/2" CV(HVD) | (O),G,H,I,J,K,L,M,N,Q,T
RPDA-II | Backflow Direct | Deringer 50G | 2.5 | H | 2018-10-24 | 2024-10-24 | Y | 10 | (ssssss), tttttt | N | Backflow Direct 1/2" CV(HVD) | (O),G,H,I,J,K,L,M,N,Q,T
RPDA-II | Backflow Direct | Deringer 50G | 3 | H | 2018-10-24 | 2024-10-24 | Y | 10 | (ssssss), tttttt | N | Backflow Direct 1/2" CV(HVD) | (O),G,H,I,J,K,L,M,N,Q,T
RPDA-II | Backflow Direct | Deringer 50G | 4 | H | 2018-10-24 | 2024-10-24 | Y | 10 | (ssssss), tttttt | N | Backflow Direct 1/2" CV(HVD) | (O),G,H,I,J,K,L,M,N,Q,T
RPDA-II | Backflow Direct | Deringer 50G | 6 | H | 2024-10-01 |  | Y | 10 | (ssssss), tttttt
RPDA-II | Backflow Direct | Deringer 50G | 8 | H | 2019-03-12 | 2022-03-12 | Y | 10 | (ssssss), tttttt | N | Backflow Direct 1/2" CV(HVD) | (O),G,H,I,J,K,L,M,N,Q,T
RPDA-II | Backflow Direct | Deringer 50GX | 4 | H | 2024-10-01 |  | Y | 10 | (ssssss), tttttt
RPDA-II | Backflow Direct | Deringer 50GX | 6 | H | 2019-03-12 | 2022-03-12 | Y | 10 | (ssssss), tttttt | N | Backflow Direct 1/2" CV(HVD) | (O),G,H,I,J,K,L,M,N,Q,T
RPDA-II | Backflow Direct | Deringer 50X | 4 | H | 2022-08-03 |  | Y | 10 | (int) | N | Backflow Direct 1/2" CV(HVD) | (O),G,H,I,J,K,L,M,N,Q,T
RPDA-II | Backflow Direct | Deringer 50X | 6 | H | 2017-06-27 | 2023-06-27 | Y | 10 | (int) | N | Backflow Direct 1/2" CV(HVD) | (O),G,H,I,J,K,L,M,N,Q,T
RPDA-II | Febco | LF866 | 2.5 | H | 2015-03-20 | 2024-03-20 | Y | 10 | (mm), ll,oo,pp,zzz,cccc,dddd,eeee,ffff,gggg,nnnnn,aaaaaaa | N | Watts 3/4" LF619 (H) | (O),G,H,I,J,K,L,M,N,P,Q,T
RPDA-II | Febco | LF866 | 3 | H | 2015-03-20 | 2024-03-20 | Y | 10 | (mm), ll,oo,pp,zzz,cccc,dddd,eeee,ffff,gggg,nnnnn,aaaaaaa | N | Watts 3/4" LF619 (H) | (O),G,H,I,J,K,L,M,N,P,Q,T
RPDA-II | Febco | LF866 | 4 | H | 2015-01-26 | 2024-01-26 | Y | 10 | (mm), ll,oo,pp,zzz,cccc,dddd,eeee,ffff,gggg,nnnnn,aaaaaaa | N | Watts 3/4" LF619 (H) | (O),G,H,I,J,K,L,M,N,P,Q,T
RPDA-II | Febco | LF866 | 6 | H | 2015-03-13 | 2024-03-13 | Y | 10 | (mm), ll,oo,pp,zzz,cccc,dddd,eeee,ffff,gggg,nnnnn,aaaaaaa | N | Watts 3/4" LF619 (H) | (O),G,H,I,J,K,L,M,N,P,Q,T
RPDA-II | Febco | LF866 | 8 | H | 2015-07-07 | 2024-07-07 | Y | 10 | (mm), ll,oo,pp,zzz,cccc,dddd,eeee,ffff,gggg,nnnnn,aaaaaaa | N | Watts 3/4" LF619 (H) | (O),G,H,I,J,K,L,M,N,P,Q,T
RPDA-II | Febco | LF866 | 10 | H | 2015-07-07 | 2024-07-07 | Y | 10 | (mm), ll,oo,pp,zzz,cccc,dddd,eeee,ffff,gggg,nnnnn | N | Watts 3/4" LF619 (H) | (O),G,H,I,J,K,L,M,N,P,Q,T
RPDA-II | Febco | LF886V | 2.5 | VUVD | 2015-03-20 | 2024-03-20 | Y | 10 | (mm), ll,oo,pp,zzz,cccc,dddd,eeee,ffff,gggg,nnnnn,aaaaaaa | N | Watts 3/4" LF619 (HVU) | (O),G,H,I,J,K,L,M,N,P,Q,T
RPDA-II | Febco | LF886V | 2.5 | VUVU | 2015-03-20 | 2024-03-20 | Y | 10 | (mm), ll,oo,pp,zzz,cccc,dddd,eeee,ffff,gggg,nnnnn,aaaaaaa | N | Watts 3/4" LF619 (HVD) | (O),G,H,I,J,K,L,M,N,P,Q,T
RPDA-II | Febco | LF886V | 3 | VUVD | 2015-03-20 | 2024-03-20 | Y | 10 | (mm), ll,oo,pp,zzz,cccc,dddd,eeee,ffff,gggg,nnnnn,aaaaaaa | N | Watts 3/4" LF619 (HVU) | (O),G,H,I,J,K,L,M,N,P,Q,T
RPDA-II | Febco | LF886V | 3 | VUVU | 2015-03-20 | 2024-03-20 | Y | 10 | (mm), ll,oo,pp,zzz,cccc,dddd,eeee,ffff,gggg,nnnnn,aaaaaaa | N | Watts 3/4" LF619 (HVD) | (O),G,H,I,J,K,L,M,N,P,Q,T
RPDA-II | Febco | LF886V | 4 | VUVD | 2015-01-26 | 2024-01-26 | Y | 10 | (mm), ll,oo,pp,zzz,cccc,dddd,eeee,ffff,gggg,nnnnn,aaaaaaa | N | Watts 3/4" LF619 (HVU) | (O),G,H,I,J,K,L,M,N,P,Q,T
RPDA-II | Febco | LF886V | 4 | VUVU | 2015-01-26 | 2024-01-26 | Y | 10 | (mm), ll,oo,pp,zzz,cccc,dddd,eeee,ffff,gggg,nnnnn,aaaaaaa | N | Watts 3/4" LF619 (HVD) | (O),G,H,I,J,K,L,M,N,P,Q,T
RPDA-II | Febco | LF886V | 6 | VUVD | 2015-01-26 | 2024-01-26 | Y | 10 | (mm), ll,oo,pp,zzz,cccc,dddd,eeee,ffff,gggg,nnnnn,aaaaaaa | N | Watts 3/4" LF619 (HVU) | (O),G,H,I,J,K,L,M,N,P,Q,T
RPDA-II | Febco | LF886V | 6 | VUVU | 2015-01-26 | 2024-01-26 | Y | 10 | (mm), ll,oo,pp,zzz,cccc,dddd,eeee,ffff,gggg,nnnnn,aaaaaaa | N | Watts 3/4" LF619 (HVD) | (O),J,K,L,M,N,P,Q
RPDA-II | Febco | LF886V | 8 | VUVD | 2015-07-07 | 2024-07-07 | Y | 10 | (mm), ll,oo,pp,zzz,cccc,dddd,eeee,ffff,gggg,nnnnn,aaaaaaa | N | Watts 3/4" LF619 (HVU) | (O)
RPDA-II | Febco | LF886V | 8 | VUVU | 2015-07-07 | 2024-07-07 | Y | 10 | (mm), ll,oo,pp,zzz,cccc,dddd,eeee,ffff,gggg,nnnnn,aaaaaaa | N | Watts 3/4" LF619 (HVD) | (O)
RPDA-II | Febco | LF886V | 10 | VUVD | 2018-05-29 | 2024-05-29 | Y | 10 | (mm),ll,oo,pp,zzz,cccc,dddd,eeee,ffff,gggg,nnnnn | N | Watts 3/4" LF619 (HVU) | (O),G,H,I,J,K,L,M,N,P,Q,T
RPDA-II | Febco | LF886V | 10 | VUVU | 2018-05-29 | 2024-05-29 | Y | 10 | (mm),ll,oo,pp,zzz,cccc,dddd,eeee,ffff,gggg,nnnnn | N | Watts 3/4" LF619 (HVD) | (O),G,H,I,J,K,L,M,N,P,Q,T
RPDA-II | Febco | LF886W | 4 | VUVD | 2020-03-26 | 2023-03-26 | Y | 10 | (mm), ll,oo,pp,zzz,cccc,dddd,eeee,ffff,gggg,nnnnn,aaaaaaa | N | Watts 3/4" LF619 (HVU) | (O),G,H,I,J,K,L,M,N,P,Q,T
RPDA-II | Febco | LF886W | 4 | VUVU | 2020-03-26 | 2023-03-26 | Y | 10 | (mm), ll,oo,pp,zzz,cccc,dddd,eeee,ffff,gggg,nnnnn,aaaaaaa | N | Watts 3/4" LF619 (HVD) | (O),G,H,I,J,K,L,M,N,P,Q,T
RPDA-II | Febco | LF886W | 6 | VUVD | 2020-03-26 | 2023-03-26 | Y | 10 | (mm), ll,oo,pp,zzz,cccc,dddd,eeee,ffff,gggg,nnnnn,aaaaaaa | N | Watts 3/4" LF619 (HVU) | (O),G,H,I,J,K,L,M,N,P,Q,T
RPDA-II | Febco | LF886W | 6 | VUVU | 2020-03-26 | 2023-03-26 | Y | 10 | (mm), ll,oo,pp,zzz,cccc,dddd,eeee,ffff,gggg,nnnnn,aaaaaaa | N | Watts 3/4" LF619 (HVD) | (O),G,H,I,J,K,L,M,N,P,Q,T
RPDA-II | Febco | LF886W | 8 | VUVD | 2020-05-15 | 2023-05-15 | Y | 10 | (mm), ll,oo,pp,zzz,cccc,dddd,eeee,ffff,gggg,nnnnn,aaaaaaa | N | Watts 3/4" LF619 (HVU) | (O)
RPDA-II | Febco | LF886W | 8 | VUVU | 2020-05-15 | 2023-05-15 | Y | 10 | (mm), ll,oo,pp,zzz,cccc,dddd,eeee,ffff,gggg,nnnnn,aaaaaaa | N | Watts 3/4" LF619 (HVD) | (O)
RPDA-II | Febco | LF886W | 10 | VUVD | 2020-05-15 | 2023-05-15 | Y | 10 | (mm),ll,oo,pp,zzz,cccc,dddd,eeee,ffff,gggg,nnnnn | N | Watts 3/4" LF619 (HVU) | (O),G,H,I,J,K,L,M,N,P,Q,T
RPDA-II | Febco | LF886W | 10 | VUVU | 2020-05-15 | 2023-05-15 | Y | 10 | (mm),ll,oo,pp,zzz,cccc,dddd,eeee,ffff,gggg,nnnnn | N | Watts 3/4" LF619 (HVD) | (O),G,H,I,J,K,L,M,N,P,Q,T
RPDA-II | Febco | LF886WZ | 4 | VUVD | 2020-03-26 | 2023-03-26 | Y | 10 | (mm), ll,oo,pp,zzz,cccc,dddd,eeee,ffff,gggg,nnnnn,aaaaaaa | N | Watts 3/4" LF619 (HVU) | (O),G,H,I,J,K,L,M,N,P,Q,T
RPDA-II | Febco | LF886WZ | 4 | VUVU | 2020-03-26 | 2023-03-26 | Y | 10 | (mm), ll,oo,pp,zzz,cccc,dddd,eeee,ffff,gggg,nnnnn,aaaaaaa | N | Watts 3/4" LF619 (HVD) | (O),G,H,I,J,K,L,M,N,P,Q,T
RPDA-II | Febco | LF886WZ | 6 | VUVD | 2020-03-26 | 2023-03-26 | Y | 10 | (mm), ll,oo,pp,zzz,cccc,dddd,eeee,ffff,gggg,nnnnn,aaaaaaa | N | Watts 3/4" LF619 (HVU) | (O),G,H,I,J,K,L,M,N,P,Q,T
RPDA-II | Febco | LF886WZ | 6 | VUVU | 2020-03-26 | 2023-03-26 | Y | 10 | (mm), ll,oo,pp,zzz,cccc,dddd,eeee,ffff,gggg,nnnnn,aaaaaaa | N | Watts 3/4" LF619 (HVD) | (O),G,H,I,J,K,L,M,N,P,Q,T
RPDA-II | Febco | LF886WZ | 8 | VUVD | 2020-05-15 | 2023-05-15 | Y | 10 | (mm), ll,oo,pp,zzz,cccc,dddd,eeee,ffff,gggg,nnnnn,aaaaaaa | N | Watts 3/4" LF619 (HVU) | (O)
RPDA-II | Febco | LF886WZ | 8 | VUVU | 2020-05-15 | 2023-05-15 | Y | 10 | (mm), ll,oo,pp,zzz,cccc,dddd,eeee,ffff,gggg,nnnnn,aaaaaaa | N | Watts 3/4" LF619 (HVD) | (O)
RPDA-II | Febco | LF886WZ | 10 | VUVD | 2020-05-15 | 2023-05-15 | Y | 10 | (mm),ll,oo,pp,zzz,cccc,dddd,eeee,ffff,gggg,nnnnn | N | Watts 3/4" LF619 (HVU) | (O),G,H,I,J,K,L,M,N,P,Q,T
RPDA-II | Febco | LF886WZ | 10 | VUVU | 2020-05-15 | 2023-05-15 | Y | 10 | (mm),ll,oo,pp,zzz,cccc,dddd,eeee,ffff,gggg,nnnnn | N | Watts 3/4" LF619 (HVD) | (O),G,H,I,J,K,L,M,N,P,Q,T
SVB | Watts | 008PCQT | 0.375 | VUH | 1998-11-18 | 2022-11-18 | N | 9 | (vv),xx,ooo,hhhh,pppp | Y
SVB | Watts | 008PCQT | 0.5 | VUH | 1998-11-18 | 2022-11-18 | N | 9 | (vv),xx,ooo,hhhh,pppp,rrrrr | Y
SVB | Watts | 008PCQT | 0.75 | VUH | 2000-06-19 | 2024-06-19 | N | 9 | (vv),xx,ooo,hhhh,pppp,rrrrr | Y
SVB | Watts | 008PCQT | 1 | VUH | 2000-06-19 | 2024-06-19 | N | 9 | (vv),xx,ooo,hhhh,pppp,rrrrr | Y
SVB | Watts | LF008PCQT | 0.375 | VUH | 2015-03-13 | 2024-03-13 | Y | 9 | (vv),xx,ooo,hhhh,pppp | N
SVB | Watts | LF008PCQT | 0.5 | VUH | 2015-03-13 | 2024-03-13 | Y | 9 | (vv),xx,ooo,hhhh,pppp,rrrrr | N
SVB | Watts | LF008PCQT | 0.75 | VUH | 2015-03-13 | 2024-03-13 | Y | 9 | (vv),xx,ooo,hhhh,pppp,rrrrr | N
SVB | Watts | LF008PCQT | 1 | VUH | 2015-03-13 | 2024-03-13 | Y | 9 | (vv),xx,ooo,hhhh,pppp,rrrrr | N
SVB | Wilkins | 460 | 0.375 | VUH | 2007-03-09 | 2022-03-09 | N | 9 | (ooo),ii | Y
SVB | Wilkins | 460 | 0.5 | VUH | 2007-03-09 | 2022-03-09 | N | 9 | (ooo),ii | Y
SVB | Wilkins | 460 | 0.75 | VUH | 2008-05-08 | 2023-05-08 | N | 9 | (ooo),ii | Y
SVB | Wilkins | 460 | 1 | VUH | 2008-05-08 | 2023-05-08 | N | 9 | (ooo),ii | Y
SVB | Wilkins | 460XL | 0.375 | VUH | 2011-03-21 | 2023-03-21 | Y | 9 | (iiii) | N |  |  | Testcocks: Female Threaded End or 45 degree male SAE flare
SVB | Wilkins | 460XL | 0.5 | VUH | 2011-03-21 | 2023-03-21 | Y | 9 | (iiii) | N |  |  | Testcocks: Female Threaded End or 45 degree male SAE flare
SVB | Wilkins | 460XL | 0.75 | VUH | 2011-03-21 | 2023-03-21 | Y | 9 | (iiii) | N |  |  | Testcocks: Female Threaded End or 45 degree male SAE flare
SVB | Wilkins | 460XL | 1 | VUH | 2011-03-21 | 2023-03-21 | Y | 9 | (iiii) | N |  |  | Testcocks: Female Threaded End or 45 degree male SAE flare

## Orientation Key
Orientation Key

## Shutoff Valves
Shutoff Valve Designations
Each backflow prevention assembly has been evaluated with a specific set of shutoff valves as an integral part of the assembly. The specific shutoff valves are coded by a parenthetic code with each assembly. This coding of shutoff valves is defined below. Other shutoff valves having similar performance characteristics which permit the assembly to comply with the standards are also shown immediately after the original shutoff valves. The use of any shutoff valve, other than those listed for that specific assembly invalidates the Approval. Assemblies listed with a Y in the “spare parts only” column may not include the shutoff valve designation.
(aa) | American Figure 1-QT
(bb) | American Figure 17-NRS RW
(cc) | American Figure 370OSY RW
(dd) | Apollo Series 7B-QT
(ee) | AVK Series 25-NRS
(ff) | AVK Series 25-OSY (Nibco F607RW OSY)
(gg) | Clow R/W Model 2640 (FxF) - NRS
(formerly Clow R/W F6102-NRS)
(hh) | Clow R/W Model 2640 (FxF) - OSY
(formerly Clow R/W F6136-OSY)
(ii) | Fortune Series 620/623 (C84400 Bronze) (Formerly Figure 601)
Private labeled as: Ames, Buckner, Febco, Flomatic, Hersey and Wilkins
(jj) | Kennedy Ken Seal I-NRS
(kk) | Kennedy Ken Seal-OSY
(ll) | Kennedy Model KS-FW Figure 8561 (FxF) - NRS (2 1/2" - 12")
Kennedy Model KS-RW Figure 7561 (FxF) - NRS (4" - 10")
(formerly Kennedy Ken Seal II-NRS)
(mm) | Kennedy Model KS-FW Figure 8068 (FxF) - OSY (2 1/2" - 12")
Kennedy Model KS-RW Figure 7068 (FxF) - OSY (4" - 10")
(formerly Kennedy Ken Seal II-OSY)
(nn) | Lee Brass-QT
(oo) | Watts Model 405 (2-1/2" - 10" NRS-RW FxF)
(pp) | Watts Model 408 (2-1/2" - 10" OSY-RW FxF)
(qq) | Mueller R/W HP NRS
(rr) | Mueller R/W HP OSY
(ss) | Toro.Orion Integral Ball Valve-QT
(tt) | American Flow Control (Waterous) Series 500-NRS
(uu) | American Flow Control (Waterous Series 500-OSY
(vv) | Watts Model FBV & FBV-E (1/4" - 2" Ball Valve QT)
Ames Model FBV & FBV-E (1/4" - 2" Ball Valve QT)
(ww) | Watts Moel G4000-FDA (2-1/2" -10" Ball Valve FxF)
(xx) | Watts Model 6080 & 6080-E (1/4" - 2" Ball Valve QT)
(yy) | Matco-Norca 10RW (NRS)
(zz) | Matco-Norca 105U (OSY)
(aaa) | American Flow Control Series 2500-NRS
(bbb) | American Flow Control Series 2500-OSY
(ccc) | M&H Model 4067-02 (NRS)
(ddd) | M&H Model 4068-02(OSY)
(eee) | Stockham Model G-610 (OSY)
(fff) | Febco Series 620 QT
(ggg) | Fortune Figure 620U-QT
(hhh) | Watts Model S-FBV & S-FBV-E (1/4" - 1" Ball Valve QT)
(iii) | Mueller Model A2360-NRS
(int) | Shutoff Valve is integral part of assembly
(jjj) | Febco Series 621-QT
(kkk) | Febco Series 620U-QT
(lll) | Mueller Model R2360-OSY
(mmm) | Conbraco Series IBVE-125-QT
(nnn) | Kennedy Model KS-FW Figure 8701 (FxF) - NRS (3" - 10") Post Indicator/Tapping
Kennedy Model KS-RW Figure 7701 (FxF) - NRS (4" - 10") Post Indicator/Tapping
(formerly Kennedy Ken Seal II Post Indicator/Tapping)
(ooo) | Ningbo Ball Valves (Febco 622F & 622FT, Watts Series 855-QT & Wilkins Series 850-QT)(1/4" - 2" Ball Valve QT)
(ppp) | Clow R/W Model 2639 (GxF) - NRS (2 1/2" - 3")
Clow R/W Model 2638 (GxF) - NRS (4" - 10")
(formerly Clow Series F6105-NRS)
(qqq) | Clow R/W Model 2639 (GxF) - OSY (2 1/2" - 3")
Clow R/W Model 2638 (GxF) - OSY (4" - 10")
(formerly Clow Series F6138-OSY)
(rrr) | Apollo Series 7B-308-01 (& 7B-308-31)
(sss) | Clow R/W Model 2639 (GxG) - NRS (2 1/2" - 3")
Clow R/W Model 2638 (GxFG) - NRS (4" - 10")
(formerly Clow Series F6104-NRS)
(ttt) | Clow R/W Model 2639 (GxG) - OSY (2 1/2" - 3")
Clow R/W Model 2638 (GxFG) - OSY (4" - 10")
(formerly Clow Series F6137-OSY)
(uuu) | Apollo Series 7H-QT
(vvv) | Clow R/W Model 2640 (FxF) - OSY Post Indicator/Tapping Valve
(formerly Clow R/W F6136-OSY Post Indicator/Tapping Valve)
(www) | Clow R/W Model 2639 (GxF) - OSY (2 1/2" - 3") Post Indicator/Tapping Valve
Clow R/W Model 2640 (GxF) - OSY (4" - 10") Post Indicator/Tapping Valve
(formerly Clow R/W F6138-OSY Post Indicator/Tapping Valve)
(xxx) | Ningbo Union Ball Valves (Febco 622UF & 622UFT & Wilkins 850U-QT)(1/2" - 2" Ball Valve QT)
(yyy) | Victaulic Series 702 (Butterfly valves)
(zzz) | Kennedy Model KS-RW Figure 7092ABF (FxG) - OSY
(formerly Kennedy Series 7092ABF-OSY)
(aaaa) | Union Model GV12 (flange by groove)-OSY
(bbbb) | Enbee Model GV12 (flange by groove)-OSY
(cccc) | Kennedy Model KS-RW Figure 7092 (FxG) - OSY
(formerly Kennedy Series 7092 (GxF) - OSY)
(dddd) | Kennedy Model KS-RW Figure 7592 (FxG) - NRS
(formerly Kennedy Series 7592ABF - NRS)
(eeee) | Kennedy Model KS-RW Figure 7592PABF (FxG) - NRS Post Indicator/Tapping Valve
(formerly Kennedy Series 7592PABF-Post Indicator/Tapping Valve)
(ffff) | Watts Model 409 (2-1/2" - 10" OSY-RW FxF)
(gggg) | Watts Model 409 (2-1/2" - 10" OSY-RW FxG)
(hhhh) | Watts Model LF-FBV & LF-FBV-E (1/4" - 2" Ball Valve QT)
Ames Model LF-FBV & LF-FBV-E (1/4" - 2" Ball Valve QT)
Febco Model LF-FBV & LF-FBV-E (1/4" - 2" Ball Valve QT)
(iiii) | Wilkins Series 850XL (850TXL) - QT
(jjjj) | WATTS Model 409 (2" OSY-RW NPTxNPT)
(kkkk) | Kennedy Model KS-RW Figure 7093 (GxG) - OSY
(llll) | Kennedy Model KS-RW Figure 7593 (GxG) - NRS
(mmmm) | Kennedy Model KS-RW Figure 7093ABF (GxG) - OSY
(nnnn) | Kennedy Model KS-RW Figure 7593ABF (GxG) - NRS
(oooo) | Kennedy Model KS-RW Figure 7593PABF (GxG) - NRS Post Indicator
(pppp) | Watts Model L-FBV & L-FBV-E (1/4" - 2" Ball Valve QT)
Ames Model L-FBV & L-FBV-E (1/4" - 2" Ball Valve QT)
Febco Model L-FBV & L-FBV-E (1/4" - 2" Ball Valve QT)
(qqqq) | Kennedy Figure G300E - Butterfly Valve (2 1/2"-6")
(rrrr) | Kennedy Figure 02G - Butterfly Valve (8")
(ssss) | Wilkins Model 48-509 (GXF) - NRS (2-1/2" - 12") [Effective 12/06/16. Formerly Model 48]
(tttt) | Wilkins Model 48-509 (FXF) - NRS (2-1/2" - 12") [Effective 12/06/16. Formerly Model 48]
(uuuu) | Wilkins Model 48-509 (GXG) - NRS (2-1/2" - 10") Post Indicator/Tapping Valve [Effective 12/06/16. Formerly Model 48]
(vvvv) | Wilkins Model 48-509 (GXF) - NRS (2-1/2" - 12") Post Indicator/Tapping Valve [Effective 12/06/16. Formerly Model 48]
(wwww) | Wilkins Model 48-509 (FXF) - NRS (2-1/2" - 12") Post Indicator/Tapping Valve [Effective 12/06/16. Formerly Model 48]
(xxxx) | Wilkins Model 48-509 (GXG) - OSY (2-1/2" - 10") [Effective 12/06/16. Formerly Model 48]
(yyyy) | Wilkins Model 48-509 (GXF) - OSY (2-1/2" - 12") [Effective 12/06/16. Formerly Model 48]
(zzzz) | Wilkins Model 48-509 (FXF) - OSY (2-1/2" - 12") [Effective 12/06/16. Formerly Model 48]
(aaaaa) | Wilkins Model 48-509 (GXG) - NRS (2-1/2" - 10") [Effective 12/06/16. Formerly Model 48]
(bbbbb) | Milwaukee BB-SC100 - Butterfly Valve
(ccccc) | Milwaukee BB-SCS02 - Butterfly Valve (with gearbox)
(ddddd) | Flomatic Model NRS
(eeeee) | Watts Model FBV-FP & FBV-E-FP (3/4" - 2" Ball Valve w/Gearbox)
Ames Model LFAFBV-FP & LFAFBV-E-FP (3/4" - 2" Ball Valve w/Gearbox)
(fffff) | Watts Model L-FBV-QT (2-1/2" - 4" Ball Valve NPTxG)
(ggggg) | Wilkins Model 850MSS
(hhhhh) | Fortune Series 620/623 (c89520 unleaded bronze)
(iiiii) | Apollo Series 77B-100 and 77C-100 - QT
(jjjjj) | Apollo Series 77BLF-100 and 77CLF-100 - QT
(kkkkk) | Wilkins Model 49 (GXF) - (2 1/2" - 10")
(lllll) | Wilkins Model 49 (GXG) - (2 1/2" - 10")
(mmmmm) | Wilkins 850UXL (850TUXL) -QT
(nnnnn) | Watts Model 405 (2 1/2" - 10" NRS-RW FxG)
(ooooo) | ARI HC260 and HC262 Ball Valves - QT
(ppppp) | Febco Model LF622UF & LF622UFT (1/2" - 2" Ball Valve QT)
(qqqqq) | Febco Model LF622F & LF622FT (1/2" - 2" Ball Valve QT)
(rrrrr) | Watts Model LFFBV-FRG & LFFBV-E-FRG (1/2" - 2" Ball Valve QT)
(sssss) | Apollo Series 91B and 91C-QT (1/2 - 2")
(ttttt) | Apollo Series 91BLF and 91CLF-QT (1/2 - 2")
(uuuuu) | Apollo Model 77B-LFU and 77C-LFU Union Ball Valves - QT (1/2")
(vvvvv) | Apollo Series 91BLF-U and 91CLF-U-QT (3/4"-2")
(wwwww) | Apollo Series 91B-U and 91C-U-QT (3/4"-2")
(xxxxx) | Apollo Model GV (FXG) - NRS (2-1/2" - 12")
(yyyyy) | Apollo Model GV (GXG) - NRS (2-1/2" - 12")
(zzzzz) | Apollo Model GV (FXG) - OSY (2-1/2" - 12")
(aaaaaa) | Apollo Model GV (GXG) - OSY (2-1/2" - 12")
(bbbbbb) | Apollo Model GV (FXF) - NRS (2-1/2" - 12")
(cccccc) | Apollo Model GV (FXF) - OSY (2-1/2" - 12")
(dddddd) | Apollo Model 77S-XT (1 1/2"-2" Ball Valve w/Gearbox)
(eeeeee) | Apollo Model 77S-LFXT (1 1/2"-2" Ball Valve w/Gearbox)
(ffffff) | ARI Model PLS-VA Ball Valves -QT (3/4"-2")
(gggggg) | Wilkins Model 48 (GXF) - NRS (2-1/2" - 12")
(hhhhhh) | Wilkins Model 48 (FXF) - NRS (2-1/2" - 12")
(iiiiii) | Wilkins Model 48 (GXG) - NRS (2-1/2" - 10") Post Indicator/Tapping Valve
(jjjjjj) | Wilkins Model 48 (GXF) - NRS (2-1/2" - 12") Post Indicator/Tapping Valve
(kkkkkk) | Wilkins Model 48 (FXF) - NRS (2-1/2" - 12") Post Indicator/Tapping Valve
(llllll) | Wilkins Model 48 (GXG) - OSY (2-1/2" - 10")
(mmmmmm) | Wilkins Model 48 (GXF) - OSY (2-1/2" - 12")
(nnnnnn) | Wilkins Model 48 (FXF) - OSY (2-1/2" - 12")
(oooooo) | Wilkins Model 48 (GXG) - NRS (2-1/2" - 10")
(pppppp) | Lansdale Model LPBLFB2 - Butterfly Valve (2")
(qqqqqq) | AVK Series 25-21 (GXF) - NRS
(rrrrrr) | AVK Series 25-11 (GXG) - NRS
(ssssss) | AVK Series 25-26 (GXF) -OSY
(tttttt) | AVK Series 25-16 (GxG) - OSY
(uuuuuu) | Ames Model LFAFBV-FP-GV-T & LFAFBV-E-FP-GV-T (1" - 2" Thread x Groove Ball Valve w/Gearbox)
(vvvvvv) | BEECO Mod GV (GXF) - NRS (2 1/2"-10")
(wwwwww) | BEECO Mod GV (GXF) - OSY (2 1/2"-10")
(xxxxxx) | Apollo Mod BFV (GXG) - (2 1/2"-10") - Butterfly Valves
(yyyyyy) | BEECO Mod BV Series (1/2"-2" Ball Valve QT)
(zzzzzz) | AVK Series 25-41 (FXF) - NRS
(aaaaaaa) | AVK Series 25-46 (FXF) - OSY

## Meters
Detector Assembly Meters
The Detector Assemblies contained herein have been evaluated with a specific meter as the detector element of the assembly. That specific meter is coded by a parenthetic letter shown in the “meters” column. The coding of meters is shown in this Section. Other meters having similar performance characteristics to permit the assembly to meet the Standard are shown immediately after the original evaluation meter. The use of any other meter or modified bypass piping invalidates the Approval. Some of the detector assemblies use a line-size assembly, which is not a standard stock Approved assembly. Increased loads are required in these line-size units to allow the assembly to accurately record low flow rates in the bypass meter. Therefore, various off-the-shelf components can not be assembled and expected to perform satisfactorily. The bypass backflow preventer Approved with the detector assembly is listed under the bypass column. This is only for verification purposes. Should replacement parts or a complete bypass be needed, the model number of the complete detector assembly should be used in ordering these components.
A | Hersey Model F-F 5/8" x 3/4"
B | Carlon 5/8" x 3/4"
C | Dandé Model D-3 5/8" x 3/4"
D | Gamon-Calmet 5/8"
E | Hays Acumeter 5/8" x 3/4"
F | Arad 5/8" x 3/4" (Master Meter)
G | Schlumberger 5/8" x 3/4" Model MBRF
H | Rockwell (Sensus) SR-II 5/8" x 3/4"
I | Hersey Model 430 - 5/8"
J | Elster AMCO Model C700 5/8”x3/4” (Formerly Kent, ABB)
K | Precision 5/8"
L | Neptune Trident 8 5/8"
M | Neptune T-10 5/8"(Lead free compliant version identified with NSF61 mark on meter)
N | Badger Model 25 3/4"
O | Badger 5/8" x 3/4" Model 25 (Lead free compliant version identified with NSF61 mark on meter)
P | Hersey Model 430 Series II 5/8"
Q | Hersey Model MVR-30 3/4"
R | Neptune T-10 1"
S | Neptune T-10 1 1/2"
T | Zenner Model PMN 5/8" x 3/4"
U | Badger Model 35 3/4" (Lead free compliant version identified with NSF61 mark on meter)

## Special Notices
Special Notices
The USC Foundation publishes Special Notices from time to time. These notices contain information that requires special attention. The Foundation makes Special Notices, in their first year of publication, an exclusive benefit for Foundation members. Members receive all Special Notices via mail immediately upon release. Please visit fccchr.usc.edu/list to view the Special Notices archive.
Notice 96-001
This notice lists Ames assemblies which have been reported with low check valve readings. Corrections to the problem are discussed.
Notice 97-001
This notice discusses changes in the retaining cup in the relief valve stem of the 8” and 10” Wilkins 975 reduced pressure principle assemblies.
Notice 97-002
This notice identifies Ames 2000SS, 3000SS, and 4000SS series assemblies that were discovered to have unapproved components.
Notice 97-003
This notice lists assemblies which were NOT Approved by the Foundation, although advertisements may have implied otherwise.
Notice 98-001
This notice advises members of certain action in the Federal Register regarding cross-connection control programs.
Notice 98-002
This notice advises members of Wilkins 950 series and 975 series modifications.
Notice 99-001
This notice lists assemblies which were NOT Approved by the Foundation, although advertisements may have implied otherwise.
Notice 99-002
This notice lists assemblies which were NOT Approved by the Foundation, although advertisements may have implied otherwise.
Notice 99-003
This notice lists assemblies which were NOT Approved by the Foundation, although advertisements may have implied otherwise.
Notice 01-001
This notice discuss silicon parts in certain Febco relief valves.
Notice 01-002/Revised Notice 01-002-R1
This notice discusses some check valves not approved in certain Ames and Watts assemblies.
Notice 01-003
This notice lists assemblies which were NOT Approved by the Foundation, although advertisements may have implied otherwise.
Notice 02-001
This notice explains there are some specific Febco assemblies with unapproved check valve retainers.
Notice 03-001
This notice explains there are improper markings of model designations on some Wilkins assemblies.
Notice 03-002
This notice explains the possibility of the interference of the check valves on some Ames and Watts assemblies.
Notice 04-001
This notice identifies some Febco 825YA assemblies sold with a dimensional variation.
Notice 05-001
This notice identifies some Ames and Watts assemblies sold with unapproved disc material.
Notice 06-001
This notice identifies unapproved guides found in certain Febco assemblies.
Notice 06-002
This notice identifies a change in the design of the Flomatic PVBs.
Notice 06-003
This notice lists assemblies which were NOT Approved by the Foundation, although advertisements may have implied otherwise.
Notice 07-001
This notice discusses out of tolerance springs on Conbraco assemblies.
Notice 09-001
This notice highlights unapproved third party components that are being distributed.
Notice 13-001
This notice discusses modifications to guiding surfaces of the check valves on Wilkins assemblies.
Notice 14-001
This notice lists assemblies which were NOT Approved by the Foundation, although advertisements may have implied otherwise.
Notice 14-002
This notice clarifies the method in which the model designation is indicated on the Wilkins 3/4” 950XLD and 975XLD assemblies.
Notice 15-001
This notice has been prepared to review Special Notice 14-002 and clarify the USC Approval Status of Wilkins Reduced Pressure Principle Detector Assemblies (RPDAs).
Notice 19-001
This notice brings to attention Ames and Watts DCDAs that may have been produced with the bypass assembly containing the incorrect model designation.

## Manufacturers
Manufacturers of Approved Backflow Prevention Assemblies
Ames Fire & Waterworks - A Watts Water Technologies Company | Cla-Val Company
http://www.amesfirewater.com/ | http://www.cla-val.com/
815 Chestnut Street | P. O. Box 1325
North Andover, MA 01845 | Newport Beach, CA 92659-0325
(978) 688-1811 | (949) 722-4800
Apollo/Conbraco Industries, Inc. | FEBCO - A Watts Water Technologies Company
http://www.apollovalves.com/ | http://www.febcoonline.com
P. O. Box 247 | 815 Chesnut Street
Matthews, NC 28105 | North Andover, MA 01845
(704) 847-9191 | (978) 688-1811
AQUESTIA (A.R.I) DIRECTING THE FLOW | Watts - A Watts Water Technologies Company
http://www.arivalves.com | http://www.wattsreg.com/
Kibbutz Kfar Charuv | 815 Chestnut Street
M.P. South Golan | North Andover, MA 01845
ISRAEL, 12932 | (978) 688-1811
972-4-6761800 or 972-4-6761988
Wilkins Regulator Company
Backflow Direct - A Watts Water Technologies Company | http://www.zurn.com/products/water-safety/backflow-prevention
www.backflowdirect.com | 1747 Commerce Way
815 Chestnut Street | Paso Robles, CA 93446
North Andover, MA 01845 | (800) 817-8177
(978) 688-1811
BEECO - Distributed by Mifab
www.beecobackflow.com
1321 West 119th St
Chicago, IL 60643-5109
(800) 465-2736